## Blue Labels
(SHT 1) ASSEMBLY CONSOLE | (SHT 10) ASSEMBLY^CONTROL PANEL | (SHT 11) 2 BAY LEFT WALL | (SHT 12) 2 BAY BACK LEFT WALL | (SHT 13) 2 BAY BACK RIGHT PANEL | (SHT 14) 2 BAY RIGHT WALL | (SHT 15) ORBIT 60^DOOR PANEL | (SHT 2) CONSOLE DOOR^PANEL | (SHT 4) METER PANEL | (SHT 5) SWITCH PANEL | (SHT 6) 1 BAY LEFT WALL | (SHT 7) 1 BAY BACK WALL | (SHT 8) 1 BAY RIGHT WALL | (SHT 9) PWR,DISTRIBUTION RAIL^LEFT DOOR
EL0274 | SH0412 | IEG8210 | IEG8220 | IEG8230 | IEG8240 | AR0610 | GF4000 | PA0703 | HL0704 | AT0140 | XT-9103 | IEG8130 | AT0680
EL0273 | SH0411 | XT-9201 | XT-9220 | XT0080 | XT-9350 | AP0629 | GF4000 | PV0700 | HL0703 | AT0220 | XT-9104 | FU0031 | XT0680
HA0273 | SH0405 | XT-9202 | XT-9221 | FU0080 | XT-9355 | AP0628 | GF4000 | PA0700 | HL0702 | XT0341 | XT9008 | XT0031 | XT0560
ZS0273 | SH0404 | XT-9203 | XT-9221A | FU0081 | XT-9360 | AP0627 | GF4000 | PA0771 | HL0701 | XT0342 | XT9015 | FU0032 | FU0680
ZS0274 | SA0400 | XT-9204 | XT-9222 | FU0082 | XT-9370 | AP0626 | GF4000 | PV0701 | SA0770 | GR9111 | XT-9107 | XT0032 | FU0560
FG0000 | SH0410 | XT-9205 | XT-9222A | XT0090 | XT-9380 | AP0625 | GF4000 | PA0701 | SA0710 | XT0930 | GR9123 | XT0085 | FU0200
24Y | SH0401 | XT-9206 | XT-9223 | FU0090 | XT-9381 | AP0624 | TM0102 | PF0701 | SA0740 | XT0340 | XT-9110 | FU0332 | FU0201
| SH0400 | XT-9207 | XT-9223A | FU0091 | GR9242 | AP0623 | AT0190K |  | PF0700 | XT0343 | XT-9113 | FU0333 | FU0190
| XT0564 | XT-9208 | XT-9242 | FU0092 | XT-9331 | AP0622 | AT0190 |  | SA0700 | XT-9390 | XT-9105 | FU0334 | FU0273
| AU0200 | XT-9209 | XT-9270 | FU0093 | XT-9334 | AP0621 |  |  | SA0701 | GR9112 | XT-9106 | FU0335 | XT0561
| HL0411 | GR9211 | XT-9271 | XT0171 | XT-9335 | AP0620 |  |  |  | KA0364 | XT-9114 | XT0332 | XT0562
| HL0410 | HIEG8210 | XT-9290 | KA0130 | XT-9336 | AP0619 |  |  |  |  | XT-9115 | XT0334 | XT0563
| HL0409 | PC0470 | XT-9291 | KA0176 | XT-9337 | AP0618 |  |  |  |  | XT-9116 | XT0335
| HL0408 | PC0471 | GR9222 | KA0177 | XT-9338 | AP0617 |  |  |  |  | XT-9117 | XT0336
| HL0407 | FU0136 | HIEG8220 | KA0221 | XT-9338A | AP0616 |  |  |  |  | XT-9118 | XT0337
| SB0400 | XT0138 | XT-9210 | KA0222 | GR9241 | AP0615 |  |  |  |  | XT-9120 | KA0310
| HL0406 | FU0137 | XT-9211 | KA0224 | XT0110 | AP0614 |  |  |  |  | XT-9150 | KA0320
| HL0405 | XT0139 | XT-9212 | KA0225 | FU0110 | AP0613 |  |  |  |  | XT-9127 | KA0330
| HL0404 | FU0210 | XT-9214 | KA0701 | FU0111 | AP0612 |  |  |  |  | GR9121 | KA0331
| HL0403 | FU0170 | XT-9215 | KA076E | FU0112 | UV0610 |  |  |  |  | RS0106 | KA0332
| HL0402 | XT0233 | XT-9216 | KA0817 | XT0050 | UV0611 |  |  |  |  | XT0106 | KA0333
| HL0401 | FU0010 | XT-9217 | KA0870 | FU0050 | [5 empty] | KA121C | KA0335
| HL0400 | FU0139 | XT-9218 | KA0871 | FU0051 | [5 empty] | KA0135 | KA0336
| SB0408 | FU0211 | XT-9219 | KA0923 | FU0052 | [5 empty] | KA3103 | KA0337
| SB0407 | FU0212 | XT-9219A | KA0924 | FU0053 | [5 empty] | KA3420 | XT0130
| SH0408 | FU0271 | GR9221 | KA0925 | FU0054 | [5 empty] | KA4100 | XT0120
| SB0405 | SPARE | UV0291 | KA0927 | FU0055 | [5 empty] | KA6211 | FU0120
| SB0406 | FU0274 | UAI9220-1 | KA0929 | XT0060 | [5 empty] | KA6212 | FU0121
| SA0401 | FU0281 | UAI9221-1 | KA093A | FU0060 | [5 empty] | KA121A | AF0123
| SB0404 | FU0291 | UAI9221-2 | KA0936 | FU0061 | [5 empty] | GR9122 | AF0122
| SB0403 | XT0134 | UAI9221-3 | KA0937 | FU0062 | [5 empty] | VD0121 | AF0121
| SB0402 | XT0135 | UAI9221-4 | KA0938 | FU0063 | [5 empty] | VD0122 | AU0120
| SB0401 | XT0235 | UAI9221-5 | KA0939 | FU0064 | [5 empty] | VD0123 | GR8131
| SH0409 | XT0237 | UAI9221A-1 | KA0942 | XT0070 | [5 empty] | VD0124 | PEG0130
| AF0201 | XT0136 | UAI9222-1 | KA0943 | FU0070 | [6 empty] | UJ0131
| AF0202 | KA0131 | UAI9222A-1 | KA0944 | FU0071 | [6 empty] | UJ0031
| GR0200 | KA0132 | UAI9223-1 | KA1020 | XT0450 | [6 empty] | QS0131
|  | KA0133 | UAI9223-2 | KA9982 | FU0450 | [6 empty] | XT-QS0131
|  | KA0134 | UAI9223-3 | KA9984 | AF0076 | [6 empty] | GR9132
|  | KA0136 | UAI9223-4 | GR9233 | AF0075 | [6 empty] | QS0031
|  | KA0137 | UAI9223-5 | XT-9319 | AF0074 | [6 empty] | XT-QS0031
|  | KA0138 | UAI9223A-1 | XT-9324 | AF0073 | [6 empty] | GR9131
|  | KA0141 | UAI9242-1 | XT-9325A | AF0072 | [6 empty] | FU0314
|  | KA0144 | UV0292 | XT-9326 | AF0071 | [6 empty] | FU0313
|  | KT0140 | UAI9270-1 | XT-9326A | AU0070 | [6 empty] | XT0360
|  | KT0141 | UAI9271-1 | XT-9327 | GR8241 | [6 empty] | FU0321
|  | KT0142 | UAI9290-1 | XT-9328 | AU0060 | [6 empty] | FU0322
|  | KT0143 | UAI9290-2 | XT-9329 | AF0061 | [6 empty] | XT0313
|  | KT0144 | UAI9290-3 | XT-9330 | AF0062 | [6 empty] | KA0121
|  | KT0145 | UAI9290-4 | GR9232 | AF0063 | [6 empty] | KA121B
|  | KT0146 | UAI9290-5 | AP0606 | AF0064 | [6 empty] | KA0123
|  | XT0240 | UAI9290-6 | XT-9300 | AF0065 | [6 empty] | XT0124
|  | KA0231 | UAI9290-7 | XT-9300A | AF0066 | [6 empty] | KA0126
|  | KA0232 | UAI9291-1 | XT-9311 | AF0067 | [6 empty] | KA0128
|  | KA0233 | UAI1520 | XT-9312 | AF0068 | [6 empty] | GR9133
|  | KA0234 | GR9224 | GR9231 | GR8242 | [6 empty] | KA0313
|  | KA0235 | UV0281 | AR0600 | AF0057 | [6 empty] | KA0314
|  | KA0236 | UAI9210-1 | KA0220 | AF0056 | [6 empty] | KA0323
|  | KA0237 | UAI9210-2 | AP0605 | AF0055 | [6 empty] | KA0324
|  | KA0238 | UAI9210-3 | AP0603 | AF0054 | [6 empty] | KA0124
|  | KA0239 | UAI9210-4 | AP0602 | AF0053 | [6 empty] | KA0125
|  | KA0240 | UAI9210-5 | AP0601 | AF0052
|  | KA0241 | UAI9210-6 | AT0600 | AF0051
|  | KA0242 | UAI9210-7 | UV0600 | AU0050
|  | KA0243 | UAI9211-1 | AP0604 | GR8243
|  | KA0244 | UAI9212-1 | AU0080 | AF0450
|  | KA0245 | UAI9212-2 | AF0081 | XT0400
|  | KA0246 | UAI9214-1 | AF0082
|  | KA0247 | UAI9214-3 | AF0083
|  | KA0248 | UAI9215-1 | AF0084
|  | KA0249 | UV0282 | AF0085
|  | KA0250 | UAI9216-1 | AF0086
|  | KA0621 | UAI9216-3 | AF0087
|  | KA0622 | UAI9217-1 | GR8231
|  | KA0810 | UAI9217-2 | AF0095
|  | KA0811 | UAI9217-5 | AF0094
|  | KA1820 | UAI9217-6 | AF0093
|  | KA1821 | UAI9217-7 | AF0092
|  | KA0822 | UAI9218-6 | AF0091
|  | KA0823 | UAI9218-7 | AU0090
|  | KA0877 | UAI9219-1 | GR8232
|  | KA0878 | UAI9219A-1
|  | GR9212 | GR9223
UV0271
UAI9201-1
UAI9201-2
UAI9201-3
UAI9201-4
UAI9201-5
UAI9201-6
UAI9201-7
UAI9201-8
UAI9201-9
UAI9201-10
UAI9202-1
UAI9202-2
UAI9203-1
UAI9204-1
UAI9205-1
UAI9205-2
UAI9205-3
UAI9205-4
UAI9205-5
UAI9205-6
UV0272
UAI9206-1
UAI9207-1
UAI9207-2
UAI9208-1
UAI9208-2
UAI9208-3
UAI9208-4
UAI9208-5
UAI9208-6
UAI9208-7
UAI9208-8
UAI9209-1
GR9213

## White Labels
(SHT 7) 1 BAY BACK WALL | (SHT 7) 1 BAY BACK WALL - (SHT 6) 1 BAY LEFT WALL | (SHT 7) 1 BAY BACK WALL - (SHT 8) 1 BAY RIGHT WALL | (SHT 6) 1 BAY LEFT WALL | (SHT 6) 1 BAY LEFT WALL - (SHT 8) 1 BAY RIGHT WALL | (SHT 8) 1 BAY RIGHT WALL | (SHT 8) 1 BAY RIGHT WALL - (SHT 11) 2 BAY LEFT WALL | (SHT 8) 1 BAY RIGHT WALL - (SHT 15) ORBIT 60^DOOR PANEL | (SHT 12) 2 BAY BACK LEFT WALL | (SHT 12) 2 BAY BACK LEFT WALL - (SHT 13) 2 BAY BACK RIGHT PANEL | (SHT 12) 2 BAY BACK LEFT WALL - (SHT 11) 2 BAY LEFT WALL | (SHT 12) 2 BAY BACK LEFT WALL - JB70 | (SHT 13) 2 BAY BACK RIGHT PANEL | (SHT 13) 2 BAY BACK RIGHT PANEL - (SHT 14) 2 BAY RIGHT WALL | (SHT 11) 2 BAY LEFT WALL | (SHT 11) 2 BAY LEFT WALL - (SHT 10) ASSEMBLY^CONTROL PANEL | (SHT 14) 2 BAY RIGHT WALL | (SHT 2) CONSOLE DOOR^PANEL
GR9123 | VBUSN | PEG013010 | GR9111 | W8104 | EXCS | IEG8210-G | PEG01301 | GR9221 | IEG8230-G | HIEG8220-HG | IEG01101 | AF0083G | IEG8240-G | HIEG8210-1 | IEG8210-1 | AF0055G | GF4000-A13
|  | W8003 |  | W8202 | GR9131 |  | PEG01302 | GR9222 |  | IEG8220-G |  | AF0084G |  | HIEG8210-2 |  | AF0056G
|  | W8004 |  | W8203 | IEG8130-1 |  |  | GR9224 |  |  |  | AF0085G |  |  |  | AF0064G
|  | W8101 |  | W8301 | IEG8130-2 |  |  | HIEG8220-1 |  |  |  | GR9231 |  |  |  | AF0065G
|  | W8102 |  |  | PMGS |  |  | HIEG8220-2 |  |  |  | GR9232 |  |  |  | AF0066G
[5 empty] | W8103 |  |  | HIEG8220-3 |  |  |  | GR9233 |  |  |  | AF0071G
[5 empty] | W8201 |  |  | HIEG8220-4 |  |  |  | IEG8230-1 |  |  |  | AF0072G
[12 empty] | IEG8230-2 |  |  |  | AF0073G
[12 empty] | IEG8230-3 |  |  |  | AF0074G
[12 empty] | IEG8230-4 |  |  |  | GR9241
[12 empty] | UV0600G |  |  |  | GR9242
IEG02304
IEG02305
IEG8240-1
IEG8240-2
IEG8240-3
IEG8240-6

## Heat Shrink Labels
(SHT 7) 1 BAY BACK WALL | (SHT 7) 1 BAY BACK WALL - (SHT 6) 1 BAY LEFT WALL | (SHT 7) 1 BAY BACK WALL - (SHT 4) METER PANEL | (SHT 6) 1 BAY LEFT WALL | (SHT 6) 1 BAY LEFT WALL - (SHT 4) METER PANEL | (SHT 12) 2 BAY BACK LEFT WALL | (SHT 12) 2 BAY BACK LEFT WALL - (SHT 13) 2 BAY BACK RIGHT PANEL | (SHT 12) 2 BAY BACK LEFT WALL - (SHT 14) 2 BAY RIGHT WALL | (SHT 12) 2 BAY BACK LEFT WALL - (SHT 15) ORBIT 60^DOOR PANEL | (SHT 13) 2 BAY BACK RIGHT PANEL - (SHT 11) 2 BAY LEFT WALL | (SHT 13) 2 BAY BACK RIGHT PANEL - (SHT 14) 2 BAY RIGHT WALL | (SHT 11) 2 BAY LEFT WALL | (SHT 11) 2 BAY LEFT WALL - (SHT 14) 2 BAY RIGHT WALL | (SHT 11) 2 BAY LEFT WALL - (SHT 15) ORBIT 60^DOOR PANEL | (SHT 14) 2 BAY RIGHT WALL
W4000 | W8164 | W8064 | WC8008 | W8065 | WI0554 | W0832 | W0554 | W6163 | W0831 | W0570 | WI0680 | W0680 | W6161 | W0552
| W8165 |  | WC8009 |  | WI0556 | W0834 | W0556 | W6224 | W0833 | W0571 | WI0681 | W0681 | W6171 | W0553
| W8264 |  |  |  | WI0557 | W0837 | W0557 | W6241 | W0835 | W0572 | WI0682 | W0682 | W6172 | W0643
[5 empty] | WI0560 | W0843 | W0560 | W6242 | W0836 | W0573 | WI0683 | W0683 | W6173 | W0646
[5 empty] | WI0561 | W0844 | W0561 | W6243 | W0840 | W0710 | WI0684 | W0684 | W6174 | W0663
[5 empty] | WI0562 | W0845 | W0562 | W6244 | W0841 | W0857 | WI0685 | W0685 | W6181 | W0665
[5 empty] | WI0563 | W0846 | W0563 |  | W0842 | W0860 | WI0686 | W0686 | W6182 | W0720
[5 empty] | WI0565 | W0852 | W0565 |  |  | W0866 | WI0730 | W0730 | W6211 | W0741
[5 empty] | WI0640 | W0853 | W0640 |  |  | WC4191 | WI0731 | W0731 | W6213 | W0742
[5 empty] | WI0641 | W0854 | W0641 |  |  | WC4681 | WI0732 | W0732 |  | W0743
[5 empty] | WI0642 | W0855 | W0642 |  |  | WC4682 | WI0733 | W0733 |  | WC4190
[5 empty] | WI0650 | W0856 | W0650 |  |  |  | WI0734 | W0734
[5 empty] | WI0722 | W0861 | W0722 |  |  |  | WI0735 | W0735
[5 empty] | WI0723 | W0863 | W0723 |  |  |  | WI0736 | W0736
[5 empty] | WI0750 | W0864 | W0750 |  |  |  | WI0746 | W0746
[5 empty] | WI0751 |  | W0751 |  |  |  | WI0747 | W0747
[5 empty] | WI0752 |  | W0752 |  |  |  | WI0831
[5 empty] | WI0753 |  | W0753 |  |  |  | WI0833
[5 empty] | WI0813A |  | W4501 |  |  |  | WI0835
[5 empty] | WI0814A | [5 empty] | WI0836
[5 empty] | WI0814B | [5 empty] | WI0840
[5 empty] | WI0816A | [5 empty] | WI0841
[5 empty] | WI0820 | [5 empty] | WI0842
[5 empty] | WI0821 | [5 empty] | WI6161
[5 empty] | WI0826A | [5 empty] | WI6171
[5 empty] | WI0826B | [5 empty] | WI6172
[5 empty] | WI0832 | [5 empty] | WI6173
[5 empty] | WI0834 | [5 empty] | WI6174
[5 empty] | WI0837 | [5 empty] | WI6181
[5 empty] | WI0843 | [5 empty] | WI6182
[5 empty] | WI0844 | [5 empty] | WI6211
[5 empty] | WI0845 | [5 empty] | WI6213
WI0846
WI0851
WI0852
WI0853
WI0854
WI0855
WI0856
WI0861
WI0863
WI0864
WI0876A
WI0910
WI0913
WI091E
WI091F
WI3200A
WI3200B
WI4501
WI6163
WI6224
WI6241
WI6242
WI6243
WI6244

## 1 BAY BACK WALL
1 BAY BACK WALL
Project # | G9440
Project Name | NOC AL SHAHEEN T130
Revision | A.5
Controls DE | G. Colby
Phone:
Controls ME | R. Duran
Phone:
From | [5 empty] | To
Device ID | Cable (W) Conductor (SC) Jumper Clip (JC) | Wire No. | Wire ID | Gauge/Size | Page/Zone | Device ID | Location | Page/Zone
XT-9103:1 | JC | EXC0 | CLIP | --- | 102.C4 | XT-9103:2 | 1 BAY BACK WALL | 102.C4
XT-9103:5 | JC | EXC2 | CLIP | --- | 102.C4 | XT-9103:4 | 1 BAY BACK WALL | 102.C5
XT-9103:6 | JC | EXCS | CLIP | --- | 102.C4 | XT-9103:7 | 1 BAY BACK WALL | 102.C5
XT-9106:2 | JC | CCT1(+) | CLIP | --- | 103.B4 | XT-9106:1 | 1 BAY BACK WALL | 103.B4
XT-9106:4 | JC | CCT1(-) | CLIP | --- | 103.B4 | XT-9106:3 | 1 BAY BACK WALL | 103.B4
XT-9110:1 | JC | VGENA | CLIP | --- | 100.D4 | XT-9110:2 | 1 BAY BACK WALL | 100.D4
XT-9110:3 | JC | VGENB | CLIP | --- | 100.D4 | XT-9110:4 | 1 BAY BACK WALL | 100.D4
XT-9110:5 | JC | VGENC | CLIP | --- | 100.D4 | XT-9110:6 | 1 BAY BACK WALL | 100.D4
XT-9113:1 | JC | VBUSA | CLIP | --- | 100.B4 | XT-9113:2 | 1 BAY BACK WALL | 100.B4
XT-9113:3 | JC | VBUSB | CLIP | --- | 100.B4 | XT-9113:4 | 1 BAY BACK WALL | 100.B4
XT-9113:5 | JC | VBUSC | CLIP | --- | 100.B4 | XT-9113:6 | 1 BAY BACK WALL | 100.B4
XT-9113:7 | JC | VBUSN | CLIP | --- | 100.B4 | XT-9113:8 | 1 BAY BACK WALL | 100.B4
XT-9113:8 | JC | VBUSN | CLIP | --- | 100.B4 | XT-9113:9 | 1 BAY BACK WALL | 100.C4
GR9121: | SC | GR9121 | GRN/YEL | 14 | 4.A4 | FRAME | 1 BAY BACK WALL | 4.A3
GR9122: | SC | GR9122 | GRN/YEL | 14 | 4.A4 | FRAME | 1 BAY BACK WALL | 4.A4
GR9123: | SC | GR9123 | GRN/YEL | 14 | 4.A5 | FG0001:1 | 1 BAY BACK WALL | 4.A5
KA0135:11 | SC | KM3150-EN | RED | 16 | 92.C6 | XT-9115:2 | 1 BAY BACK WALL | 92.C4
KA0135:12 | SC | KM3150-EP | RED | 16 | 92.C6 | XT-9115:1 | 1 BAY BACK WALL | 92.C4
KA121C:11 | SC | KM2220-N | RED | 16 | 63.C6 | XT-9114:2 | 1 BAY BACK WALL | 63.C4
KA121C:14 | SC | KM2220-P | RED | 16 | 63.C6 | XT-9114:1 | 1 BAY BACK WALL | 63.C4
KA3103:11 | SC | KH3103-EN | RED | 16 | 96.C6 | XT-9116:2 | 1 BAY BACK WALL | 96.C4
KA3103:14 | SC | KH3103-EP | RED | 16 | 96.C6 | XT-9116:1 | 1 BAY BACK WALL | 96.C4
KA3420:11 | SC | KM3420-EN | RED | 16 | 87.C5 | XT-9150:2 | 1 BAY BACK WALL | 87.C4
KA3420:14 | SC | KM3420-EP | RED | 16 | 87.C5 | XT-9150:1 | 1 BAY BACK WALL | 87.B4
KA4100:11 | SC | KM4100-EN | RED | 16 | 88.A6 | XT-9120:2 | 1 BAY BACK WALL | 88.A4
KA4100:12 | SC | KM4100-EP | RED | 16 | 88.A6 | XT-9120:1 | 1 BAY BACK WALL | 88.A4
KA6211:11 | SC | KM6211-EN | RED | 16 | 117.C6 | XT-9118:2 | 1 BAY BACK WALL | 117.C4
KA6211:14 | SC | KM6211-EP | RED | 16 | 117.C6 | XT-9118:1 | 1 BAY BACK WALL | 117.C4
KA6212:11 | SC | KM6212-EN | RED | 16 | 118.C6 | XT-9117:2 | 1 BAY BACK WALL | 118.C4
KA6212:14 | SC | KM6212-EP | RED | 16 | 118.C6 | XT-9117:1 | 1 BAY BACK WALL | 118.C4
VD0121:- | SC | VD0122 | WHT | 12 | 102.D4 | VD0122:+ | 1 BAY BACK WALL | 102.D4
VD0121:+ | SC | EXC2 | WHT | 12 | 102.D4 | XT-9103:5 | 1 BAY BACK WALL | 102.C4
VD0122:- | SC | VD0123 | WHT | 12 | 102.D4 | VD0123:+ | 1 BAY BACK WALL | 102.D4
VD0123:- | SC | VD0124 | WHT | 12 | 102.D4 | VD0124:+ | 1 BAY BACK WALL | 102.D4
VD0124:- | SC | EXC0 |  |  | 102.D4 | XT-9103:1 | 1 BAY BACK WALL | 102.C4
XT-9103:2 | SC | EXC0 |  |  | 102.C4 | XT-9103:1 | 1 BAY BACK WALL | 102.C4
XT-9105:3 | W4000 | RE4000-S | SH | 16 | 105.A4 | FG-GF4000:2 | 1 BAY BACK WALL | 105.B5
XT-9106:1 | SC | CCT1(+) | BLU | 12 | 103.B4 | AT0220:33 ID RES(+) | 1 BAY LEFT WALL | 103.D7
XT-9106:2 | SC | CCT1(+) | BLU | 12 | 103.B4 | AT0220:27 ID RLY | 1 BAY LEFT WALL | 103.D7
XT-9106:3 | SC | CCT1(-) | BLU | 12 | 103.B4 | AT0140:43 ID(-) | 1 BAY LEFT WALL | 103.C7
XT-9106:4 | SC | CCT1(-) | BLU | 12 | 103.B4 | AT0140:28 ID RLY | 1 BAY LEFT WALL | 103.C7
XT-9110:1 | SC | VGENA | RED | 16 | 100.D4 | AT0140:13 VGEN-A | 1 BAY LEFT WALL | 100.D7
XT-9110:1 | SC | VGENA | RED | 16 | 100.D4 | AT0220:13 VGEN-A | 1 BAY LEFT WALL | 100.C7
XT-9110:2 | SC | VGENA | RED | 16 | 100.D4 | XT0341:7 | 1 BAY LEFT WALL | 21.D2
XT-9110:3 | SC | VGENB | RED | 16 | 100.D4 | AT0140:14 VGEN-B | 1 BAY LEFT WALL | 100.D7
XT-9110:3 | SC | VGENB | RED | 16 | 100.D4 | AT0220:14 VGEN-B | 1 BAY LEFT WALL | 100.C7
XT-9110:4 | SC | VGENB | RED | 16 | 100.D4 | XT0341:4 | 1 BAY LEFT WALL | 21.D2
XT-9110:4 | SC | VGENB | RED | 16 | 100.D4 | KA0364:2 | 1 BAY LEFT WALL | 21.C1
XT-9110:5 | SC | VGENC | RED | 16 | 100.D4 | AT0140:15 VGEN-C | 1 BAY LEFT WALL | 100.D7
XT-9110:5 | SC | VGENC | RED | 16 | 100.D4 | AT0220:15 VGEN-C | 1 BAY LEFT WALL | 100.C7
XT-9110:6 | SC | VGENC | RED | 16 | 100.D4 | XT0341:6 | 1 BAY LEFT WALL | 21.D2
XT-9110:6 | SC | VGENC | RED | 16 | 100.D4 | KA0364:1 | 1 BAY LEFT WALL | 21.C1
XT-9113:1 | SC | VBUSA | RED | 16 | 100.B4 | AT0140:17 VBUS-A | 1 BAY LEFT WALL | 100.B7
XT-9113:1 | SC | VBUSA | RED | 16 | 100.B4 | AT0220:17 VBUS-A | 1 BAY LEFT WALL | 100.A7
XT-9113:2 | SC | VBUSA | RED | 16 | 100.B4 | XT0341:2 | 1 BAY LEFT WALL | 21.D2
XT-9113:3 | SC | VBUSB | RED | 16 | 100.B4 | AT0140:18 VBUS-B | 1 BAY LEFT WALL | 100.B7
XT-9113:3 | SC | VBUSB | RED | 16 | 100.B4 | AT0220:18 VBUS-B | 1 BAY LEFT WALL | 100.A7
XT-9113:4 | SC | VBUSB | RED | 16 | 100.B4 | XT0341:1 | 1 BAY LEFT WALL | 21.D2
XT-9113:5 | SC | VBUSC | RED | 16 | 100.B4 | AT0140:19 VBUS-C | 1 BAY LEFT WALL | 100.B7
XT-9113:5 | SC | VBUSC | RED | 16 | 100.B4 | AT0220:19 VBUS-C | 1 BAY LEFT WALL | 100.A7
XT-9113:6 | SC | VBUSC | RED | 16 | 100.B4 | XT0341:3 | 1 BAY LEFT WALL | 21.D2
XT-9113:7 | SC | VBUSN | GRN/YEL | 14 | 100.B4 | AT0140:20 VBUS-N | 1 BAY LEFT WALL | 100.B7
XT-9113:7 | SC | VBUSN | GRN/YEL | 14 | 100.B4 | AT0220:20 VBUS-N | 1 BAY LEFT WALL | 100.A7
XT-9113:8 | SC | VBUSN | GRN/YEL | 14 | 100.B4 | AT0140:16 VGEN-N | 1 BAY LEFT WALL | 100.D7
XT-9113:8 | SC | VBUSN | GRN/YEL | 14 | 100.B4 | AT0220:16 VGEN-N | 1 BAY LEFT WALL | 100.C7
XT-9127:1 | SC | MCTA | BLU | 12 | 101.B4 | AT0140:36 I1(+) | 1 BAY LEFT WALL | 101.B7
XT-9127:2 | SC | MCTB | BLU | 12 | 101.B4 | AT0140:38 I2(+) | 1 BAY LEFT WALL | 101.B7
XT-9127:3 | SC | MCTC | BLU | 12 | 101.B4 | AT0140:40 I3(+) | 1 BAY LEFT WALL | 101.B7
XT-9127:4 | SC | MCTN | BLU | 16 | 101.B4 | XT0342:2 | 1 BAY LEFT WALL | 21.B2
RS0106:2 | W8164 | EXC1 | WHT | 16 | 20.A4 | XT0340:2 | 1 BAY LEFT WALL | 20.A5
RS0106:4 | W8164 | EXC0 | BLK | 16 | 20.A4 | XT0340:3 | 1 BAY LEFT WALL | 20.A5
XT0106:1 | W8164 | EXCS | SH | 16 | 20.A4 | XT0340:4 | 1 BAY LEFT WALL | 20.A5
XT-9103:2 | W8165 | EXC0 | WHT | 16 | 102.C4 | XT0340:5 | 1 BAY LEFT WALL | 20.A5
XT-9103:5 | W8165 | EXC2 | BLK | 16 | 102.C4 | XT0340:6 | 1 BAY LEFT WALL | 20.B5
XT-9103:7 | W8165 | EXCS | SH | 16 | 102.C5 | XT0340:7 | 1 BAY LEFT WALL | 20.B5
XT-9103:3 | W8264 | EXC1 | WHT | 16 | 102.C5 | XT0340:2 | 1 BAY LEFT WALL | 20.A5
XT-9103:2 | W8264 | EXC0 | BLK | 16 | 102.C4 | XT0340:3 | 1 BAY LEFT WALL | 20.A5
XT-9103:6 | W8264 | EXCS | SH | 16 | 102.C4 | XT0340:4 | 1 BAY LEFT WALL | 20.A5
KA121A:A1 | SC | 012110 | WHT | 20 | 30.A5 | AF0121:10 | 1 BAY RIGHT WALL | 30.A7
KA121A:A2 | SC | 012126 | WHT | 20 | 30.A5 | AF0121:26 | 1 BAY RIGHT WALL | 30.A7
KA121C:A2 | SC | 012128 | WHT | 20 | 63.C6 | AF0121:28 | 1 BAY RIGHT WALL | 63.C7
KA3103:A1 | SC | 012115 | WHT | 20 | 96.C6 | AF0121:15 | 1 BAY RIGHT WALL | 96.C7
KA3103:A2 | SC | 012131 | WHT | 20 | 96.C6 | AF0121:31 | 1 BAY RIGHT WALL | 96.C7
KA3420:A1 | SC | 012113 | WHT | 20 | 87.B5 | AF0121:13 | 1 BAY RIGHT WALL | 87.B7
KA3420:A2 | SC | 012129 | WHT | 20 | 87.B5 | AF0121:29 | 1 BAY RIGHT WALL | 87.B7
KA4100:A1 | SC | KA033614 | WHT | 20 | 88.A6 | KA0336:14 | 1 BAY RIGHT WALL | 88.A5
KA4100:A2 | SC | 012130 | WHT | 20 | 88.A6 | AF0121:30 | 1 BAY RIGHT WALL | 88.A7
XT-9107:1 | SC | KA0332-11 | WHT | 20 | 29.C4 | KA0332:11 | 1 BAY RIGHT WALL | 29.C6
XT-9107:10 | SC | KA0333-24 | WHT | 20 | 29.D4 | KA0333:24 | 1 BAY RIGHT WALL | 29.D6
XT-9107:2 | SC | KA0332-14 | WHT | 20 | 29.C4 | KA0332:14 | 1 BAY RIGHT WALL | 29.C6
XT-9107:3 | SC | KA0333-11 | WHT | 20 | 29.D4 | KA0333:11 | 1 BAY RIGHT WALL | 29.D6
XT-9107:4 | SC | KA0333-14 | WHT | 20 | 29.D4 | KA0333:14 | 1 BAY RIGHT WALL | 29.D6
XT-9107:5 | SC | KA0128-21 | WHT | 20 | 29.C4 | KA0128:21 | 1 BAY RIGHT WALL | 29.C6
XT-9107:6 | SC | KA0128-24 | WHT | 20 | 29.C4 | KA0128:24 | 1 BAY RIGHT WALL | 29.C6
XT-9107:9 | SC | KA0333-21 | WHT | 20 | 29.D4 | KA0333:21 | 1 BAY RIGHT WALL | 29.D6
XT-9127:5 | SC | PEG013010 | GRN/YEL | 12 | 101.B4 | PEG0130:10 | 1 BAY RIGHT WALL | 101.B5
XT-9104:1 | W8003 | PMG1 | WHT | 12 | 102.B4 | FU0321:LI | 1 BAY RIGHT WALL | 102.B5
XT-9104:2 | W8003 | PMG2 | BLK | 12 | 102.B4 | FU0322:LI | 1 BAY RIGHT WALL | 102.B5
XT-9104:3 | W8003 | PMGS | SH | 12 | 102.B4 | XT0360:2 | 1 BAY RIGHT WALL | 102.B5
XT-9103:3 | W8004 | EXC1 | WHT | 12 | 102.C5 | KA0125:14 | 1 BAY RIGHT WALL | 102.D6
XT-9103:4 | W8004 | EXC2 | BLK | 12 | 102.C5 | KA0125:44 | 1 BAY RIGHT WALL | 102.D6
XT-9103:7 | W8004 | EXCS | SH | 12 | 102.C5 | XT0124:2 | 1 BAY RIGHT WALL | 102.D6
XT-9104:1 | W8101 | PMG1 | WHT | 12 | 102.B4 | FU0313:LI | 1 BAY RIGHT WALL | 102.B5
XT-9104:2 | W8101 | PMG2 | BLK | 12 | 102.B4 | FU0314:LI | 1 BAY RIGHT WALL | 102.B5
XT-9104:3 | W8101 | PMGS | SH | 12 | 102.B4 | XT0360:1 | 1 BAY RIGHT WALL | 102.B5
XT-9103:3 | W8102 | EXC1 | WHT | 12 | 102.C5 | KA0124:14 | 1 BAY RIGHT WALL | 102.C6
XT-9103:4 | W8102 | EXC2 | BLK | 12 | 102.C5 | KA0124:44 | 1 BAY RIGHT WALL | 102.C6
XT-9103:7 | W8102 | EXCS | SH | 12 | 102.C5 | XT0124:1 | 1 BAY RIGHT WALL | 102.C6
KA121A:21 | SC | YK7580-1 | WHT | 20 | 30.A5 | XT-9300:1 | 2 BAY BACK RIGHT PANEL | 30.A4
KA121A:24 | SC | YK7580-2 | WHT | 20 | 30.A5 | XT-9300:2 | 2 BAY BACK RIGHT PANEL | 30.A4
KA6211:A2 | SC | 009320 | WHT | 20 | 117.C6 | AF0093:20 | 2 BAY BACK RIGHT PANEL | 117.C7
KA6212:A2 | SC | 009321 | WHT | 20 | 118.C6 | AF0093:21 | 2 BAY BACK RIGHT PANEL | 118.C7
KA0135:A1 | SC | KA0135A1 | WHT | 20 | 17.D6 | KA0144:A1 | 2 BAY LEFT WALL | 17.C6
KA0135:A1 | SC | KA0135A1 | WHT | 20 | 17.D6 | KA0131:11 | 2 BAY LEFT WALL | 17.D4
KA0135:A2 | SC | 0V | WHT | 20 | 17.D6 | KA0144:A2 | 2 BAY LEFT WALL | 17.C6
KA0135:A2 | SC | 0V | WHT | 20 | 17.D6 | KA0136:A2 | 2 BAY LEFT WALL | 17.D6
KA121C:A1 | SC | KA0239-14 | WHT | 20 | 63.C6 | KA0239:14 | 2 BAY LEFT WALL | 63.C5
KA6211:A1 | SC | KA6211A1 | WHT | 20 | 117.C6 | KA0246:14 | 2 BAY LEFT WALL | 117.C5
KA6212:A1 | SC | KA6212A1 | WHT | 20 | 118.C6 | KA0247:14 | 2 BAY LEFT WALL | 118.C5
XT-9105:1 | W4000 | RE4000-1 | WHT | 16 | 105.A4 | GF4000:A1 | CONSOLE DOOR^PANEL | 105.A5
XT-9105:2 | W4000 | RE4000-2 | BLK | 16 | 105.A4 | GF4000:A3 | CONSOLE DOOR^PANEL | 105.A5
KA121A:14 | SC | PF07017 | RED | 16 | 21.B6 | PF0701:7 | METER PANEL | 21.B6
XT-9110:6 | SC | VGENC | RED | 16 | 100.D4 | PA0771:8 | METER PANEL | 21.C3
RS0106:1 | W8064 | PA07017 | RED | 20 | 20.A4 | PA0701:7 | METER PANEL | 20.A1
RS0106:3 | W8064 | PA07018 | BLK | 20 | 20.A4 | PA0701:8 | METER PANEL | 20.A1
XT0106:1 | W8064 | EXCS | SH | 20 | 20.A4 | FLOATING | METER PANEL | 20.A1
KA121A:11 | SC | VGENC | RED | 16 | 21.B6 | SA0770:24 | SWITCH PANEL | 21.B6
SolarTools ver. 24.0.84.26264 (Jun 3, 2025)
Report date: 7/10/2025 2:58 PM

## 1 BAY LEFT WALL
1 BAY LEFT WALL
Project # | G9440
Project Name | NOC AL SHAHEEN T130
Revision | A.5
Controls DE | G. Colby
Phone:
Controls ME | R. Duran
Phone:
From | [5 empty] | To
Device ID | Cable (W) Conductor (SC) Jumper Clip (JC) | Wire No. | Wire ID | Gauge/Size | Page/Zone | Device ID | Location | Page/Zone
XT0341:4 | JC | VGENB | CLIP | --- | 21.D2 | XT0341:5 | 1 BAY LEFT WALL | 21.D2
AT0140:27 ID RLY | SC | AT022028 | BLU | 12 | 103.C7 | AT0220:28 ID RLY | 1 BAY LEFT WALL | 103.D7
AT0140:33 ID RES(+) | SC | AT022043 | BLU | 12 | 103.C7 | AT0220:43 ID(-) | 1 BAY LEFT WALL | 103.D7
AT0140:34 ID RES(-) | SC | AT014034 | WHT | 16 | 103.C7 | AT0140:42 ID(+) | 1 BAY LEFT WALL | 103.C7
AT0140:37 I1(-) | SC | AT0140I1(-) | BLU | 12 | 101.B7 | AT0220:36 I1(+) | 1 BAY LEFT WALL | 101.C7
AT0140:39 I2(-) | SC | AT0140I2(-) | BLU | 12 | 101.B7 | AT0220:38 I2(+) | 1 BAY LEFT WALL | 101.C7
AT0140:41 I3(-) | SC | AT0140I3(-) | BLU | 12 | 101.B7 | AT0220:40 I3(+) | 1 BAY LEFT WALL | 101.C7
AT0140:56 FG | SC | AT0140G | GRN/YEL | 12 | 25.C6 | FRAME | 1 BAY LEFT WALL | 25.C6
AT0220:34 ID RES(-) | SC | AT022034 | WHT | 16 | 103.D7 | AT0220:42 ID(+) | 1 BAY LEFT WALL | 103.D7
AT0220:37 I1(-) | SC | PA07716 | BLU | 16 | 101.C7 | XT0342:4 | 1 BAY LEFT WALL | 21.C2
AT0220:39 I2(-) | SC | SA074013 | BLU | 16 | 101.C7 | XT0342:3 | 1 BAY LEFT WALL | 21.B3
AT0220:41 I3(-) | SC | PA07035 | BLU | 16 | 101.C7 | XT0342:1 | 1 BAY LEFT WALL | 21.A2
AT0220:56 FG | SC | AT0220G | GRN/YEL | 12 | 25.D6 | FRAME | 1 BAY LEFT WALL | 25.D5
GR9111: | SC | GR9111 | GRN/YEL | 14 | 4.A4 | FG-GR9112:1 | 1 BAY LEFT WALL | 4.A3
GR9112: | SC | GR9112 | GRN/YEL | 14 | 4.A4 | FRAME | 1 BAY LEFT WALL | 4.A4
KA0364:3 | SC | VBUSC | RED | 16 | 21.C1 | XT0341:3 | 1 BAY LEFT WALL | 21.D2
KA0364:4 | SC | VBUSB | RED | 16 | 21.C1 | XT0341:1 | 1 BAY LEFT WALL | 21.D2
AT0140:P2 | WC0114 | AT0140P2 | ENET | CABLE | 3.B3 | AT0220:P1 | 1 BAY LEFT WALL | 3.B4
XT-9390:1 | WC8008 | AT0140LS(+) | WHT | 16 | 104.C4 | XT0930:1 | 1 BAY LEFT WALL | 104.C5
XT-9390:2 | WC8008 | AT0140LS(-) | BLK | 16 | 104.C4 | XT0930:2 | 1 BAY LEFT WALL | 104.C5
XT-9390:3 | WC8008 | AT0140LS(S) | SH | 16 | 104.C4 | XT0930:3 | 1 BAY LEFT WALL | 104.C5
AT0140:1 LS(+) | WC8009 | AT0140LS(+) | WHT | 16 | 104.C7 | XT0930:1 | 1 BAY LEFT WALL | 104.C5
AT0140:2 LS(-) | WC8009 | AT0140LS(-) | BLK | 16 | 104.C7 | XT0930:2 | 1 BAY LEFT WALL | 104.C5
FW0140:3 | WC8009 | AT0140LS(S) | SH | 16 | 104.C6 | XT0930:3 | 1 BAY LEFT WALL | 104.C5
AT0220:1 LS(+) | WC8010 | AT0140LS(+) | WHT | 16 | 104.D7 | XT0930:1 | 1 BAY LEFT WALL | 104.C5
AT0220:2 LS(-) | WC8010 | AT0140LS(-) | BLK | 16 | 104.D7 | XT0930:2 | 1 BAY LEFT WALL | 104.C5
AT0140:DB-9 | WC8061 | AT0220DB9 | CABLE | CABLE | 25.C6 | AT0220:DB-9 | 1 BAY LEFT WALL | 25.D6
AT0140:13 VGEN-A | SC | VGENA | RED | 16 | 100.D7 | XT-9110:1 | 1 BAY BACK WALL | 100.D4
AT0140:14 VGEN-B | SC | VGENB | RED | 16 | 100.D7 | XT-9110:3 | 1 BAY BACK WALL | 100.D4
AT0140:15 VGEN-C | SC | VGENC | RED | 16 | 100.D7 | XT-9110:5 | 1 BAY BACK WALL | 100.D4
AT0140:16 VGEN-N | SC | VBUSN | GRN/YEL | 14 | 100.D7 | XT-9113:8 | 1 BAY BACK WALL | 100.B4
AT0140:17 VBUS-A | SC | VBUSA | RED | 16 | 100.B7 | XT-9113:1 | 1 BAY BACK WALL | 100.B4
AT0140:18 VBUS-B | SC | VBUSB | RED | 16 | 100.B7 | XT-9113:3 | 1 BAY BACK WALL | 100.B4
AT0140:19 VBUS-C | SC | VBUSC | RED | 16 | 100.B7 | XT-9113:5 | 1 BAY BACK WALL | 100.B4
AT0140:20 VBUS-N | SC | VBUSN | GRN/YEL | 14 | 100.B7 | XT-9113:7 | 1 BAY BACK WALL | 100.B4
AT0140:28 ID RLY | SC | CCT1(-) | BLU | 12 | 103.C7 | XT-9106:4 | 1 BAY BACK WALL | 103.B4
AT0140:36 I1(+) | SC | MCTA | BLU | 12 | 101.B7 | XT-9127:1 | 1 BAY BACK WALL | 101.B4
AT0140:38 I2(+) | SC | MCTB | BLU | 12 | 101.B7 | XT-9127:2 | 1 BAY BACK WALL | 101.B4
AT0140:40 I3(+) | SC | MCTC | BLU | 12 | 101.B7 | XT-9127:3 | 1 BAY BACK WALL | 101.B4
AT0140:43 ID(-) | SC | CCT1(-) | BLU | 12 | 103.C7 | XT-9106:3 | 1 BAY BACK WALL | 103.B4
AT0220:13 VGEN-A | SC | VGENA | RED | 16 | 100.C7 | XT-9110:1 | 1 BAY BACK WALL | 100.D4
AT0220:14 VGEN-B | SC | VGENB | RED | 16 | 100.C7 | XT-9110:3 | 1 BAY BACK WALL | 100.D4
AT0220:15 VGEN-C | SC | VGENC | RED | 16 | 100.C7 | XT-9110:5 | 1 BAY BACK WALL | 100.D4
AT0220:16 VGEN-N | SC | VBUSN | GRN/YEL | 14 | 100.C7 | XT-9113:8 | 1 BAY BACK WALL | 100.B4
AT0220:17 VBUS-A | SC | VBUSA | RED | 16 | 100.A7 | XT-9113:1 | 1 BAY BACK WALL | 100.B4
AT0220:18 VBUS-B | SC | VBUSB | RED | 16 | 100.A7 | XT-9113:3 | 1 BAY BACK WALL | 100.B4
AT0220:19 VBUS-C | SC | VBUSC | RED | 16 | 100.A7 | XT-9113:5 | 1 BAY BACK WALL | 100.B4
AT0220:20 VBUS-N | SC | VBUSN | GRN/YEL | 14 | 100.A7 | XT-9113:7 | 1 BAY BACK WALL | 100.B4
AT0220:27 ID RLY | SC | CCT1(+) | BLU | 12 | 103.D7 | XT-9106:2 | 1 BAY BACK WALL | 103.B4
AT0220:33 ID RES(+) | SC | CCT1(+) | BLU | 12 | 103.D7 | XT-9106:1 | 1 BAY BACK WALL | 103.B4
KA0364:1 | SC | VGENC | RED | 16 | 21.C1 | XT-9110:6 | 1 BAY BACK WALL | 100.D4
KA0364:2 | SC | VGENB | RED | 16 | 21.C1 | XT-9110:4 | 1 BAY BACK WALL | 100.D4
XT0341:1 | SC | VBUSB | RED | 16 | 21.D2 | XT-9113:4 | 1 BAY BACK WALL | 100.B4
XT0341:2 | SC | VBUSA | RED | 16 | 21.D2 | XT-9113:2 | 1 BAY BACK WALL | 100.B4
XT0341:3 | SC | VBUSC | RED | 16 | 21.D2 | XT-9113:6 | 1 BAY BACK WALL | 100.B4
XT0341:4 | SC | VGENB | RED | 16 | 21.D2 | XT-9110:4 | 1 BAY BACK WALL | 100.D4
XT0341:6 | SC | VGENC | RED | 16 | 21.D2 | XT-9110:6 | 1 BAY BACK WALL | 100.D4
XT0341:7 | SC | VGENA | RED | 16 | 21.D2 | XT-9110:2 | 1 BAY BACK WALL | 100.D4
XT0342:2 | SC | MCTN | BLU | 16 | 21.B2 | XT-9127:4 | 1 BAY BACK WALL | 101.B4
XT0340:2 | W8164 | EXC1 | WHT | 16 | 20.A5 | RS0106:2 | 1 BAY BACK WALL | 20.A4
XT0340:3 | W8164 | EXC0 | BLK | 16 | 20.A5 | RS0106:4 | 1 BAY BACK WALL | 20.A4
XT0340:4 | W8164 | EXCS | SH | 16 | 20.A5 | XT0106:1 | 1 BAY BACK WALL | 20.A4
XT0340:5 | W8165 | EXC0 | WHT | 16 | 20.A5 | XT-9103:2 | 1 BAY BACK WALL | 102.C4
XT0340:6 | W8165 | EXC2 | BLK | 16 | 20.B5 | XT-9103:5 | 1 BAY BACK WALL | 102.C4
XT0340:7 | W8165 | EXCS | SH | 16 | 20.B5 | XT-9103:7 | 1 BAY BACK WALL | 102.C5
XT0340:2 | W8264 | EXC1 | WHT | 16 | 20.A5 | XT-9103:3 | 1 BAY BACK WALL | 102.C5
XT0340:3 | W8264 | EXC0 | BLK | 16 | 20.A5 | XT-9103:2 | 1 BAY BACK WALL | 102.C4
XT0340:4 | W8264 | EXCS | SH | 16 | 20.A5 | XT-9103:6 | 1 BAY BACK WALL | 102.C4
AT0140:3 EX-D(-) | SC | 0V | WHT | 16 | 104.C7 | XT0336:4 | 1 BAY RIGHT WALL | 24.D4
AT0140:4 EX-D(+) | SC | KA012314 | WHT | 16 | 104.C7 | KA0123:14 | 1 BAY RIGHT WALL | 24.B5
AT0140:BAT(-) 48 | SC | 0V | WHT | 16 | 25.C6 | XT0336:4 | 1 BAY RIGHT WALL | 24.D4
AT0140:BAT(+) 47 | SC | FU0334 | WHT | 16 | 25.C6 | XT0335:2 | 1 BAY RIGHT WALL | 24.B4
AT0140:FLT 29 | SC | KA0310A2 | WHT | 20 | 25.C6 | KA0310:A2 | 1 BAY RIGHT WALL | 24.B5
AT0140:FLT 30 | SC | 0V | WHT | 14 | 25.C6 | XT0336:4 | 1 BAY RIGHT WALL | 24.D4
AT0140:RD_RLY 31 | SC | KA0124A2 | WHT | 20 | 25.C6 | KA0124:A2 | 1 BAY RIGHT WALL | 27.C5
AT0140:RD_RLY 32 | SC | 0V | WHT | 14 | 25.C6 | XT0336:4 | 1 BAY RIGHT WALL | 24.D4
AT0220:3 EX-D(-) | SC | 0V | WHT | 16 | 104.D7 | XT0336:5 | 1 BAY RIGHT WALL | 24.D4
AT0220:4 EX-D(+) | SC | KA012614 | WHT | 16 | 104.D7 | KA0126:14 | 1 BAY RIGHT WALL | 24.A5
AT0220:BAT(-) 48 | SC | 0V | WHT | 16 | 25.D6 | XT0336:5 | 1 BAY RIGHT WALL | 24.D4
AT0220:BAT(+) 47 | SC | FU0335 | WHT | 16 | 25.D6 | XT0335:3 | 1 BAY RIGHT WALL | 24.A4
AT0220:FLT 29 | SC | KA0320A2 | WHT | 20 | 25.D6 | KA0320:A2 | 1 BAY RIGHT WALL | 24.A5
AT0220:FLT 30 | SC | 0V | WHT | 16 | 25.D6 | XT0336:5 | 1 BAY RIGHT WALL | 24.D4
AT0220:RD_RLY 31 | SC | KA0125A2 | WHT | 20 | 25.D6 | KA0125:A2 | 1 BAY RIGHT WALL | 27.C5
AT0220:RD_RLY 32 | SC | 0V | WHT | 16 | 25.D6 | XT0336:5 | 1 BAY RIGHT WALL | 24.D4
KA0364:11 | SC | KA0185A2 | WHT | 20 | 30.B5 | KA121B:A2 | 1 BAY RIGHT WALL | 30.B5
KA0364:14 | SC | 012127 | WHT | 20 | 30.B5 | AF0121:27 | 1 BAY RIGHT WALL | 30.A7
XT0343:1 | SC | KA018511 | WHT | 20 | 20.C5 | XT0337:4 | 1 BAY RIGHT WALL | 28.C3
XT0343:2 | SC | KA0333A1 | WHT | 20 | 20.C5 | XT0337:2 | 1 BAY RIGHT WALL | 28.B3
AT0220:54 EXC(+) | W8104 | KA0125-13 | WHT | 12 | 102.D7 | KA0125:13 | 1 BAY RIGHT WALL | 102.D6
AT0220:55 EXC(-) | W8104 | KA0125-43 | BLK | 12 | 102.D7 | KA0125:43 | 1 BAY RIGHT WALL | 102.D6
XT0124:2 | W8104 | EXCS | SH | 12 | 102.D6 | FW220:1 | 1 BAY RIGHT WALL | 102.D6
AT0140:54 EXC(+) | W8202 | KA0124-13 | WHT | 12 | 102.C7 | KA0124:13 | 1 BAY RIGHT WALL | 102.C6
AT0140:55 EXC(-) | W8202 | KA0124-43 | BLK | 12 | 102.C7 | KA0124:43 | 1 BAY RIGHT WALL | 102.C6
XT0124:1 | W8202 | EXCS | SH | 12 | 102.C6 | FW140:1 | 1 BAY RIGHT WALL | 102.C6
AT0220:49 PMG-A | W8203 | KA0323-3 | WHT | 12 | 102.C7 | KA0323:3 | 1 BAY RIGHT WALL | 102.B6
AT0220:50 PMG-B | W8203 | KA0323-6 | BLK | 12 | 102.C7 | KA0323:6 | 1 BAY RIGHT WALL | 102.B6
XT0313:2 | W8203 | PMGS | SH | 12 | 102.B6 | FW220:2 | 1 BAY RIGHT WALL | 102.B6
AT0140:49 PMG-A | W8301 | KA0313-3 | WHT | 12 | 102.B7 | KA0313:3 | 1 BAY RIGHT WALL | 102.B6
AT0140:50 PMG-B | W8301 | KA0313-6 | BLK | 12 | 102.B7 | KA0313:6 | 1 BAY RIGHT WALL | 102.B6
XT0313:1 | W8301 | PMGS | SH | 12 | 102.B6 | FW140:2 | 1 BAY RIGHT WALL | 102.B6
AT0140:P1 | WC0012 | AU0120L2 | ENET | CABLE | 3.B3 | AU0120:L2 | 1 BAY RIGHT WALL | 3.B2
XT0343:3 | SC | KA9602NC | WHT | 16 | 20.C5 | XT-9326A:2 | 2 BAY BACK RIGHT PANEL | 28.C2
XT0343:4 | SC | KA0330A1 | WHT | 20 | 20.C5 | XT-9326A:3 | 2 BAY BACK RIGHT PANEL | 28.B2
AT0220:P2 | WC0122 | AT0220P2 | ENET | CABLE | 3.B4 | AU0200:L1 | ASSEMBLY^CONTROL PANEL | 3.C2
XT0341:4 | SC | VGENB | RED | 16 | 21.D2 | PA0771:7 | METER PANEL | 21.C3
XT0342:1 | SC | PA07035 | BLU | 16 | 21.A2 | PA0703:5 | METER PANEL | 21.A4
XT0342:4 | SC | PA07716 | BLU | 16 | 21.C2 | PA0771:6 | METER PANEL | 21.C3
XT0340:5 | W8065 | EXC0 | RED | 20 | 20.A5 | PV0701:7 | METER PANEL | 20.A1
XT0340:6 | W8065 | EXC2 | BLK | 20 | 20.B5 | PV0701:8 | METER PANEL | 20.A1
XT0340:7 | W8065 | EXCS | SH | 20 | 20.B5 | FLOATING | METER PANEL | 20.B1
XT0341:1 | SC | VBUSB | RED | 16 | 21.D2 | SA0710:23 | SWITCH PANEL | 21.D5
XT0341:2 | SC | VBUSA | RED | 16 | 21.D2 | SA0710:12 | SWITCH PANEL | 21.D5
XT0341:2 | SC | VBUSA | RED | 16 | 21.D2 | HL0703: | SWITCH PANEL | 21.A5
XT0341:3 | SC | VBUSC | RED | 16 | 21.D2 | SA0710:14 | SWITCH PANEL | 21.D5
XT0341:3 | SC | VBUSC | RED | 16 | 21.D2 | HL0704: | SWITCH PANEL | 21.A5
XT0341:4 | SC | VGENB | RED | 16 | 21.D2 | SA0770:14 | SWITCH PANEL | 21.B6
XT0341:5 | SC | VGENB | RED | 16 | 21.D2 | SA0710:27 | SWITCH PANEL | 21.D5
XT0341:6 | SC | VGENC | RED | 16 | 21.D2 | SA0700:17 | SWITCH PANEL | 21.A5
XT0341:6 | SC | VGENC | RED | 16 | 21.D2 | SA0710:18 | SWITCH PANEL | 21.D5
XT0341:7 | SC | VGENA | RED | 16 | 21.D2 | SA0700:13 | SWITCH PANEL | 21.A5
XT0342:2 | SC | MCTN | BLU | 16 | 21.B2 | SA0740:21 | SWITCH PANEL | 21.B2
XT0342:3 | SC | SA074013 | BLU | 16 | 21.B3 | SA0740:13 | SWITCH PANEL | 21.B2
XT0343:1 | SC | KA018511 | WHT | 16 | 20.C5 | SA0700:23 | SWITCH PANEL | 20.C3
XT0343:2 | SC | KA0333A1 | WHT | 16 | 20.C5 | SA0701:15 | SWITCH PANEL | 20.C2
XT0343:3 | SC | KA9602NC | WHT | 16 | 20.C5 | HL0701:A+ | SWITCH PANEL | 20.C2
XT0343:4 | SC | KA0330A1 | WHT | 16 | 20.C5 | HL0702:A+ | SWITCH PANEL | 20.C2
Report date: 7/10/2025 2:58 PM |  |  |  |  | SolarTools ver. 24.0.84.26264 (Jun 3, 2025)

## 1 BAY RIGHT WALL
1 BAY RIGHT WALL
Project # | G9440
Project Name | NOC AL SHAHEEN T130
Revision | A.5
Controls DE | G. Colby
Phone:
Controls ME | R. Duran
Phone:
From | [5 empty] | To
Device ID | Cable (W) Conductor (SC) Jumper Clip (JC) | Wire No. | Wire ID | Gauge/Size | Page/Zone | Device ID | Location | Page/Zone
XT0031:2 | JC | 24V | CLIP | --- | 15.D5 | XT0031:1 | 1 BAY RIGHT WALL | 15.D5
XT0031:4 | JC | 0V | CLIP | --- | 15.D5 | XT0031:3 | 1 BAY RIGHT WALL | 15.D5
XT0032:1 | JC | 24V | CLIP | --- | 15.C5 | XT0032:2 | 1 BAY RIGHT WALL | 15.C5
XT0032:3 | JC | 0V | CLIP | --- | 15.C5 | XT0032:4 | 1 BAY RIGHT WALL | 15.C5
XT0085:3 | JC | 0V | CLIP | --- | 15.C6 | XT0085:4 | 1 BAY RIGHT WALL | 15.C6
XT0085:4 | JC | 0V | CLIP | --- | 15.C6 | XT0085:5 | 1 BAY RIGHT WALL | 15.C6
XT0120:1 | JC | 0V | CLIP | --- | 25.D1 | XT0120:2 | 1 BAY RIGHT WALL | 25.D1
XT0130:3 | JC | 0V | CLIP | --- | 25.A5 | XT0130:2 | 1 BAY RIGHT WALL | 25.A5
XT0336:2 | JC | 0V | CLIP | --- | 24.C4 | XT0336:3 | 1 BAY RIGHT WALL | 24.C4
XT0336:3 | JC | 0V | CLIP | --- | 24.C4 | XT0336:4 | 1 BAY RIGHT WALL | 24.D4
XT0336:4 | JC | 0V | CLIP | --- | 24.D4 | XT0336:5 | 1 BAY RIGHT WALL | 24.D4
AF0121:01 | SC | 012101 | WHT | 20 | 27.A7 | KA0121:A1 | 1 BAY RIGHT WALL | 27.A5
AF0121:03 | SC | 012103 | WHT | 20 | 27.A7 | KA0123:A1 | 1 BAY RIGHT WALL | 27.B5
AF0121:04 | SC | 012104 | WHT | 20 | 27.C7 | KA0124:A1 | 1 BAY RIGHT WALL | 27.C5
AF0121:05 | SC | 012105 | WHT | 20 | 27.C7 | KA0125:A1 | 1 BAY RIGHT WALL | 27.C5
AF0121:06 | SC | 012106 | WHT | 20 | 27.D7 | KA0126:A1 | 1 BAY RIGHT WALL | 27.D5
AF0121:08 | SC | 012108 | WHT | 20 | 27.B7 | KA0128:A1 | 1 BAY RIGHT WALL | 27.B5
AF0121:11 | SC | 012111 | WHT | 20 | 30.A7 | KA121B:A1 | 1 BAY RIGHT WALL | 30.B5
AF0121:14 | SC | KA033611 | WHT | 20 | 88.A7 | KA0336:11 | 1 BAY RIGHT WALL | 88.A5
AF0121:17 | SC | 012117 | WHT | 20 | 27.A7 | KA0121:A2 | 1 BAY RIGHT WALL | 27.A5
AF0121:19 | SC | 012119 | WHT | 20 | 27.A7 | KA0123:A2 | 1 BAY RIGHT WALL | 27.B5
AF0121:22 | SC | 012122 | WHT | 20 | 27.D7 | KA0126:A2 | 1 BAY RIGHT WALL | 27.D5
AF0121:24 | SC | 012124 | WHT | 20 | 27.B7 | KA0128:A2 | 1 BAY RIGHT WALL | 27.B5
AF0121:COM | SC | 0V | WHT | 14 | 25.D2 | XT0120:2 | 1 BAY RIGHT WALL | 25.D1
AF0121:J | SC | * |  |  | 25.D2 | AF0122:P | 1 BAY RIGHT WALL | 25.D3
AF0121:P | SC | * |  |  | 25.D2 | AU0120:J | 1 BAY RIGHT WALL | 25.C1
AF0121:V+ | SC | FU0121 | WHT | 14 | 25.D2 | FU0121:LD | 1 BAY RIGHT WALL | 25.D1
AF0122:00 | SC | 012200 | WHT | 20 | 29.A7 | KA0330:11 | 1 BAY RIGHT WALL | 29.A6
AF0122:01 | SC | 012201 | WHT | 20 | 29.A7 | KA0331:11 | 1 BAY RIGHT WALL | 29.A6
AF0122:02 | SC | 012202 | WHT | 20 | 29.B7 | KA0310:11 | 1 BAY RIGHT WALL | 29.B6
AF0122:08 | SC | 012208 | WHT | 20 | 29.B7 | KA0320:11 | 1 BAY RIGHT WALL | 29.B6
AF0122:12 | SC | UJ0131OK2 | WHT | 20 | 15.B7 | UJ0131:OK2 | 1 BAY RIGHT WALL | 15.B4
AF0122:13 | SC | UJ0031OK2 | WHT | 20 | 15.D7 | UJ0031:OK2 | 1 BAY RIGHT WALL | 15.D4
AF0122:32 | SC | 012232 | WHT | 20 | 29.A7 | KA0330:14 | 1 BAY RIGHT WALL | 29.A6
AF0122:33 | SC | 012233 | WHT | 20 | 29.A7 | KA0331:14 | 1 BAY RIGHT WALL | 29.A6
AF0122:34 | SC | 012234 | WHT | 20 | 29.B7 | KA0310:14 | 1 BAY RIGHT WALL | 29.B6
AF0122:40 | SC | 012240 | WHT | 20 | 29.B7 | KA0320:14 | 1 BAY RIGHT WALL | 29.B6
AF0122:44 | SC | UJ0131OK1 | WHT | 20 | 15.B7 | UJ0131:OK1 | 1 BAY RIGHT WALL | 15.B4
AF0122:45 | SC | UJ0031OK1 | WHT | 20 | 15.D7 | UJ0031:OK1 | 1 BAY RIGHT WALL | 15.D4
AF0122:COM | SC | AF0122N | WHT | 16 | 25.D3 | AF0123:COM | 1 BAY RIGHT WALL | 25.D3
AF0122:COM | SC | AU0120N | WHT | 16 | 25.D3 | AU0120:COM | 1 BAY RIGHT WALL | 25.C1
AF0122:J | SC | * |  |  | 25.D3 | AF0123:P | 1 BAY RIGHT WALL | 25.D3
AF0122:V+ | SC | AF0122P | WHT | 16 | 25.D3 | AF0123:V+ | 1 BAY RIGHT WALL | 25.D3
AF0122:V+ | SC | AU0120P | WHT | 16 | 25.D3 | AU0120:V+ | 1 BAY RIGHT WALL | 25.C1
AF0123:00 | SC | 012300 | WHT | 20 | 15.B7 | XT0085:2 | 1 BAY RIGHT WALL | 15.C6
AF0123:01 | SC | 0V | WHT | 20 | 15.B7 | XT0085:3 | 1 BAY RIGHT WALL | 15.C6
AF0123:04 | SC | UJ0131VIN | WHT | 20 | 15.A7 | UJ0131:VIN | 1 BAY RIGHT WALL | 15.B4
AF0123:05 | SC | 0V | WHT | 20 | 15.A7 | AF0123:09 | 1 BAY RIGHT WALL | 15.C7
AF0123:05 | SC | 0V | WHT | 20 | 15.A7 | XT0085:4 | 1 BAY RIGHT WALL | 15.C6
AF0123:06 | SC | UJ0131IOUT | WHT | 20 | 15.B7 | UJ0131:IOUT | 1 BAY RIGHT WALL | 15.B4
AF0123:07 | SC | 0V | WHT | 20 | 15.B7 | AF0123:11 | 1 BAY RIGHT WALL | 15.C7
AF0123:07 | SC | 0V | WHT | 20 | 15.B7 | XT0085:5 | 1 BAY RIGHT WALL | 15.C6
AF0123:08 | SC | UJ0031VIN | WHT | 20 | 15.C7 | UJ0031:VIN | 1 BAY RIGHT WALL | 15.D4
AF0123:10 | SC | UJ0031IOUT | WHT | 20 | 15.C7 | UJ0031:IOUT | 1 BAY RIGHT WALL | 15.D4
AF0123:SH | SC | IEG8130-2 | GRN | 14 | 25.D3 | IEG8130:2 | 1 BAY RIGHT WALL | 25.D5
AU0120:COM | SC | 0V | WHT | 14 | 25.C1 | XT0120:1 | 1 BAY RIGHT WALL | 25.D1
AU0120:V+ | SC | FU0120 | WHT | 14 | 25.C1 | FU0120:LD | 1 BAY RIGHT WALL | 25.D1
FU0031:LD | SC | 24V | WHT | 10 | 15.D5 | XT0031:1 | 1 BAY RIGHT WALL | 15.D5
FU0031:LI | SC | 24V2 | WHT | 10 | 15.D5 | UJ0031:OUT(+) | 1 BAY RIGHT WALL | 15.D4
FU0032:LD | SC | 24V | WHT | 10 | 15.C5 | XT0032:1 | 1 BAY RIGHT WALL | 15.C5
FU0032:LI | SC | 24V1 | WHT | 10 | 15.C5 | UJ0131:OUT(+) | 1 BAY RIGHT WALL | 15.B4
FU0120:LI | SC | FU0332 | WHT | 14 | 25.D1 | XT0130:1 | 1 BAY RIGHT WALL | 25.A5
FU0120:LI | SC | FU0332 | WHT | 14 | 25.D1 | FU0121:LI | 1 BAY RIGHT WALL | 25.D1
FU0332:LD | SC | FU0332 | WHT | 14 | 24.B3 | XT0130:1 | 1 BAY RIGHT WALL | 25.A5
FU0332:LD | SC | FU0332 | WHT | 14 | 24.B3 | FU0333:LI | 1 BAY RIGHT WALL | 24.B3
FU0332:LI | SC | FU0136 | WHT | 12 | 24.B3 | XT0332:1 | 1 BAY RIGHT WALL | 24.B2
FU0333:LD | SC | FU0333 | WHT | 16 | 24.B3 | XT0335:1 | 1 BAY RIGHT WALL | 24.B4
FU0333:LI | SC | FU0332 | WHT | 14 | 24.B3 | FU0334:LI | 1 BAY RIGHT WALL | 24.B3
FU0334:LD | SC | FU0334 | WHT | 14 | 24.B3 | XT0335:2 | 1 BAY RIGHT WALL | 24.B4
FU0334:LI | SC | FU0332 | WHT | 14 | 24.B3 | FU0335:LI | 1 BAY RIGHT WALL | 24.A3
FU0335:LD | SC | FU0335 | WHT | 14 | 24.A3 | XT0335:3 | 1 BAY RIGHT WALL | 24.A4
GR8131: | SC | IEG8130-1 | GRN | 14 | 4.B4 | IEG8130:1 | 1 BAY RIGHT WALL | 4.B3
GR9131: | SC | GR9131 | GRN/YEL | 14 | 4.B4 | FG0002:1 | 1 BAY RIGHT WALL | 4.B3
GR9132: | SC | GR9132 | GRN/YEL | 14 | 4.B4 | FRAME | 1 BAY RIGHT WALL | 4.B4
GR9133: | SC | GR9133 | GRN/YEL | 14 | 4.B5 | FRAME | 1 BAY RIGHT WALL | 4.B5
KA0121:11 | SC | KA018511 | WHT | 20 | 28.C4 | XT0337:4 | 1 BAY RIGHT WALL | 28.C3
KA0121:14 | SC | FU0333 | WHT | 20 | 28.C4 | XT0337:3 | 1 BAY RIGHT WALL | 28.C3
KA0123:11 | SC | FU0334 | WHT | 20 | 24.B5 | XT0335:2 | 1 BAY RIGHT WALL | 24.B4
KA0123:A1 | SC | 012103 | WHT | 20 | 27.B5 | KA0313:2 | 1 BAY RIGHT WALL | 27.A5
KA0123:A2 | SC | 012119 | WHT | 20 | 27.B5 | KA0313:7 | 1 BAY RIGHT WALL | 27.A5
KA0126:11 | SC | FU0335 | WHT | 16 | 24.A5 | XT0335:3 | 1 BAY RIGHT WALL | 24.A4
KA0126:A1 | SC | 012106 | WHT | 20 | 27.D5 | KA0323:2 | 1 BAY RIGHT WALL | 27.D5
KA0126:A2 | SC | 012122 | WHT | 20 | 27.D5 | KA0323:7 | 1 BAY RIGHT WALL | 27.D5
KA0128:11 | SC | KA0333A1 | WHT | 20 | 28.B4 | KA0335:21 | 1 BAY RIGHT WALL | 28.B4
KA0128:14 | SC | FU0333 | WHT | 20 | 28.B4 | KA0335:22 | 1 BAY RIGHT WALL | 28.B4
KA0128:14 | SC | FU0333 | WHT | 20 | 28.B4 | XT0337:1 | 1 BAY RIGHT WALL | 28.B3
KA0310:21 | SC | KA0333A1 | WHT | 20 | 28.B4 | KA0335:21 | 1 BAY RIGHT WALL | 28.B4
KA0310:21 | SC | KA0333A1 | WHT | 20 | 28.B4 | XT0337:2 | 1 BAY RIGHT WALL | 28.B3
KA0310:24 | SC | KA031024 | WHT | 20 | 28.B4 | KA0320:21 | 1 BAY RIGHT WALL | 28.B5
KA0310:A1 | SC | FU0334 | WHT | 20 | 24.B5 | XT0335:2 | 1 BAY RIGHT WALL | 24.B4
KA0313:2 | SC | 012103 | WHT | 20 | 27.A5 | KA0314:2 | 1 BAY RIGHT WALL | 27.A5
KA0313:7 | SC | 012119 | WHT | 20 | 27.A5 | KA0314:7 | 1 BAY RIGHT WALL | 27.A5
KA0320:24 | SC | FU0333 | WHT | 20 | 28.B5 | KA0335:22 | 1 BAY RIGHT WALL | 28.B4
KA0320:A1 | SC | FU0335 | WHT | 20 | 24.A5 | XT0335:3 | 1 BAY RIGHT WALL | 24.A4
KA0323:2 | SC | 012106 | WHT | 20 | 27.D5 | KA0324:2 | 1 BAY RIGHT WALL | 27.D5
KA0323:7 | SC | 012122 | WHT | 20 | 27.D5 | KA0324:7 | 1 BAY RIGHT WALL | 27.D5
KA0330:A2 | SC | 0V | WHT | 20 | 28.B6 | KA0333:A2 | 1 BAY RIGHT WALL | 28.B6
KA0330:A2 | SC | 0V | WHT | 20 | 28.B6 | KA0331:A2 | 1 BAY RIGHT WALL | 28.C6
KA0331:A2 | SC | 0V | WHT | 20 | 28.C6 | KA0332:A2 | 1 BAY RIGHT WALL | 28.C6
KA0332:A1 | SC | KA0332A1 | WHT | 20 | 28.C6 | XT0337:5 | 1 BAY RIGHT WALL | 28.C3
KA0332:A2 | SC | 0V | WHT | 20 | 28.C6 | XT0337:6 | 1 BAY RIGHT WALL | 28.D3
KA0333:11 | SC | KA0333-11 | WHT | 20 | 29.D6 | KA0335:11 | 1 BAY RIGHT WALL | 29.D6
KA0333:14 | SC | KA0333-14 | WHT | 20 | 29.D6 | KA0335:12 | 1 BAY RIGHT WALL | 29.D6
KA0333:21 | SC | KA0333-21 | WHT | 20 | 29.D6 | KA0337:11 | 1 BAY RIGHT WALL | 29.D6
KA0333:24 | SC | KA0333-24 | WHT | 20 | 29.D6 | KA0337:12 | 1 BAY RIGHT WALL | 29.D6
KA0333:A1 | SC | KA0333A1 | WHT | 20 | 28.B6 | XT0337:2 | 1 BAY RIGHT WALL | 28.B3
KA0335:A1 | SC | ESTOP | WHT | 20 | 24.C5 | KA0337:A1 | 1 BAY RIGHT WALL | 24.C5
KA0335:A1 | SC | ESTOP | WHT | 20 | 24.C5 | XT0336:1 | 1 BAY RIGHT WALL | 24.C4
KA0335:A2 | SC | 0V | WHT | 20 | 24.C5 | KA0337:A2 | 1 BAY RIGHT WALL | 24.C5
KA0335:A2 | SC | 0V | WHT | 20 | 24.C5 | XT0336:2 | 1 BAY RIGHT WALL | 24.C4
KA0336:A1 | SC | KA0231A1 | WHT | 14 | 24.C3 | XT0334:2 | 1 BAY RIGHT WALL | 24.C2
KA0336:A2 | SC | 0V | WHT | 14 | 24.C3 | XT0336:2 | 1 BAY RIGHT WALL | 24.C4
KA121B:11 | SC | KA018511 | WHT | 20 | 28.C3 | XT0337:4 | 1 BAY RIGHT WALL | 28.C3
KA121B:14 | SC | KA0332A1 | WHT | 20 | 28.C3 | XT0337:5 | 1 BAY RIGHT WALL | 28.C3
PEG0130:11 | SC | EXCS | GRN/YEL | 12 | 102.D6 | XT0124:1 | 1 BAY RIGHT WALL | 102.C6
PEG0130:12 | SC | EXCS | GRN/YEL | 12 | 102.D6 | XT0124:2 | 1 BAY RIGHT WALL | 102.D6
PEG0130:13 | SC | PMGS | GRN/YEL | 12 | 102.B6 | XT0313:1 | 1 BAY RIGHT WALL | 102.B6
PEG0130:14 | SC | PMGS | GRN/YEL | 12 | 102.C6 | XT0313:2 | 1 BAY RIGHT WALL | 102.B6
QS0031:LD-1 | SC | UJ0031P | WHT | 12 | 15.D3 | UJ0031:+ | 1 BAY RIGHT WALL | 15.D4
QS0031:LD-3 | SC | UJ0031N | WHT | 12 | 15.D3 | UJ0031:- | 1 BAY RIGHT WALL | 15.D4
QS0131:LD-1 | SC | UJ0131P | WHT | 12 | 15.B3 | UJ0131:+ | 1 BAY RIGHT WALL | 15.B4
QS0131:LD-3 | SC | UJ0131N | WHT | 12 | 15.B3 | UJ0131:- | 1 BAY RIGHT WALL | 15.B4
RR0851: -3.01K OHM | SC | 012300 | LEAD | --- | 15.C6 | XT0085:2 | 1 BAY RIGHT WALL | 15.C6
RR0851: -3.01K OHM | SC | 24V | LEAD | --- | 15.C6 | XT0085:1 | 1 BAY RIGHT WALL | 15.C6
RR0852: -1.0K OHM | SC | 012300 | LEAD | --- | 15.C6 | XT0085:2 | 1 BAY RIGHT WALL | 15.C6
RR0852: -1.0K OHM | SC | 0V | LEAD | --- | 15.C6 | XT0085:3 | 1 BAY RIGHT WALL | 15.C6
UJ0031:G | SC | UJ0031G | GRN/YEL | 12 | 15.D4 | FRAME | 1 BAY RIGHT WALL | 15.D4
UJ0031:IS | SC | UJ0131IS |  |  | 15.D4 | UJ0131:IS | 1 BAY RIGHT WALL | 15.B4
UJ0031:OUT(-) | SC | 0V | WHT | 10 | 15.D4 | XT0031:4 | 1 BAY RIGHT WALL | 15.D5
UJ0131:G | SC | UJ0131G | GRN/YEL | 12 | 15.B4 | FRAME | 1 BAY RIGHT WALL | 15.B4
UJ0131:OUT(-) | SC | 0V | WHT | 10 | 15.B4 | XT0032:3 | 1 BAY RIGHT WALL | 15.C5
XT0032:1 | SC | 24V | WHT | 12 | 15.C5 | XT0085:1 | 1 BAY RIGHT WALL | 15.C6
XT0032:2 | SC | 24V | WHT | 10 | 15.C5 | XT0031:2 | 1 BAY RIGHT WALL | 15.D5
XT0032:3 | SC | 0V | WHT | 12 | 15.C5 | XT0085:3 | 1 BAY RIGHT WALL | 15.C6
XT0032:4 | SC | 0V | WHT | 10 | 15.C5 | XT0031:3 | 1 BAY RIGHT WALL | 15.D5
XT0120:1 | SC | 0V | WHT | 14 | 25.D1 | XT0130:2 | 1 BAY RIGHT WALL | 25.A5
XT0130:2 | SC | 0V | WHT | 14 | 25.A5 | XT0336:3 | 1 BAY RIGHT WALL | 24.C4
XT0334:1 | SC | 0V | WHT | 12 | 24.C2 | XT0336:2 | 1 BAY RIGHT WALL | 24.C4
XT0335:1 | SC | FU0333 | WHT | 16 | 24.B4 | XT0337:3 | 1 BAY RIGHT WALL | 28.C3
XT0336:3 | SC | 0V | WHT | 14 | 24.C4 | XT0337:6 | 1 BAY RIGHT WALL | 28.D3
XT0337:1 | SC | FU0333 | WHT | 20 | 28.B3 | XT0337:3 | 1 BAY RIGHT WALL | 28.C3
FU0321:LD | W8103 | FU0321 | WHT | 12 | 102.B5 | KA0323:1 | 1 BAY RIGHT WALL | 102.B6
FU0322:LD | W8103 | FU0322 | BLK | 12 | 102.B5 | KA0323:8 | 1 BAY RIGHT WALL | 102.B6
XT0360:2 | W8103 | PMGS | SH | 12 | 102.B5 | XT0313:2 | 1 BAY RIGHT WALL | 102.B6
FU0313:LD | W8201 | FU0313 | WHT | 12 | 102.B5 | KA0313:1 | 1 BAY RIGHT WALL | 102.B6
FU0314:LD | W8201 | FU0314 | BLK | 12 | 102.B5 | KA0313:8 | 1 BAY RIGHT WALL | 102.B6
XT0360:1 | W8201 | PMGS | SH | 12 | 102.B5 | XT0313:1 | 1 BAY RIGHT WALL | 102.B6
AF0121:10 | SC | 012110 | WHT | 20 | 30.A7 | KA121A:A1 | 1 BAY BACK WALL | 30.A5
AF0121:13 | SC | 012113 | WHT | 20 | 87.B7 | KA3420:A1 | 1 BAY BACK WALL | 87.B5
AF0121:15 | SC | 012115 | WHT | 20 | 96.C7 | KA3103:A1 | 1 BAY BACK WALL | 96.C6
AF0121:26 | SC | 012126 | WHT | 20 | 30.A7 | KA121A:A2 | 1 BAY BACK WALL | 30.A5
AF0121:28 | SC | 012128 | WHT | 20 | 63.C7 | KA121C:A2 | 1 BAY BACK WALL | 63.C6
AF0121:29 | SC | 012129 | WHT | 20 | 87.B7 | KA3420:A2 | 1 BAY BACK WALL | 87.B5
AF0121:30 | SC | 012130 | WHT | 20 | 88.A7 | KA4100:A2 | 1 BAY BACK WALL | 88.A6
AF0121:31 | SC | 012131 | WHT | 20 | 96.C7 | KA3103:A2 | 1 BAY BACK WALL | 96.C6
KA0128:21 | SC | KA0128-21 | WHT | 20 | 29.C6 | XT-9107:5 | 1 BAY BACK WALL | 29.C4
KA0128:24 | SC | KA0128-24 | WHT | 20 | 29.C6 | XT-9107:6 | 1 BAY BACK WALL | 29.C4
KA0332:11 | SC | KA0332-11 | WHT | 20 | 29.C6 | XT-9107:1 | 1 BAY BACK WALL | 29.C4
KA0332:14 | SC | KA0332-14 | WHT | 20 | 29.C6 | XT-9107:2 | 1 BAY BACK WALL | 29.C4
KA0333:11 | SC | KA0333-11 | WHT | 20 | 29.D6 | XT-9107:3 | 1 BAY BACK WALL | 29.D4
KA0333:14 | SC | KA0333-14 | WHT | 20 | 29.D6 | XT-9107:4 | 1 BAY BACK WALL | 29.D4
KA0333:21 | SC | KA0333-21 | WHT | 20 | 29.D6 | XT-9107:9 | 1 BAY BACK WALL | 29.D4
KA0333:24 | SC | KA0333-24 | WHT | 20 | 29.D6 | XT-9107:10 | 1 BAY BACK WALL | 29.D4
KA0336:14 | SC | KA033614 | WHT | 20 | 88.A5 | KA4100:A1 | 1 BAY BACK WALL | 88.A6
PEG0130:10 | SC | PEG013010 | GRN/YEL | 12 | 101.B5 | XT-9127:5 | 1 BAY BACK WALL | 101.B4
FU0321:LI | W8003 | PMG1 | WHT | 12 | 102.B5 | XT-9104:1 | 1 BAY BACK WALL | 102.B4
FU0322:LI | W8003 | PMG2 | BLK | 12 | 102.B5 | XT-9104:2 | 1 BAY BACK WALL | 102.B4
XT0360:2 | W8003 | PMGS | SH | 12 | 102.B5 | XT-9104:3 | 1 BAY BACK WALL | 102.B4
KA0125:14 | W8004 | EXC1 | WHT | 12 | 102.D6 | XT-9103:3 | 1 BAY BACK WALL | 102.C5
KA0125:44 | W8004 | EXC2 | BLK | 12 | 102.D6 | XT-9103:4 | 1 BAY BACK WALL | 102.C5
XT0124:2 | W8004 | EXCS | SH | 12 | 102.D6 | XT-9103:7 | 1 BAY BACK WALL | 102.C5
FU0313:LI | W8101 | PMG1 | WHT | 12 | 102.B5 | XT-9104:1 | 1 BAY BACK WALL | 102.B4
FU0314:LI | W8101 | PMG2 | BLK | 12 | 102.B5 | XT-9104:2 | 1 BAY BACK WALL | 102.B4
XT0360:1 | W8101 | PMGS | SH | 12 | 102.B5 | XT-9104:3 | 1 BAY BACK WALL | 102.B4
KA0124:14 | W8102 | EXC1 | WHT | 12 | 102.C6 | XT-9103:3 | 1 BAY BACK WALL | 102.C5
KA0124:44 | W8102 | EXC2 | BLK | 12 | 102.C6 | XT-9103:4 | 1 BAY BACK WALL | 102.C5
XT0124:1 | W8102 | EXCS | SH | 12 | 102.C6 | XT-9103:7 | 1 BAY BACK WALL | 102.C5
AF0121:27 | SC | 012127 | WHT | 20 | 30.A7 | KA0364:14 | 1 BAY LEFT WALL | 30.B5
KA0123:14 | SC | KA012314 | WHT | 16 | 24.B5 | AT0140:4 EX-D(+) | 1 BAY LEFT WALL | 104.C7
KA0124:A2 | SC | KA0124A2 | WHT | 20 | 27.C5 | AT0140:RD_RLY 31 | 1 BAY LEFT WALL | 25.C6
KA0125:A2 | SC | KA0125A2 | WHT | 20 | 27.C5 | AT0220:RD_RLY 31 | 1 BAY LEFT WALL | 25.D6
KA0126:14 | SC | KA012614 | WHT | 16 | 24.A5 | AT0220:4 EX-D(+) | 1 BAY LEFT WALL | 104.D7
KA0310:A2 | SC | KA0310A2 | WHT | 20 | 24.B5 | AT0140:FLT 29 | 1 BAY LEFT WALL | 25.C6
KA0320:A2 | SC | KA0320A2 | WHT | 20 | 24.A5 | AT0220:FLT 29 | 1 BAY LEFT WALL | 25.D6
KA121B:A2 | SC | KA0185A2 | WHT | 20 | 30.B5 | KA0364:11 | 1 BAY LEFT WALL | 30.B5
XT0335:2 | SC | FU0334 | WHT | 16 | 24.B4 | AT0140:BAT(+) 47 | 1 BAY LEFT WALL | 25.C6
XT0335:3 | SC | FU0335 | WHT | 16 | 24.A4 | AT0220:BAT(+) 47 | 1 BAY LEFT WALL | 25.D6
XT0336:4 | SC | 0V | WHT | 14 | 24.D4 | AT0140:RD_RLY 32 | 1 BAY LEFT WALL | 25.C6
XT0336:4 | SC | 0V | WHT | 14 | 24.D4 | AT0140:FLT 30 | 1 BAY LEFT WALL | 25.C6
XT0336:4 | SC | 0V | WHT | 16 | 24.D4 | AT0140:3 EX-D(-) | 1 BAY LEFT WALL | 104.C7
XT0336:4 | SC | 0V | WHT | 16 | 24.D4 | AT0140:BAT(-) 48 | 1 BAY LEFT WALL | 25.C6
XT0336:5 | SC | 0V | WHT | 16 | 24.D4 | AT0220:3 EX-D(-) | 1 BAY LEFT WALL | 104.D7
XT0336:5 | SC | 0V | WHT | 16 | 24.D4 | AT0220:RD_RLY 32 | 1 BAY LEFT WALL | 25.D6
XT0336:5 | SC | 0V | WHT | 16 | 24.D4 | AT0220:BAT(-) 48 | 1 BAY LEFT WALL | 25.D6
XT0336:5 | SC | 0V | WHT | 16 | 24.D4 | AT0220:FLT 30 | 1 BAY LEFT WALL | 25.D6
XT0337:2 | SC | KA0333A1 | WHT | 20 | 28.B3 | XT0343:2 | 1 BAY LEFT WALL | 20.C5
XT0337:4 | SC | KA018511 | WHT | 20 | 28.C3 | XT0343:1 | 1 BAY LEFT WALL | 20.C5
KA0125:13 | W8104 | KA0125-13 | WHT | 12 | 102.D6 | AT0220:54 EXC(+) | 1 BAY LEFT WALL | 102.D7
KA0125:43 | W8104 | KA0125-43 | BLK | 12 | 102.D6 | AT0220:55 EXC(-) | 1 BAY LEFT WALL | 102.D7
FW220:1 | W8104 | EXCS | SH | 12 | 102.D6 | XT0124:2 | 1 BAY LEFT WALL | 102.D6
KA0124:13 | W8202 | KA0124-13 | WHT | 12 | 102.C6 | AT0140:54 EXC(+) | 1 BAY LEFT WALL | 102.C7
KA0124:43 | W8202 | KA0124-43 | BLK | 12 | 102.C6 | AT0140:55 EXC(-) | 1 BAY LEFT WALL | 102.C7
FW140:1 | W8202 | EXCS | SH | 12 | 102.C6 | XT0124:1 | 1 BAY LEFT WALL | 102.C6
KA0323:3 | W8203 | KA0323-3 | WHT | 12 | 102.B6 | AT0220:49 PMG-A | 1 BAY LEFT WALL | 102.C7
KA0323:6 | W8203 | KA0323-6 | BLK | 12 | 102.B6 | AT0220:50 PMG-B | 1 BAY LEFT WALL | 102.C7
FW220:2 | W8203 | PMGS | SH | 12 | 102.B6 | XT0313:2 | 1 BAY LEFT WALL | 102.B6
KA0313:3 | W8301 | KA0313-3 | WHT | 12 | 102.B6 | AT0140:49 PMG-A | 1 BAY LEFT WALL | 102.B7
KA0313:6 | W8301 | KA0313-6 | BLK | 12 | 102.B6 | AT0140:50 PMG-B | 1 BAY LEFT WALL | 102.B7
FW140:2 | W8301 | PMGS | SH | 12 | 102.B6 | XT0313:1 | 1 BAY LEFT WALL | 102.B6
AU0120:L2 | WC0012 | AU0120L2 | ENET | CABLE | 3.B2 | AT0140:P1 | 1 BAY LEFT WALL | 3.B3
AF0122:03 | SC | KA96002 | WHT | 20 | 28.A7 | XT-9326A:5 | 2 BAY BACK RIGHT PANEL | 28.A2
AF0122:04 | SC | KA96012 | WHT | 20 | 28.A7 | XT-9326A:7 | 2 BAY BACK RIGHT PANEL | 28.A2
AF0122:06 | SC | 012207 | WHT | 20 | 31.B7 | XT-9300:8 | 2 BAY BACK RIGHT PANEL | 31.B4
AF0122:35 | SC | KA96001 | WHT | 20 | 28.A7 | XT-9326A:4 | 2 BAY BACK RIGHT PANEL | 28.A2
AF0122:36 | SC | KA96011 | WHT | 20 | 28.A7 | XT-9326A:6 | 2 BAY BACK RIGHT PANEL | 28.A2
AF0122:38 | SC | 012239 | WHT | 20 | 31.B7 | XT-9300:7 | 2 BAY BACK RIGHT PANEL | 31.B4
KA0330:A1 | SC | KA0330A1 | WHT | 20 | 28.B6 | XT-9326A:3 | 2 BAY BACK RIGHT PANEL | 28.B2
KA0331:A1 | SC | KA0331A1 | WHT | 20 | 28.C6 | XT-9326A:8 | 2 BAY BACK RIGHT PANEL | 28.C2
XT0337:1 | SC | FU0333 | WHT | 20 | 28.B3 | XT-9326A:1 | 2 BAY BACK RIGHT PANEL | 28.B2
XT0337:3 | SC | FU0333 | WHT | 20 | 28.C3 | XT-9326A:9 | 2 BAY BACK RIGHT PANEL | 28.C2
AF0121:12 | SC | 012112 | WHT | 20 | 63.C7 | KA0239:11 | 2 BAY LEFT WALL | 63.C5
IEG8130:0 | SC | IEG8210-G | GRN | 8 | 4.B2 | IEG8210:00 | 2 BAY LEFT WALL | 4.B2
XT0031:2 | SC | 24V | WHT | 10 | 15.D5 | FU0136:LI | 2 BAY LEFT WALL | 16.A4
XT0031:3 | SC | 0V | WHT | 10 | 15.D5 | XT0134:1 | 2 BAY LEFT WALL | 16.B4
XT0332:1 | SC | FU0136 | WHT | 12 | 24.B2 | XT0138:3 | 2 BAY LEFT WALL | 16.A4
XT0334:1 | SC | 0V | WHT | 16 | 24.C2 | XT0134:3 | 2 BAY LEFT WALL | 16.B4
XT0334:2 | SC | KA0231A1 | WHT | 14 | 24.C2 | XT0136:10 | 2 BAY LEFT WALL | 17.B5
XT0336:1 | SC | ESTOP | WHT | 20 | 24.C4 | XT0240:5 | 2 BAY LEFT WALL | 18.B3
AU0120:L1 | WC0045 | AF0450L2 | ENET | CABLE | 3.B2 | AF0450:L2 | 2 BAY RIGHT WALL | 3.A5
AF0122:14 | SC | 012214 | WHT | 20 | 105.A7 | GF4000:A5 | CONSOLE DOOR^PANEL | 105.A6
AF0122:15 | SC | 012215 | WHT | 20 | 105.B7 | GF4000:A7 | CONSOLE DOOR^PANEL | 105.B6
AF0122:46 | SC | 012246 | WHT | 20 | 105.A7 | GF4000:A4 | CONSOLE DOOR^PANEL | 105.A6
AF0122:47 | SC | 012247 | WHT | 20 | 105.B7 | GF4000:A6 | CONSOLE DOOR^PANEL | 105.B6
PEG0130:1 | SC | PEG01301 | GRN/YEL | 14 | 23.C1 | UV0610:P.E. | ORBIT 60^DOOR PANEL | 23.B1
PEG0130:2 | SC | PEG01302 | GRN/YEL | 14 | 23.C2 | UV0611:P.E. | ORBIT 60^DOOR PANEL | 23.C1
XT0335:1 | SC | FU0333 | WHT | 16 | 24.B4 | SA0701:14 | SWITCH PANEL | 20.C2
XT0336:3 | SC | 0V | WHT | 16 | 24.C4 | HL0702:A | SWITCH PANEL | 20.C2
SolarTools ver. 24.0.84.26264 (Jun 3, 2025)
Report date: 7/10/2025 2:58 PM

## 2 BAY BACK LEFT WALL
2 BAY BACK LEFT WALL
Project # | G9440
Project Name | NOC AL SHAHEEN T130
Revision | A.5
Controls DE | G. Colby
Phone:
Controls ME | R. Duran
Phone:
From | [5 empty] | To
Device ID | Cable (W) Conductor (SC) Jumper Clip (JC) | Wire No. | Wire ID | Gauge/Size | Page/Zone | Device ID | Location | Page/Zone
XT-9216:5 | SC | JP100 | VIO | 20 | 34.C4 | XT-9216:4 | 2 BAY BACK LEFT WALL | 34.C4
GR9221: | SC | GR9221 | GRN/YEL | 14 | 4.C4 | FG0003:1 | 2 BAY BACK LEFT WALL | 4.C3
GR9222: | SC | GR9222 | GRN/YEL | 14 | 4.C4 | FG0004:1 | 2 BAY BACK LEFT WALL | 4.C4
GR9223: | SC | GR9223 | GRN/YEL | 14 | 4.C5 | FRAME | 2 BAY BACK LEFT WALL | 4.C5
GR9224: | SC | GR9224 | GRN/YEL | 14 | 4.C4 | FG0003:2 | 2 BAY BACK LEFT WALL | 4.C3
HIEG8220:1 | SC | HIEG8220-1 | GRN | 14 | 16.C1 | UV0281:IE | 2 BAY BACK LEFT WALL | 16.C1
HIEG8220:2 | SC | HIEG8220-2 | GRN | 14 | 16.C1 | UV0282:IE | 2 BAY BACK LEFT WALL | 16.C1
HIEG8220:3 | SC | HIEG8220-3 | GRN | 14 | 16.D1 | UV0291:IE | 2 BAY BACK LEFT WALL | 16.D1
HIEG8220:4 | SC | HIEG8220-4 | GRN | 14 | 16.D1 | UV0292:IE | 2 BAY BACK LEFT WALL | 16.D1
UAI9221-1:1 | SC | TE42103 | WHT | 20 | 85.A5 | UAI9221-1:2 | 2 BAY BACK LEFT WALL | 85.A5
UAI9221-2:1 | SC | TE42133 | WHT | 20 | 85.B5 | UAI9221-2:2 | 2 BAY BACK LEFT WALL | 85.B5
UAI9221-3:1 | SC | TE42163 | WHT | 20 | 85.C5 | UAI9221-3:2 | 2 BAY BACK LEFT WALL | 85.C5
UAI9221-4:1 | SC | TE4230-3 | WHT | 20 | 86.B5 | UAI9221-4:2 | 2 BAY BACK LEFT WALL | 86.B5
UAI9221-5:1 | SC | TE4240-3 | WHT | 20 | 86.A5 | UAI9221-5:2 | 2 BAY BACK LEFT WALL | 86.A5
UAI9221A-1:1 | SC | TE3630-3 | WHT | 20 | 99.B5 | UAI9221A-1:2 | 2 BAY BACK LEFT WALL | 99.B5
UAI9222A-1:1 | SC | TE3620-3 | WHT | 20 | 99.A5 | UAI9222A-1:2 | 2 BAY BACK LEFT WALL | 99.A5
UV0281:11+ | SC | UV028118 | WHT | 16 | 16.C1 | UV0282:8+ | 2 BAY BACK LEFT WALL | 16.C1
UV0281:12- | SC | UV02819 | WHT | 16 | 16.C1 | UV0282:9- | 2 BAY BACK LEFT WALL | 16.C1
UV0291:11+ | SC | UV029118 | WHT | 16 | 16.D1 | UV0292:8+ | 2 BAY BACK LEFT WALL | 16.D1
UV0291:12- | SC | UV02919 | WHT | 16 | 16.D1 | UV0292:9- | 2 BAY BACK LEFT WALL | 16.D1
UAI9219A-1:1+ | WI0554 | UA2611-1 | RED | 20 | 78.B5 | XT-9219A:1 | 2 BAY BACK LEFT WALL | 78.B4
UAI9219A-1:3 | WI0554 | UA2611-2 | BLK | 20 | 78.B5 | XT-9219A:2 | 2 BAY BACK LEFT WALL | 78.C4
UAI9219A-1:IE | WI0554 | UA2611-S | SH | 20 | 78.B5 | XT-9219A:3 | 2 BAY BACK LEFT WALL | 78.C4
UAI9212-1:1+ | WI0556 | PT2225-1 | RED | 20 | 64.A5 | XT-9212:1 | 2 BAY BACK LEFT WALL | 64.A4
UAI9212-1:3 | WI0556 | PT2225-2 | BLK | 20 | 64.A5 | XT-9212:2 | 2 BAY BACK LEFT WALL | 64.A4
UAI9212-1:IE | WI0556 | PT2225-S | SH | 20 | 64.A5 | XT-9212:3 | 2 BAY BACK LEFT WALL | 64.A4
UAI9242-1:1+ | WI0557 | PT6402-1 | RED | 20 | 75.A5 | XT-9242:1 | 2 BAY BACK LEFT WALL | 75.A4
UAI9242-1:3 | WI0557 | PT6402-2 | BLK | 20 | 75.A5 | XT-9242:2 | 2 BAY BACK LEFT WALL | 75.A4
UAI9242-1:IE | WI0557 | PT6402-S | SH | 20 | 75.A5 | XT-9242:3 | 2 BAY BACK LEFT WALL | 75.A4
UAI9212-2:1+ | WI0560 | PT2220-1 | RED | 20 | 69.A5 | XT-9212:4 | 2 BAY BACK LEFT WALL | 69.A4
UAI9212-2:3 | WI0560 | PT2220-2 | BLK | 20 | 69.A5 | XT-9212:5 | 2 BAY BACK LEFT WALL | 69.A4
UAI9212-2:IE | WI0560 | PT2220-S | SH | 20 | 69.A5 | XT-9212:6 | 2 BAY BACK LEFT WALL | 69.A4
UAI9218-6:1+ | WI0561 | PT2230-1 | RED | 20 | 80.A5 | XT-9218:16 | 2 BAY BACK LEFT WALL | 80.A4
UAI9218-6:3 | WI0561 | PT2230-2 | BLK | 20 | 80.A5 | XT-9218:17 | 2 BAY BACK LEFT WALL | 80.A4
UAI9218-6:IE | WI0561 | PT2230-S | SH | 20 | 80.A5 | XT-9218:18 | 2 BAY BACK LEFT WALL | 80.A4
UAI9218-7:1+ | WI0562 | PT2240-1 | RED | 20 | 73.A5 | XT-9218:19 | 2 BAY BACK LEFT WALL | 73.A4
UAI9218-7:3 | WI0562 | PT2240-2 | BLK | 20 | 73.A5 | XT-9218:20 | 2 BAY BACK LEFT WALL | 73.A4
UAI9218-7:IE | WI0562 | PT2240-S | SH | 20 | 73.A5 | XT-9218:21 | 2 BAY BACK LEFT WALL | 73.A4
UAI9211-1:1+ | WI0563 | PT2645-1 | RED | 20 | 77.B5 | XT-9211:1 | 2 BAY BACK LEFT WALL | 77.B4
UAI9211-1:3 | WI0563 | PT2645-2 | BLK | 20 | 77.B5 | XT-9211:2 | 2 BAY BACK LEFT WALL | 77.B4
UAI9211-1:IE | WI0563 | PT2645-S | SH | 20 | 77.B5 | XT-9211:3 | 2 BAY BACK LEFT WALL | 77.B4
UAI9219-1:1+ | WI0565 | PDT2201-1 | RED | 20 | 65.A5 | XT-9219:1 | 2 BAY BACK LEFT WALL | 65.A4
UAI9219-1:3 | WI0565 | PDT2201-2 | BLK | 20 | 65.A5 | XT-9219:2 | 2 BAY BACK LEFT WALL | 65.A4
UAI9219-1:IE | WI0565 | PDT2201-S | SH | 20 | 65.A5 | XT-9219:3 | 2 BAY BACK LEFT WALL | 65.A4
UAI9217-6:1+ | WI0640 | PT2121-1 | RED | 20 | 56.A5 | XT-9217:16 | 2 BAY BACK LEFT WALL | 56.A4
UAI9217-6:3 | WI0640 | PT2121-2 | BLK | 20 | 56.A5 | XT-9217:17 | 2 BAY BACK LEFT WALL | 56.A4
UAI9217-6:IE | WI0640 | PT2121-S | SH | 20 | 56.A5 | XT-9217:18 | 2 BAY BACK LEFT WALL | 56.A4
UAI9290-4:1+ | WI0641 | PT2130-1 | RED | 20 | 56.C5 | XT-9290:10 | 2 BAY BACK LEFT WALL | 56.C4
UAI9290-4:3 | WI0641 | PT2130-2 | BLK | 20 | 56.C5 | XT-9290:11 | 2 BAY BACK LEFT WALL | 56.C4
UAI9290-4:IE | WI0641 | PT2130-S | SH | 20 | 56.C5 | XT-9290:12 | 2 BAY BACK LEFT WALL | 56.C4
UAI9290-6:1+ | WI0642 | PT21401 | RED | 20 | 58.A5 | XT-9290:16 | 2 BAY BACK LEFT WALL | 58.A4
UAI9290-6:3 | WI0642 | PT21402 | BLK | 20 | 58.A5 | XT-9290:17 | 2 BAY BACK LEFT WALL | 58.A4
UAI9290-6:IE | WI0642 | PT2140S | SH | 20 | 58.A5 | XT-9290:18 | 2 BAY BACK LEFT WALL | 58.A4
UAI9217-1:1+ | WI0650 | PT1120-1 | RED | 20 | 50.A5 | XT-9217:1 | 2 BAY BACK LEFT WALL | 50.A4
UAI9217-1:3 | WI0650 | PT1120-2 | BLK | 20 | 50.A5 | XT-9217:2 | 2 BAY BACK LEFT WALL | 50.A4
UAI9217-1:IE | WI0650 | PT1120-S | SH | 20 | 50.A5 | XT-9217:3 | 2 BAY BACK LEFT WALL | 50.A4
UAI9217-5:1+ | WI0722 | PT2120-1 | RED | 20 | 60.A5 | XT-9217:13 | 2 BAY BACK LEFT WALL | 60.A4
UAI9217-5:3 | WI0722 | PT2120-2 | BLK | 20 | 60.A5 | XT-9217:14 | 2 BAY BACK LEFT WALL | 60.A4
UAI9217-5:IE | WI0722 | PT2120-S | SH | 20 | 60.A5 | XT-9217:15 | 2 BAY BACK LEFT WALL | 60.A4
UAI9217-7:1+ | WI0723 | PT6400-1 | RED | 20 | 74.A5 | XT-9217:19 | 2 BAY BACK LEFT WALL | 74.A4
UAI9217-7:3 | WI0723 | PT6400-2 | BLK | 20 | 74.A5 | XT-9217:20 | 2 BAY BACK LEFT WALL | 74.A4
UAI9217-7:IE | WI0723 | PT6400-S | SH | 20 | 74.A5 | XT-9217:21 | 2 BAY BACK LEFT WALL | 74.A4
UAI9290-7:1+ | WI0750 | PT21413 | RED | 20 | 58.A5 | XT-9290:19 | 2 BAY BACK LEFT WALL | 58.A4
UAI9290-7:3 | WI0750 | PT21412 | BLK | 20 | 58.A5 | XT-9290:20 | 2 BAY BACK LEFT WALL | 58.B4
UAI9290-7:IE | WI0750 | PT2141S | SH | 20 | 58.A5 | XT-9290:21 | 2 BAY BACK LEFT WALL | 58.B4
UAI9290-5:1+ | WI0751 | PT2131-1 | RED | 20 | 56.D5 | XT-9290:13 | 2 BAY BACK LEFT WALL | 56.D4
UAI9290-5:3 | WI0751 | PT2131-2 | BLK | 20 | 56.D5 | XT-9290:14 | 2 BAY BACK LEFT WALL | 56.D4
UAI9290-5:IE | WI0751 | PT2131-S | SH | 20 | 56.D5 | XT-9290:15 | 2 BAY BACK LEFT WALL | 56.D4
UAI9210-1:1+ | WI0752 | PT2126-1 | RED | 20 | 56.B5 | XT-9210:1 | 2 BAY BACK LEFT WALL | 56.B4
UAI9210-1:3 | WI0752 | PT2126-2 | BLK | 20 | 56.B5 | XT-9210:2 | 2 BAY BACK LEFT WALL | 56.B4
UAI9210-1:IE | WI0752 | PT2126-S | SH | 20 | 56.B5 | XT-9210:3 | 2 BAY BACK LEFT WALL | 56.B4
UAI9290-3:1+ | WI0753 | PDT1500-1 | RED | 20 | 50.B5 | XT-9290:7 | 2 BAY BACK LEFT WALL | 50.B4
UAI9290-3:3 | WI0753 | PDT1500-2 | BLK | 20 | 50.B5 | XT-9290:8 | 2 BAY BACK LEFT WALL | 50.B4
UAI9290-3:IE | WI0753 | PDT1500-S | SH | 20 | 50.B5 | XT-9290:9 | 2 BAY BACK LEFT WALL | 50.B4
UAI9216-3:1+ | WI0813A | SB0473-21 | RED | 20 | 34.C5 | XT-9216:7 | 2 BAY BACK LEFT WALL | 34.C4
UAI9216-3:3- | WI0813A | SB0473-22 | BLK | 20 | 34.C5 | XT-9216:8 | 2 BAY BACK LEFT WALL | 34.C4
UAI9216-3:IE | WI0813A | SB0473-S1 | SH | 20 | 34.C5 | XT-9216:9 | 2 BAY BACK LEFT WALL | 34.D4
UAI9216-1:1+ | WI0814A | SB0472-21 | RED | 20 | 34.B5 | XT-9216:1 | 2 BAY BACK LEFT WALL | 34.B4
UAI9216-1:3- | WI0814A | SB0472-22 | BLK | 20 | 34.B5 | XT-9216:2 | 2 BAY BACK LEFT WALL | 34.B4
UAI9216-1:IE | WI0814A | SB0472-S1 | SH | 20 | 34.B5 | XT-9216:3 | 2 BAY BACK LEFT WALL | 34.B4
UAI9216-1:4+ | WI0814B | SB0472-11 | RED | 20 | 34.C5 | XT-9216:4 | 2 BAY BACK LEFT WALL | 34.C4
UAI9216-1:6- | WI0814B | SB0473-12 | BLK | 20 | 34.C5 | XT-9216:5 | 2 BAY BACK LEFT WALL | 34.C4
UAI9216-1:IE | WI0814B | SB0473-S2 | SH | 20 | 34.C5 | XT-9216:6 | 2 BAY BACK LEFT WALL | 34.C4
UAI9291-1:1+ | WI0816A | ZS2220-2 | RED | 20 | 70.A5 | XT-9291:1 | 2 BAY BACK LEFT WALL | 70.A4
UAI9291-1:3- | WI0816A | ZS22201-3 | BLK | 20 | 70.A5 | XT-9291:2 | 2 BAY BACK LEFT WALL | 70.A4
UAI9291-1:IE | WI0816A | ZS2220-S | SH | 20 | 70.A5 | XT-9291:3 | 2 BAY BACK LEFT WALL | 70.A4
UAI9214-3:1+ | WI0820 | PS3170-1 | RED | 20 | 93.A5 | XT-9214:10 | 2 BAY BACK LEFT WALL | 93.A4
UAI9214-3:3- | WI0820 | PS3170-2 | BLK | 20 | 93.A5 | XT-9214:11 | 2 BAY BACK LEFT WALL | 93.A4
UAI9214-3:IE | WI0820 | PS3170-S | SH | 20 | 93.A5 | XT-9214:12 | 2 BAY BACK LEFT WALL | 93.A4
UAI9214-3:4+ | WI0821 | PS3150-1 | RED | 20 | 93.B5 | XT-9214:7 | 2 BAY BACK LEFT WALL | 93.B4
UAI9214-3:6- | WI0821 | PS3150-2 | BLK | 20 | 93.B5 | XT-9214:8 | 2 BAY BACK LEFT WALL | 93.B4
UAI9214-3:IE | WI0821 | PS3150-S | SH | 20 | 93.B5 | XT-9214:9 | 2 BAY BACK LEFT WALL | 93.B4
UAI9214-1:1+ | WI0826A | SA0475-23 | RED | 20 | 34.A5 | XT-9214:1 | 2 BAY BACK LEFT WALL | 34.A4
UAI9214-1:3- | WI0826A | SA0475-24 | BLK | 20 | 34.A5 | XT-9214:2 | 2 BAY BACK LEFT WALL | 34.A4
UAI9214-1:IE | WI0826A | SA0475-S1 | SH | 20 | 34.A5 | XT-9214:3 | 2 BAY BACK LEFT WALL | 34.A4
UAI9214-1:4+ | WI0826B | SA0475-11 | RED | 20 | 34.A5 | XT-9214:4 | 2 BAY BACK LEFT WALL | 34.A4
UAI9214-1:6- | WI0826B | SA0475-12 | BLK | 20 | 34.A5 | XT-9214:5 | 2 BAY BACK LEFT WALL | 34.A4
UAI9214-1:IE | WI0826B | SA0475-S2 | SH | 20 | 34.A5 | XT-9214:6 | 2 BAY BACK LEFT WALL | 34.A4
UAI9221-1:4 | WI0832 | TE42101 | RED | 20 | 85.A5 | XT-9221:1 | 2 BAY BACK LEFT WALL | 85.A4
UAI9221-1:3 | WI0832 | TE42102 | WHT | 20 | 85.A5 | XT-9221:2 | 2 BAY BACK LEFT WALL | 85.A4
UAI9221-1:2 | WI0832 | TE42103 | BLK | 20 | 85.A5 | XT-9221:3 | 2 BAY BACK LEFT WALL | 85.A4
UAI9221-1:IE | WI0832 | TE4210S | SH | 20 | 85.A5 | XT-9221:4 | 2 BAY BACK LEFT WALL | 85.A4
UAI9221-3:4 | WI0834 | TE42161 | RED | 20 | 85.C5 | XT-9221:9 | 2 BAY BACK LEFT WALL | 85.C4
UAI9221-3:3 | WI0834 | TE42162 | WHT | 20 | 85.C5 | XT-9221:10 | 2 BAY BACK LEFT WALL | 85.D4
UAI9221-3:2 | WI0834 | TE42163 | BLK | 20 | 85.C5 | XT-9221:11 | 2 BAY BACK LEFT WALL | 85.D4
UAI9221-3:IE | WI0834 | TE4216S | SH | 20 | 85.C5 | XT-9221:12 | 2 BAY BACK LEFT WALL | 85.D4
UAI9221-2:4 | WI0837 | TE42131 | RED | 20 | 85.B5 | XT-9221:5 | 2 BAY BACK LEFT WALL | 85.B4
UAI9221-2:3 | WI0837 | TE42132 | WHT | 20 | 85.B5 | XT-9221:6 | 2 BAY BACK LEFT WALL | 85.B4
UAI9221-2:2 | WI0837 | TE42133 | BLK | 20 | 85.B5 | XT-9221:7 | 2 BAY BACK LEFT WALL | 85.B4
UAI9221-2:IE | WI0837 | TE4213S | SH | 20 | 85.B5 | XT-9221:8 | 2 BAY BACK LEFT WALL | 85.C4
UAI9222A-1:4 | WI0843 | TE3620-1 | RED | 20 | 99.A5 | XT-9222A:1 | 2 BAY BACK LEFT WALL | 99.A4
UAI9222A-1:3 | WI0843 | TE3620-2 | WHT | 20 | 99.A5 | XT-9222A:2 | 2 BAY BACK LEFT WALL | 99.A4
UAI9222A-1:2 | WI0843 | TE3620-3 | BLK | 20 | 99.A5 | XT-9222A:3 | 2 BAY BACK LEFT WALL | 99.A4
UAI9222A-1:IE | WI0843 | TE3620-S | SH | 20 | 99.A5 | XT-9222A:4 | 2 BAY BACK LEFT WALL | 99.A4
UAI9221A-1:4 | WI0844 | TE3630-1 | RED | 20 | 99.B5 | XT-9221A:1 | 2 BAY BACK LEFT WALL | 99.B4
UAI9221A-1:3 | WI0844 | TE3630-2 | WHT | 20 | 99.B5 | XT-9221A:2 | 2 BAY BACK LEFT WALL | 99.B4
UAI9221A-1:2 | WI0844 | TE3630-3 | BLK | 20 | 99.B5 | XT-9221A:3 | 2 BAY BACK LEFT WALL | 99.B4
UAI9221A-1:IE | WI0844 | TE3630-S | SH | 20 | 99.B5 | XT-9221A:4 | 2 BAY BACK LEFT WALL | 99.B4
UAI9221-4:4 | WI0845 | TE4230-1 | RED | 20 | 86.B5 | XT-9221:13 | 2 BAY BACK LEFT WALL | 86.B4
UAI9221-4:3 | WI0845 | TE4230-2 | WHT | 20 | 86.B5 | XT-9221:14 | 2 BAY BACK LEFT WALL | 86.C4
UAI9221-4:2 | WI0845 | TE4230-3 | BLK | 20 | 86.B5 | XT-9221:15 | 2 BAY BACK LEFT WALL | 86.C4
UAI9221-4:IE | WI0845 | TE4230-S | SH | 20 | 86.B5 | XT-9221:16 | 2 BAY BACK LEFT WALL | 86.C4
UAI9221-5:4 | WI0846 | TE4240-1 | RED | 20 | 86.A5 | XT-9221:17 | 2 BAY BACK LEFT WALL | 86.A4
UAI9221-5:3 | WI0846 | TE4240-2 | WHT | 20 | 86.A5 | XT-9221:18 | 2 BAY BACK LEFT WALL | 86.A4
UAI9221-5:2 | WI0846 | TE4240-3 | BLK | 20 | 86.A5 | XT-9221:19 | 2 BAY BACK LEFT WALL | 86.A4
UAI9221-5:IE | WI0846 | TE4240-S | SH | 20 | 86.A5 | XT-9221:20 | 2 BAY BACK LEFT WALL | 86.A4
UAI9210-2:1+ | WI0851 | LT3100-1 | RED | 20 | 95.A5 | XT-9210:4 | 2 BAY BACK LEFT WALL | 95.A4
UAI9210-2:3 | WI0851 | LT3100-2 | BLK | 20 | 95.A5 | XT-9210:5 | 2 BAY BACK LEFT WALL | 95.A4
UAI9210-2:IE | WI0851 | LT3100-S | SH | 20 | 95.A5 | XT-9210:6 | 2 BAY BACK LEFT WALL | 95.A4
UAI9217-2:1+ | WI0852 | PDT6210-1 | RED | 20 | 116.A5 | XT-9217:4 | 2 BAY BACK LEFT WALL | 116.A4
UAI9217-2:3 | WI0852 | PDT6210-2 | BLK | 20 | 116.A5 | XT-9217:5 | 2 BAY BACK LEFT WALL | 116.A4
UAI9217-2:IE | WI0852 | PDT6210-S | SH | 20 | 116.A5 | XT-9217:6 | 2 BAY BACK LEFT WALL | 116.A4
UAI9210-4:1+ | WI0853 | PT3200-1 | RED | 20 | 91.C5 | XT-9210:10 | 2 BAY BACK LEFT WALL | 91.C4
UAI9210-4:3 | WI0853 | PT3200-2 | BLK | 20 | 91.C5 | XT-9210:11 | 2 BAY BACK LEFT WALL | 91.C4
UAI9210-4:IE | WI0853 | PT3200-S | SH | 20 | 91.C5 | XT-9210:12 | 2 BAY BACK LEFT WALL | 91.C4
UAI9210-3:1+ | WI0854 | PDT3100-1 | RED | 20 | 98.A5 | XT-9210:7 | 2 BAY BACK LEFT WALL | 98.A4
UAI9210-3:3 | WI0854 | PDT3100-2 | BLK | 20 | 98.A5 | XT-9210:8 | 2 BAY BACK LEFT WALL | 98.A4
UAI9210-3:IE | WI0854 | PDT3100-S | SH | 20 | 98.A5 | XT-9210:9 | 2 BAY BACK LEFT WALL | 98.A4
UAI9210-7:1+ | WI0855 | PDT1110-1 | RED | 20 | 51.A5 | XT-9210:19 | 2 BAY BACK LEFT WALL | 51.A4
UAI9210-7:3 | WI0855 | PDT1110-2 | BLK | 20 | 51.A5 | XT-9210:20 | 2 BAY BACK LEFT WALL | 51.A4
UAI9210-7:IE | WI0855 | PDT1110-S | SH | 20 | 51.A5 | XT-9210:21 | 2 BAY BACK LEFT WALL | 51.A4
UAI9210-5:1+ | WI0856 | PDT3240-1 | RED | 20 | 91.B5 | XT-9210:13 | 2 BAY BACK LEFT WALL | 91.B4
UAI9210-5:3 | WI0856 | PDT3240-3 | BLK | 20 | 91.B5 | XT-9210:14 | 2 BAY BACK LEFT WALL | 91.B4
UAI9210-5:IE | WI0856 | PDT3240-S | SH | 20 | 91.B5 | XT-9210:15 | 2 BAY BACK LEFT WALL | 91.B4
UAI9290-1:1+ | WI0861 | PDT6311-1 | RED | 20 | 119.B5 | XT-9290:1 | 2 BAY BACK LEFT WALL | 119.B4
UAI9290-1:3 | WI0861 | PDT6311-2 | BLK | 20 | 119.B5 | XT-9290:2 | 2 BAY BACK LEFT WALL | 119.B4
UAI9290-1:IE | WI0861 | PDT6311-S | SH | 20 | 119.B5 | XT-9290:3 | 2 BAY BACK LEFT WALL | 119.B4
UAI9210-6:1+ | WI0863 | PDT6180-1 | RED | 20 | 112.B5 | XT-9210:16 | 2 BAY BACK LEFT WALL | 112.B4
UAI9210-6:3 | WI0863 | PDT6180-2 | BLK | 20 | 112.B5 | XT-9210:17 | 2 BAY BACK LEFT WALL | 112.B4
UAI9210-6:IE | WI0863 | PDT6180-S | SH | 20 | 112.B5 | XT-9210:18 | 2 BAY BACK LEFT WALL | 112.B4
UAI9290-2:1+ | WI0864 | PDT6312-1 | RED | 20 | 119.B5 | XT-9290:4 | 2 BAY BACK LEFT WALL | 119.B4
UAI9290-2:3 | WI0864 | PDT6312-2 | BLK | 20 | 119.B5 | XT-9290:5 | 2 BAY BACK LEFT WALL | 119.B4
UAI9290-2:IE | WI0864 | PDT6312-S | SH | 20 | 119.B5 | XT-9290:6 | 2 BAY BACK LEFT WALL | 119.C4
UAI9220-1:1+ | WI0876A | ZS6151P | RED | 20 | 111.A5 | XT-9220:1 | 2 BAY BACK LEFT WALL | 111.A4
UAI9220-1:3- | WI0876A | ZS61561 | BLK | 20 | 111.A5 | XT-9220:2 | 2 BAY BACK LEFT WALL | 111.A4
UAI9220-1:IE | WI0876A | 0816A-S | SH | 20 | 111.A5 | XT-9220:3 | 2 BAY BACK LEFT WALL | 111.A4
UAI9222-1:1+ | WI0910 | LS4270-1 | RED | 20 | 99.C5 | XT-9222:1 | 2 BAY BACK LEFT WALL | 99.C4
UAI9222-1:3- | WI0910 | LS4270-2 | BLK | 20 | 99.C5 | XT-9222:2 | 2 BAY BACK LEFT WALL | 99.C4
UAI9222-1:IE | WI0910 | LS4270-S | SH | 20 | 99.C5 | XT-9222:3 | 2 BAY BACK LEFT WALL | 99.C4
UAI9271-1:4+ | WI0913 | ZSC6431-1 | RED | 20 | 75.B5 | XT-9271:1 | 2 BAY BACK LEFT WALL | 75.B4
UAI9271-1:6- | WI0913 | ZSC6431-2 | BLK | 20 | 75.B5 | XT-9271:2 | 2 BAY BACK LEFT WALL | 75.B4
UAI9271-1:IE | WI0913 | ZSC6431-S | SH | 20 | 75.B5 | XT-9271:3 | 2 BAY BACK LEFT WALL | 75.B4
UAI9270-1:1+ | WI091E | FS2646-1 | RED | 20 | 76.A5 | XT-9270:1 | 2 BAY BACK LEFT WALL | 76.A4
UAI9270-1:3- | WI091E | FS2646-2 | BLK | 20 | 76.A5 | XT-9270:2 | 2 BAY BACK LEFT WALL | 76.A4
UAI9270-1:IE | WI091E | FS2646-S1 | SH | 20 | 76.A5 | XT-9270:3 | 2 BAY BACK LEFT WALL | 76.A4
UAI9270-1:4+ | WI091F | FS2648-1 | RED | 20 | 76.B5 | XT-9270:7 | 2 BAY BACK LEFT WALL | 76.B4
UAI9270-1:6- | WI091F | FS2648-2 | BLK | 20 | 76.B5 | XT-9270:8 | 2 BAY BACK LEFT WALL | 76.B4
UAI9270-1:IE | WI091F | FS2648-S1 | SH | 20 | 76.B5 | XT-9270:9 | 2 BAY BACK LEFT WALL | 76.B4
UAI9215-1:1+ | WI3200A | PS3200-1 | RED | 20 | 91.D5 | XT-9215:1 | 2 BAY BACK LEFT WALL | 91.D4
UAI9215-1:3- | WI3200A | PS3200-2 | BLK | 20 | 91.D5 | XT-9215:2 | 2 BAY BACK LEFT WALL | 91.D4
UAI9215-1:IE | WI3200A | PS3200-S1 | SH | 20 | 91.D5 | XT-9215:3 | 2 BAY BACK LEFT WALL | 91.D4
UAI9215-1:4+ | WI3200B | PS3200-4 | RED | 20 | 91.D5 | XT-9215:4 | 2 BAY BACK LEFT WALL | 91.D4
UAI9215-1:6- | WI3200B | PS3200-5 | BLK | 20 | 91.D5 | XT-9215:5 | 2 BAY BACK LEFT WALL | 91.D4
UAI9215-1:IE | WI3200B | PS3200-S2 | SH | 20 | 91.D5 | XT-9215:6 | 2 BAY BACK LEFT WALL | 91.D4
UAI1520:+ | WI4501 | UA1520P | RED | 20 | 52.A5 | XT-9290:22 | 2 BAY BACK LEFT WALL | 52.A4
UAI1520:- | WI4501 | UA1520N | BLK | 20 | 52.A5 | XT-9290:23 | 2 BAY BACK LEFT WALL | 52.A4
UAI1520:IE | WI4501 | PE1520S | SH | 20 | 52.A5 | XT-9290:24 | 2 BAY BACK LEFT WALL | 52.A4
UAI9223-1:6 | WI6163 | UA4201-2 | RED | 20 | 89.A5 | XT-9223:2 | 2 BAY BACK LEFT WALL | 89.A4
UAI9223-1:4 | WI6163 | UA4201-3 | WHT | 20 | 89.A5 | XT-9223:3 | 2 BAY BACK LEFT WALL | 89.A4
UAI9223-1:5 | WI6163 | UA4201-1 | BLK | 20 | 89.A5 | XT-9223:1 | 2 BAY BACK LEFT WALL | 89.A4
UAI9223-1:IE | WI6163 | UA4201-S | SH | 20 | 89.A5 | XT-9223:4 | 2 BAY BACK LEFT WALL | 89.A4
UAI9223A-1:4+ | WI6224 | VE4234-A | RED | 20 | 89.D5 | XT-9223A:1 | 2 BAY BACK LEFT WALL | 89.D4
UAI9223A-1:5- | WI6224 | VE4234-B | BLK | 20 | 89.D5 | XT-9223A:2 | 2 BAY BACK LEFT WALL | 89.D4
UAI9223A-1:IE | WI6224 | VE4234-S | SH | 20 | 89.D5 | XT-9223A:3 | 2 BAY BACK LEFT WALL | 89.D4
UAI9223-2:6 | WI6241 | UA4231-2 | RED | 20 | 89.B5 | XT-9223:6 | 2 BAY BACK LEFT WALL | 89.B4
UAI9223-2:4 | WI6241 | UA4231-3 | WHT | 20 | 89.B5 | XT-9223:7 | 2 BAY BACK LEFT WALL | 89.B4
UAI9223-2:5 | WI6241 | UA4231-1 | BLK | 20 | 89.B5 | XT-9223:5 | 2 BAY BACK LEFT WALL | 89.B4
UAI9223-2:IE | WI6241 | UA4231-S | SH | 20 | 89.B5 | XT-9223:8 | 2 BAY BACK LEFT WALL | 89.B4
UAI9223-3:6 | WI6242 | UA4230-2 | RED | 20 | 89.B5 | XT-9223:10 | 2 BAY BACK LEFT WALL | 89.B4
UAI9223-3:4 | WI6242 | UA4230-3 | WHT | 20 | 89.B5 | XT-9223:11 | 2 BAY BACK LEFT WALL | 89.B4
UAI9223-3:5 | WI6242 | UA4230-1 | BLK | 20 | 89.B5 | XT-9223:9 | 2 BAY BACK LEFT WALL | 89.B4
UAI9223-3:IE | WI6242 | UA4230-S | SH | 20 | 89.B5 | XT-9223:12 | 2 BAY BACK LEFT WALL | 89.B4
UAI9223-4:6 | WI6243 | UA4241-2 | RED | 20 | 89.C5 | XT-9223:14 | 2 BAY BACK LEFT WALL | 89.C4
UAI9223-4:4 | WI6243 | UA4241-3 | WHT | 20 | 89.C5 | XT-9223:15 | 2 BAY BACK LEFT WALL | 89.C4
UAI9223-4:5 | WI6243 | UA4241-1 | BLK | 20 | 89.C5 | XT-9223:13 | 2 BAY BACK LEFT WALL | 89.C4
UAI9223-4:IE | WI6243 | UA4241-S | SH | 20 | 89.C5 | XT-9223:16 | 2 BAY BACK LEFT WALL | 89.C4
UAI9223-5:6 | WI6244 | UA4240-2 | RED | 20 | 89.C5 | XT-9223:18 | 2 BAY BACK LEFT WALL | 89.C4
UAI9223-5:4 | WI6244 | UA4240-3 | WHT | 20 | 89.C5 | XT-9223:19 | 2 BAY BACK LEFT WALL | 89.C4
UAI9223-5:5 | WI6244 | UA4240-1 | BLK | 20 | 89.C5 | XT-9223:17 | 2 BAY BACK LEFT WALL | 89.C4
UAI9223-5:IE | WI6244 | UA4240-S | SH | 20 | 89.C5 | XT-9223:20 | 2 BAY BACK LEFT WALL | 89.C4
IEG8220:1 | SC | IEG01101 | GRN | 14 | 22.C6 | XT0400:3 | JB70 | 22.C6
IEG8220:0 | SC | IEG8230-G | GRN | 8 | 4.C2 | IEG8230:00 | 2 BAY BACK RIGHT PANEL | 4.C2
UAI9214-1:10 | SC | 008243 | WHT | 20 | 34.A5 | AF0082:43 | 2 BAY BACK RIGHT PANEL | 34.A7
UAI9214-1:11 | SC | 008211 | WHT | 20 | 34.A5 | AF0082:11 | 2 BAY BACK RIGHT PANEL | 34.A7
UAI9214-1:7 | SC | 008242 | WHT | 20 | 34.A5 | AF0082:42 | 2 BAY BACK RIGHT PANEL | 34.A7
UAI9214-1:8 | SC | 008210 | WHT | 20 | 34.A5 | AF0082:10 | 2 BAY BACK RIGHT PANEL | 34.A7
UAI9214-3:10 | SC | 008233 | WHT | 20 | 93.B5 | AF0082:33 | 2 BAY BACK RIGHT PANEL | 93.B7
UAI9214-3:11 | SC | 008201 | WHT | 20 | 93.B5 | AF0082:01 | 2 BAY BACK RIGHT PANEL | 93.B7
UAI9214-3:7 | SC | 008232 | WHT | 20 | 93.A5 | AF0082:32 | 2 BAY BACK RIGHT PANEL | 93.A7
UAI9214-3:8 | SC | 008200 | WHT | 20 | 93.A5 | AF0082:00 | 2 BAY BACK RIGHT PANEL | 93.A7
UAI9216-1:7 | SC | 008138 | WHT | 20 | 34.B5 | AF0081:38 | 2 BAY BACK RIGHT PANEL | 34.B7
UAI9216-1:8 | SC | 008106 | WHT | 20 | 34.B5 | AF0081:06 | 2 BAY BACK RIGHT PANEL | 34.B7
UAI9216-3:7 | SC | 008136 | WHT | 20 | 34.C5 | AF0081:36 | 2 BAY BACK RIGHT PANEL | 34.C7
UAI9216-3:8 | SC | 008104 | WHT | 20 | 34.C5 | AF0081:04 | 2 BAY BACK RIGHT PANEL | 34.C7
UAI9220-1:7 | SC | 008742 | WHT | 20 | 111.A5 | AF0087:42 | 2 BAY BACK RIGHT PANEL | 111.A7
UAI9220-1:8 | SC | 008710 | WHT | 20 | 111.A5 | AF0087:10 | 2 BAY BACK RIGHT PANEL | 111.A7
UAI9222-1:7 | SC | 009132 | WHT | 20 | 99.C5 | AF0091:32 | 2 BAY BACK RIGHT PANEL | 99.C7
UAI9222-1:8 | SC | 009100 | WHT | 20 | 99.C5 | AF0091:00 | 2 BAY BACK RIGHT PANEL | 99.C7
UAI9270-1:10 | SC | 009147 | WHT | 20 | 76.B5 | AF0091:47 | 2 BAY BACK RIGHT PANEL | 76.B7
UAI9270-1:11 | SC | 009115 | WHT | 20 | 76.B5 | AF0091:15 | 2 BAY BACK RIGHT PANEL | 76.B7
UAI9270-1:7 | SC | 009146 | WHT | 20 | 76.A5 | AF0091:46 | 2 BAY BACK RIGHT PANEL | 76.A7
UAI9270-1:8 | SC | 009114 | WHT | 20 | 76.A5 | AF0091:14 | 2 BAY BACK RIGHT PANEL | 76.A7
UAI9271-1:10 | SC | 009135 | WHT | 20 | 75.B5 | AF0091:35 | 2 BAY BACK RIGHT PANEL | 75.B7
UAI9271-1:11 | SC | 009103 | WHT | 20 | 75.B5 | AF0091:03 | 2 BAY BACK RIGHT PANEL | 75.B7
UAI9291-1:7 | SC | 008142 | WHT | 20 | 70.A5 | AF0081:42 | 2 BAY BACK RIGHT PANEL | 70.A7
UAI9291-1:8 | SC | 008110 | WHT | 20 | 70.A5 | AF0081:10 | 2 BAY BACK RIGHT PANEL | 70.A7
UAI9221-1:-7 | W0832 | 008321 | RED | 20 | 85.A5 | AF0083:21 | 2 BAY BACK RIGHT PANEL | 85.A7
UAI9221-1:-5 | W0832 | 008305 | WHT | 20 | 85.A5 | AF0083:05 | 2 BAY BACK RIGHT PANEL | 85.A7
UAI9221-1:+6 | W0832 | 008304 | BLK | 20 | 85.A5 | AF0083:04 | 2 BAY BACK RIGHT PANEL | 85.A7
FW1208:1 | W0832 | 008352 | SH | 20 | 85.A6 | AF0083:52 | 2 BAY BACK RIGHT PANEL | 85.A7
UAI9221-3:-7 | W0834 | 008325 | RED | 20 | 85.C5 | AF0083:25 | 2 BAY BACK RIGHT PANEL | 85.C7
UAI9221-3:-5 | W0834 | 008309 | WHT | 20 | 85.C5 | AF0083:09 | 2 BAY BACK RIGHT PANEL | 85.C7
UAI9221-3:+6 | W0834 | 008308 | BLK | 20 | 85.C5 | AF0083:08 | 2 BAY BACK RIGHT PANEL | 85.C7
FW1208:3 | W0834 | 008356 | SH | 20 | 85.D6 | AF0083:56 | 2 BAY BACK RIGHT PANEL | 85.C7
UAI9221-2:-7 | W0837 | 008331 | RED | 20 | 85.B5 | AF0083:31 | 2 BAY BACK RIGHT PANEL | 85.B7
UAI9221-2:-5 | W0837 | 008315 | WHT | 20 | 85.B5 | AF0083:15 | 2 BAY BACK RIGHT PANEL | 85.B7
UAI9221-2:+6 | W0837 | 008314 | BLK | 20 | 85.B5 | AF0083:14 | 2 BAY BACK RIGHT PANEL | 85.B7
FW1208:2 | W0837 | 008362 | SH | 20 | 85.C6 | AF0083:62 | 2 BAY BACK RIGHT PANEL | 85.B7
UAI9222A-1:-7 | W0843 | 012323 | RED | 20 | 99.A5 | AF0084:23 | 2 BAY BACK RIGHT PANEL | 99.A7
UAI9222A-1:-5 | W0843 | 012307 | WHT | 20 | 99.A5 | AF0084:07 | 2 BAY BACK RIGHT PANEL | 99.A7
UAI9222A-1:+6 | W0843 | 012306 | BLK | 20 | 99.A5 | AF0084:06 | 2 BAY BACK RIGHT PANEL | 99.A7
FW1215:1 | W0843 | 012354 | SH | 20 | 99.A6 | AF0084:54 | 2 BAY BACK RIGHT PANEL | 99.A7
UAI9221A-1:-7 | W0844 | 012325 | RED | 20 | 99.B5 | AF0084:25 | 2 BAY BACK RIGHT PANEL | 99.B7
UAI9221A-1:-5 | W0844 | 012309 | WHT | 20 | 99.B5 | AF0084:09 | 2 BAY BACK RIGHT PANEL | 99.B7
UAI9221A-1:+6 | W0844 | 012308 | BLK | 20 | 99.B5 | AF0084:08 | 2 BAY BACK RIGHT PANEL | 99.B7
FW1215:2 | W0844 | 012356 | SH | 20 | 99.B6 | AF0084:56 | 2 BAY BACK RIGHT PANEL | 99.B7
UAI9221-4:-7 | W0845 | 008427 | RED | 20 | 86.B5 | AF0084:27 | 2 BAY BACK RIGHT PANEL | 86.B7
UAI9221-4:-5 | W0845 | 008411 | WHT | 20 | 86.B5 | AF0084:11 | 2 BAY BACK RIGHT PANEL | 86.B7
UAI9221-4:+6 | W0845 | 008410 | BLK | 20 | 86.B5 | AF0084:10 | 2 BAY BACK RIGHT PANEL | 86.B7
FW-W0845:1 | W0845 | 008458 | SH | 20 | 86.C6 | AF0084:58 | 2 BAY BACK RIGHT PANEL | 86.B7
UAI9221-5:-7 | W0846 | 008429 | RED | 20 | 86.A5 | AF0084:29 | 2 BAY BACK RIGHT PANEL | 86.A7
UAI9221-5:-5 | W0846 | 008413 | WHT | 20 | 86.A5 | AF0084:13 | 2 BAY BACK RIGHT PANEL | 86.A7
UAI9221-5:+6 | W0846 | 008412 | BLK | 20 | 86.A5 | AF0084:12 | 2 BAY BACK RIGHT PANEL | 86.A7
FW-W0846:1 | W0846 | 008460 | SH | 20 | 86.A6 | AF0084:60 | 2 BAY BACK RIGHT PANEL | 86.A7
UAI9210-2:+8 | W0851 | 008502 | RED | 20 | 95.A5 | AF0085:02 | 2 BAY BACK RIGHT PANEL | 95.A7
UAI9210-2:-7 | W0851 | 008518 | BLK | 20 | 95.A5 | AF0085:18 | 2 BAY BACK RIGHT PANEL | 95.A7
UAI9217-2:+8 | W0852 | 008504 | RED | 20 | 116.A5 | AF0085:04 | 2 BAY BACK RIGHT PANEL | 116.A7
UAI9217-2:-7 | W0852 | 008520 | BLK | 20 | 116.A5 | AF0085:20 | 2 BAY BACK RIGHT PANEL | 116.A7
FW0870:1 | W0852 | 008552 | SH | 20 | 116.A6 | AF0085:52 | 2 BAY BACK RIGHT PANEL | 116.A7
UAI9210-4:+8 | W0853 | 008506 | RED | 20 | 91.C5 | AF0085:06 | 2 BAY BACK RIGHT PANEL | 91.C7
UAI9210-4:-7 | W0853 | 008522 | BLK | 20 | 91.C5 | AF0085:22 | 2 BAY BACK RIGHT PANEL | 91.C7
FW0884:1 | W0853 | 008554 | SH | 20 | 91.C6 | AF0085:54 | 2 BAY BACK RIGHT PANEL | 91.C7
UAI9210-3:+8 | W0854 | 008508 | RED | 20 | 98.A5 | AF0085:08 | 2 BAY BACK RIGHT PANEL | 98.A7
UAI9210-3:-7 | W0854 | 008524 | BLK | 20 | 98.A5 | AF0085:24 | 2 BAY BACK RIGHT PANEL | 98.A7
FW0885:1 | W0854 | 008556 | SH | 20 | 98.A6 | AF0085:56 | 2 BAY BACK RIGHT PANEL | 98.A7
UAI9210-7:+8 | W0855 | 008510 | RED | 20 | 51.A5 | AF0085:10 | 2 BAY BACK RIGHT PANEL | 51.A7
UAI9210-7:-7 | W0855 | 008526 | BLK | 20 | 51.A5 | AF0085:26 | 2 BAY BACK RIGHT PANEL | 51.A7
FW0886:1 | W0855 | 008558 | SH | 20 | 51.A6 | AF0085:58 | 2 BAY BACK RIGHT PANEL | 51.A7
UAI9210-5:+8 | W0856 | 008512 | RED | 20 | 91.B5 | AF0085:12 | 2 BAY BACK RIGHT PANEL | 91.B7
UAI9210-5:-7 | W0856 | 008528 | BLK | 20 | 91.B5 | AF0085:28 | 2 BAY BACK RIGHT PANEL | 91.B7
FW0883:1 | W0856 | 008560 | SH | 20 | 91.B6 | AF0085:60 | 2 BAY BACK RIGHT PANEL | 91.B7
UAI9290-1:+8 | W0861 | 008602 | RED | 20 | 119.B5 | AF0086:02 | 2 BAY BACK RIGHT PANEL | 119.B7
UAI9290-1:-7 | W0861 | 008618 | BLK | 20 | 119.B5 | AF0086:18 | 2 BAY BACK RIGHT PANEL | 119.B7
FW7:1 | W0861 | 008650 | SH | 20 | 119.B6 | AF0086:50 | 2 BAY BACK RIGHT PANEL | 119.B7
UAI9210-6:+8 | W0863 | 008606 | RED | 20 | 112.B5 | AF0086:06 | 2 BAY BACK RIGHT PANEL | 112.B7
UAI9210-6:-7 | W0863 | 008622 | BLK | 20 | 112.B5 | AF0086:22 | 2 BAY BACK RIGHT PANEL | 112.B7
FW1203:1 | W0863 | 008654 | SH | 20 | 112.B6 | AF0086:54 | 2 BAY BACK RIGHT PANEL | 112.B7
UAI9290-2:+8 | W0864 | 008608 | RED | 20 | 119.B5 | AF0086:08 | 2 BAY BACK RIGHT PANEL | 119.B7
UAI9290-2:-7 | W0864 | 008624 | BLK | 20 | 119.B5 | AF0086:24 | 2 BAY BACK RIGHT PANEL | 119.B7
FW8:1 | W0864 | 008656 | SH | 20 | 119.B6 | AF0086:56 | 2 BAY BACK RIGHT PANEL | 119.B7
HIEG8220:00 | SC | HIEG8220-HG | GRN | 8 | 4.C2 | HIEG8210:0 | 2 BAY LEFT WALL | 4.C2
IEG8220:00 | SC | IEG8220-G | GRN | 8 | 4.B2 | IEG8210:0 | 2 BAY LEFT WALL | 4.B2
UAI9215-1:10 | SC | KA024821 | WHT | 20 | 91.D5 | KA0248:21 | 2 BAY LEFT WALL | 91.D6
UAI9215-1:7 | SC | FU0139 | WHT | 20 | 91.D5 | XT0136:1 | 2 BAY LEFT WALL | 17.A2
UAI9215-1:8 | SC | PS32002 | WHT | 20 | 91.D5 | KA0136:A1 | 2 BAY LEFT WALL | 17.D6
UAI9216-1:10 | SC | ESTOPA | WHT | 20 | 34.C5 | XT0240:3 | 2 BAY LEFT WALL | 18.A3
UAI9216-1:11 | SC | ESTOP | WHT | 20 | 34.C5 | XT0240:4 | 2 BAY LEFT WALL | 18.A3
UV0281:8+ | SC | UV0281P | WHT | 16 | 16.C1 | FU0281:LD | 2 BAY LEFT WALL | 16.C2
UV0281:9- | SC | 0V | WHT | 16 | 16.C1 | XT0135:3 | 2 BAY LEFT WALL | 16.B5
UV0291:8+ | SC | UV0291P | WHT | 16 | 16.D1 | FU0291:LD | 2 BAY LEFT WALL | 16.D2
UV0291:9- | SC | 0V | WHT | 16 | 16.D1 | XT0135:4 | 2 BAY LEFT WALL | 16.B5
UAI1520:+24V | SC | FU0450 | WHT | 16 | 52.A5 | FU0450:LD | 2 BAY RIGHT WALL | 22.A4
UAI1520:-24V | SC | 0V | WHT | 10 | 52.A5 | XT0450:2 | 2 BAY RIGHT WALL | 22.A5
UAI9215-1:11 | SC | UF1300-DI2P | WHT | 20 | 91.D5 | XT-9355:2 | 2 BAY RIGHT WALL | 43.A5
UAI9219A-1:+8 | W0554 | 005508 | RED | 20 | 78.B5 | AF0055:08 | 2 BAY RIGHT WALL | 78.B7
UAI9219A-1:-7 | W0554 | 005524 | BLK | 20 | 78.B5 | AF0055:24 | 2 BAY RIGHT WALL | 78.B7
FW1207:2 | W0554 | 005556 | SH | 20 | 78.C6 | AF0055:56 | 2 BAY RIGHT WALL | 78.B7
UAI9212-1:+8 | W0556 | 005512 | RED | 20 | 64.A5 | AF0055:12 | 2 BAY RIGHT WALL | 64.A7
UAI9212-1:-7 | W0556 | 005528 | BLK | 20 | 64.A5 | AF0055:28 | 2 BAY RIGHT WALL | 64.A7
FW1205:1 | W0556 | 005560 | SH | 20 | 64.A6 | AF0055:60 | 2 BAY RIGHT WALL | 64.A7
UAI9242-1:+8 | W0557 | 005514 | RED | 20 | 75.A5 | AF0055:14 | 2 BAY RIGHT WALL | 75.A7
UAI9242-1:-7 | W0557 | 005530 | BLK | 20 | 75.A5 | AF0055:30 | 2 BAY RIGHT WALL | 75.A7
FW1214:1 | W0557 | 005562 | SH | 20 | 75.A6 | AF0055:62 | 2 BAY RIGHT WALL | 75.A7
UAI9212-2:+8 | W0560 | 005600 | RED | 20 | 69.A5 | AF0056:00 | 2 BAY RIGHT WALL | 69.A7
UAI9212-2:-7 | W0560 | 005616 | BLK | 20 | 69.A5 | AF0056:16 | 2 BAY RIGHT WALL | 69.A7
FW1206:1 | W0560 | 005648 | SH | 20 | 69.A6 | AF0056:48 | 2 BAY RIGHT WALL | 69.A7
UAI9218-6:+8 | W0561 | 005602 | RED | 20 | 80.A5 | AF0056:02 | 2 BAY RIGHT WALL | 80.A7
UAI9218-6:-7 | W0561 | 005618 | BLK | 20 | 80.A5 | AF0056:18 | 2 BAY RIGHT WALL | 80.A7
FW1210:1 | W0561 | 005650 | SH | 20 | 80.A6 | AF0056:50 | 2 BAY RIGHT WALL | 80.A7
UAI9218-7:+8 | W0562 | 005604 | RED | 20 | 73.A5 | AF0056:04 | 2 BAY RIGHT WALL | 73.A7
UAI9218-7:-7 | W0562 | 005620 | BLK | 20 | 73.A5 | AF0056:20 | 2 BAY RIGHT WALL | 73.A7
FW1211:1 | W0562 | 005652 | SH | 20 | 73.A6 | AF0056:52 | 2 BAY RIGHT WALL | 73.A7
UAI9211-1:+8 | W0563 | 005606 | RED | 20 | 77.B5 | AF0056:06 | 2 BAY RIGHT WALL | 77.B7
UAI9211-1:-7 | W0563 | 005622 | BLK | 20 | 77.B5 | AF0056:22 | 2 BAY RIGHT WALL | 77.B7
FW1204:1 | W0563 | 005654 | SH | 20 | 77.B6 | AF0056:54 | 2 BAY RIGHT WALL | 77.B7
UAI9219-1:+8 | W0565 | 005610 | RED | 20 | 65.A5 | AF0056:10 | 2 BAY RIGHT WALL | 65.A7
UAI9219-1:-7 | W0565 | 005626 | BLK | 20 | 65.A5 | AF0056:26 | 2 BAY RIGHT WALL | 65.A7
FW1212:1 | W0565 | 005658 | SH | 20 | 65.A6 | AF0056:58 | 2 BAY RIGHT WALL | 65.A7
UAI9217-6:+8 | W0640 | 006400 | RED | 20 | 56.A5 | AF0064:00 | 2 BAY RIGHT WALL | 56.A7
UAI9217-6:-7 | W0640 | 006416 | BLK | 20 | 56.A5 | AF0064:16 | 2 BAY RIGHT WALL | 56.A7
FW1209:1 | W0640 | 006448 | SH | 20 | 56.A6 | AF0064:48 | 2 BAY RIGHT WALL | 56.A7
UAI9290-4:+8 | W0641 | 006404 | RED | 20 | 56.C5 | AF0064:04 | 2 BAY RIGHT WALL | 56.C7
UAI9290-4:-7 | W0641 | 006420 | BLK | 20 | 56.C5 | AF0064:20 | 2 BAY RIGHT WALL | 56.C7
FW0888:2 | W0641 | 006452 | SH | 20 | 56.C6 | AF0064:52 | 2 BAY RIGHT WALL | 56.C7
UAI9290-6:+8 | W0642 | 006408 | RED | 20 | 58.A5 | AF0064:08 | 2 BAY RIGHT WALL | 58.A7
UAI9290-6:-7 | W0642 | 006424 | BLK | 20 | 58.A5 | AF0064:24 | 2 BAY RIGHT WALL | 58.A7
FW1216:1 | W0642 | 006456 | SH | 20 | 58.A6 | AF0064:56 | 2 BAY RIGHT WALL | 58.A7
UAI9217-1:+8 | W0650 | 006500 | RED | 20 | 50.A5 | AF0065:00 | 2 BAY RIGHT WALL | 50.A7
UAI9217-1:-7 | W0650 | 006516 | BLK | 20 | 50.A5 | AF0065:16 | 2 BAY RIGHT WALL | 50.A7
FW0890:1 | W0650 | 006548 | SH | 20 | 50.A6 | AF0065:48 | 2 BAY RIGHT WALL | 50.A7
UAI9217-5:+8 | W0722 | 007208 | RED | 20 | 60.A5 | AF0072:08 | 2 BAY RIGHT WALL | 60.A7
UAI9217-5:-7 | W0722 | 007224 | BLK | 20 | 60.A5 | AF0072:24 | 2 BAY RIGHT WALL | 60.A7
FW0892:1 | W0722 | 007256 | SH | 20 | 60.A6 | AF0072:56 | 2 BAY RIGHT WALL | 60.A7
UAI9217-7:+8 | W0723 | 007212 | RED | 20 | 74.A5 | AF0072:12 | 2 BAY RIGHT WALL | 74.A7
UAI9217-7:-7 | W0723 | 007228 | BLK | 20 | 74.A5 | AF0072:28 | 2 BAY RIGHT WALL | 74.A7
FW0887:1 | W0723 | 007260 | SH | 20 | 74.A6 | AF0072:60 | 2 BAY RIGHT WALL | 74.A7
UAI9290-7:+8 | W0750 | 007500 | RED | 20 | 58.A5 | AF0075:00 | 2 BAY RIGHT WALL | 58.A7
UAI9290-7:-7 | W0750 | 007516 | BLK | 20 | 58.A5 | AF0075:16 | 2 BAY RIGHT WALL | 58.A7
FW1217:1 | W0750 | 007548 | SH | 20 | 58.B6 | AF0075:48 | 2 BAY RIGHT WALL | 58.A7
UAI9290-5:+8 | W0751 | 007504 | RED | 20 | 56.D5 | AF0075:04 | 2 BAY RIGHT WALL | 56.D7
UAI9290-5:-7 | W0751 | 007520 | BLK | 20 | 56.D5 | AF0075:20 | 2 BAY RIGHT WALL | 56.D7
FW0888:3 | W0751 | 007552 | SH | 20 | 56.D6 | AF0075:52 | 2 BAY RIGHT WALL | 56.D7
UAI9210-1:+8 | W0752 | 007508 | RED | 20 | 56.B5 | AF0075:08 | 2 BAY RIGHT WALL | 56.B7
UAI9210-1:-7 | W0752 | 007524 | BLK | 20 | 56.B5 | AF0075:24 | 2 BAY RIGHT WALL | 56.B7
FW0888:1 | W0752 | 007556 | SH | 20 | 56.B6 | AF0075:56 | 2 BAY RIGHT WALL | 56.B7
UAI9290-3:+8 | W0753 | 007512 | RED | 20 | 50.B5 | AF0075:12 | 2 BAY RIGHT WALL | 50.B7
UAI9290-3:-7 | W0753 | 007528 | BLK | 20 | 50.B5 | AF0075:28 | 2 BAY RIGHT WALL | 50.B7
FW0891:1 | W0753 | 007560 | SH | 20 | 50.B6 | AF0075:60 | 2 BAY RIGHT WALL | 50.B7
UAI1520:O/P | W4501 | UAI1520O/P | RED | 20 | 52.A5 | AF0450:06 | 2 BAY RIGHT WALL | 52.A7
UAI1520:0V | W4501 | UAI15200V | BLK | 20 | 52.A5 | AF0450:08 | 2 BAY RIGHT WALL | 52.A7
FW-UAI1520:1 | W4501 | UAI1520S | SH | 20 | 52.A6 | AF0450:23 | 2 BAY RIGHT WALL | 52.A7
UAI9223-1:7 | W6163 | 0616SIG3 | RED | 20 | 89.A5 | AP0616:SIG3 | ORBIT 60^DOOR PANEL | 89.A6
UAI9223-1:8 | W6163 | 0616COM3 | BLK | 20 | 89.A5 | AP0616:COM3 | ORBIT 60^DOOR PANEL | 89.A6
FLOATING | W6163 | 0616SHLD3 | SH | 20 | 89.A6 | AP0616:SHLD3 | ORBIT 60^DOOR PANEL | 89.A6
UAI9223A-1:8+ | W6224 | 0622A4 | RED | 20 | 89.D5 | AP0622:A4(+) | ORBIT 60^DOOR PANEL | 89.D6
UAI9223A-1:7- | W6224 | 0622B4 | BLK | 20 | 89.D5 | AP0622:B4(-) | ORBIT 60^DOOR PANEL | 89.D6
FW2?:1 | W6224 | 06224SHLD4 | SH | 20 | 89.D6 | AP0622:SHLD4 | ORBIT 60^DOOR PANEL | 89.D6
UAI9223-2:7 | W6241 | 0624SIG1 | RED | 20 | 89.B5 | AP0624:SIG1 | ORBIT 60^DOOR PANEL | 89.B6
UAI9223-2:8 | W6241 | 0624COM1 | BLK | 20 | 89.B5 | AP0624:COM1 | ORBIT 60^DOOR PANEL | 89.B6
FLOATING | W6241 | 0624SHLD1 | SH | 20 | 89.B6 | AP0624:SHLD1 | ORBIT 60^DOOR PANEL | 89.B6
UAI9223-3:7 | W6242 | 0624SIG2 | RED | 20 | 89.B5 | AP0624:SIG2 | ORBIT 60^DOOR PANEL | 89.B6
UAI9223-3:8 | W6242 | 0624COM2 | BLK | 20 | 89.B5 | AP0624:COM2 | ORBIT 60^DOOR PANEL | 89.B6
FLOATING | W6242 | 0624SHLD2 | SH | 20 | 89.B6 | AP0624:SHLD2 | ORBIT 60^DOOR PANEL | 89.B6
UAI9223-4:7 | W6243 | 0624SIG3 | RED | 20 | 89.C5 | AP0624:SIG3 | ORBIT 60^DOOR PANEL | 89.C6
UAI9223-4:8 | W6243 | 0624COM3 | BLK | 20 | 89.C5 | AP0624:COM3 | ORBIT 60^DOOR PANEL | 89.C6
FLOATING | W6243 | 0624SHLD3 | SH | 20 | 89.C6 | AP0624:SHLD3 | ORBIT 60^DOOR PANEL | 89.C6
UAI9223-5:7 | W6244 | 0624SIG4 | RED | 20 | 89.C5 | AP0624:SIG4 | ORBIT 60^DOOR PANEL | 89.C6
UAI9223-5:8 | W6244 | 0624COM4 | BLK | 20 | 89.C5 | AP0624:COM4 | ORBIT 60^DOOR PANEL | 89.C6
FLOATING | W6244 | 0624SHLD4 | SH | 20 | 89.C6 | AP0624:SHLD4 | ORBIT 60^DOOR PANEL | 89.C6
SolarTools ver. 24.0.84.26264 (Jun 3, 2025)
Report date: 7/10/2025 2:58 PM

## 2 BAY BACK RIGHT PANEL
2 BAY BACK RIGHT PANEL
Project # | G9440
Project Name | NOC AL SHAHEEN T130
Revision | A.5
Controls DE | G. Colby
Phone:
Controls ME | R. Duran
Phone:
From | [5 empty] | To
Device ID | Cable (W) Conductor (SC) Jumper Clip (JC) | Wire No. | Wire ID | Gauge/Size | Page/Zone | Device ID | Location | Page/Zone
XT0080:1 | JC | 0V | CLIP | --- | 8.D1 | XT0080:2 | 2 BAY BACK RIGHT PANEL | 8.D1
XT0080:2 | JC | 0V | CLIP | --- | 8.D1 | XT0080:3 | 2 BAY BACK RIGHT PANEL | 8.D1
XT0090:1 | JC | 0V | CLIP | --- | 8.B1 | XT0090:2 | 2 BAY BACK RIGHT PANEL | 8.B1
AF0081:03 | SC | 008103 | WHT | 20 | 19.C7 | KA0130:14 | 2 BAY BACK RIGHT PANEL | 19.C6
AF0081:07 | SC | 008107 | WHT | 20 | 37.A7 | KA0817:14 | 2 BAY BACK RIGHT PANEL | 37.A5
AF0081:19 | SC | UA1200J27 | WHT | 20 | 19.C7 | XT-9326:4 | 2 BAY BACK RIGHT PANEL | 19.D4
AF0081:35 | SC | 008135 | WHT | 20 | 19.C7 | KA0130:A2 | 2 BAY BACK RIGHT PANEL | 19.C5
AF0081:39 | SC | 008139 | WHT | 20 | 37.A7 | KA0817:11 | 2 BAY BACK RIGHT PANEL | 37.A5
AF0081:07 | SC | JP2 | VIO | 20 | 37.A7 | AF0081:39 | 2 BAY BACK RIGHT PANEL | 37.A7
AF0082:02 | SC | JP4 | VIO | 20 | 120.A7 | AF0082:34 | 2 BAY BACK RIGHT PANEL | 120.A7
AF0082:03 | SC | JP6 | VIO | 20 | 120.B7 | AF0082:35 | 2 BAY BACK RIGHT PANEL | 120.B7
AF0087:12 | SC | JP3 | VIO | 20 | 36.B7 | AF0087:44 | 2 BAY BACK RIGHT PANEL | 36.B7
XT-9300:8 | SC | JP1 | VIO | 20 | 31.B4 | XT-9300:7 | 2 BAY BACK RIGHT PANEL | 31.B4
AF0081:COM | SC | AU0080N | WHT | 20 | 8.C2 | AU0080:COM | 2 BAY BACK RIGHT PANEL | 8.C2
AF0081:J | SC | * |  |  | 8.C2 | AF0082:P | 2 BAY BACK RIGHT PANEL | 8.D3
AF0081:P | SC | * |  |  | 8.C2 | AU0080:J | 2 BAY BACK RIGHT PANEL | 8.C2
AF0081:V+ | SC | AU0080P | WHT | 20 | 8.C2 | AU0080:V+ | 2 BAY BACK RIGHT PANEL | 8.C2
AF0082:COM | SC | 0V | WHT | 16 | 8.D3 | XT0080:2 | 2 BAY BACK RIGHT PANEL | 8.D1
AF0082:COM | SC | AF0082N | WHT | 20 | 8.D3 | AF0083:COM | 2 BAY BACK RIGHT PANEL | 8.D3
AF0082:J | SC | * |  |  | 8.D3 | AF0083:P | 2 BAY BACK RIGHT PANEL | 8.D3
AF0082:V+ | SC | FU0081 | WHT | 14 | 8.D3 | FU0081:LD | 2 BAY BACK RIGHT PANEL | 8.D1
AF0082:V+ | SC | AF0082P | WHT | 20 | 8.D3 | AF0083:V+ | 2 BAY BACK RIGHT PANEL | 8.D3
AF0083:COM | SC | AF0083N | WHT | 20 | 8.D3 | AF0084:COM | 2 BAY BACK RIGHT PANEL | 8.D4
AF0083:J | SC | * |  |  | 8.D3 | AF0084:P | 2 BAY BACK RIGHT PANEL | 8.D4
AF0083:V+ | SC | AF0083P | WHT | 20 | 8.D3 | AF0084:V+ | 2 BAY BACK RIGHT PANEL | 8.D4
AF0084:COM | SC | AF0084N | WHT | 20 | 8.D4 | AF0085:COM | 2 BAY BACK RIGHT PANEL | 8.D5
AF0084:J | SC | * |  |  | 8.D4 | AF0085:P | 2 BAY BACK RIGHT PANEL | 8.D5
AF0084:SH | SC | AF0083G | GRN | 14 | 8.D4 | AF0083:SH | 2 BAY BACK RIGHT PANEL | 8.D3
AF0084:SH | SC | AF0084G | GRN | 14 | 8.D4 | AF0085:SH | 2 BAY BACK RIGHT PANEL | 8.D5
AF0084:V+ | SC | AF0084P | WHT | 20 | 8.D4 | AF0085:V+ | 2 BAY BACK RIGHT PANEL | 8.D5
AF0085:COM | SC | AF0085N | WHT | 20 | 8.D5 | AF0086:COM | 2 BAY BACK RIGHT PANEL | 8.D5
AF0085:J | SC | * |  |  | 8.D5 | AF0086:P | 2 BAY BACK RIGHT PANEL | 8.D5
AF0085:SH | SC | AF0085G | GRN | 14 | 8.D5 | AF0086:SH | 2 BAY BACK RIGHT PANEL | 8.D5
AF0085:V+ | SC | AF0085P | WHT | 20 | 8.D5 | AF0086:V+ | 2 BAY BACK RIGHT PANEL | 8.D5
AF0086:COM | SC | AF0086N | WHT | 20 | 8.D5 | AF0087:COM | 2 BAY BACK RIGHT PANEL | 8.D6
AF0086:J | SC | * |  |  | 8.D5 | AF0087:P | 2 BAY BACK RIGHT PANEL | 8.D6
AF0086:SH | SC | IEG8230-4 | GRN | 14 | 8.D5 | IEG8230:4 | 2 BAY BACK RIGHT PANEL | 8.D5
AF0086:V+ | SC | AF0086P | WHT | 20 | 8.D5 | AF0087:V+ | 2 BAY BACK RIGHT PANEL | 8.D6
AF0087:00 | SC | 008700 | WHT | 20 | 37.B7 | KA0870:14 | 2 BAY BACK RIGHT PANEL | 37.B5
AF0087:01 | SC | 008701 | WHT | 20 | 37.C7 | KA0871:14 | 2 BAY BACK RIGHT PANEL | 37.C5
AF0087:03 | SC | SB75512 | WHT | 20 | 36.C7 | XT-9311:2 | 2 BAY BACK RIGHT PANEL | 36.C4
AF0087:04 | SC | SB75522 | WHT | 20 | 36.D7 | XT-9311:4 | 2 BAY BACK RIGHT PANEL | 36.D4
AF0087:13 | SC | SB75552 | WHT | 20 | 36.B7 | XT-9311:8 | 2 BAY BACK RIGHT PANEL | 36.B4
AF0087:14 | SC | SB75542 | WHT | 20 | 36.C7 | XT-9311:6 | 2 BAY BACK RIGHT PANEL | 36.C4
AF0087:32 | SC | 008732 | WHT | 20 | 37.B7 | KA0870:11 | 2 BAY BACK RIGHT PANEL | 37.B5
AF0087:33 | SC | 008733 | WHT | 20 | 37.C7 | KA0871:11 | 2 BAY BACK RIGHT PANEL | 37.C5
AF0087:35 | SC | SB75511 | WHT | 20 | 36.C7 | XT-9311:1 | 2 BAY BACK RIGHT PANEL | 36.C4
AF0087:36 | SC | SB75521 | WHT | 20 | 36.D7 | XT-9311:3 | 2 BAY BACK RIGHT PANEL | 36.D4
AF0087:45 | SC | SB75551 | WHT | 20 | 36.B7 | XT-9311:7 | 2 BAY BACK RIGHT PANEL | 36.B4
AF0087:46 | SC | SB75541 | WHT | 20 | 36.C7 | XT-9311:5 | 2 BAY BACK RIGHT PANEL | 36.C4
AF0091:COM | SC | AU0090N | WHT | 20 | 8.B2 | AU0090:COM | 2 BAY BACK RIGHT PANEL | 8.A2
AF0091:J | SC | * |  |  | 8.B2 | AF0092:P | 2 BAY BACK RIGHT PANEL | 8.B3
AF0091:P | SC | * |  |  | 8.B2 | AU0090:J | 2 BAY BACK RIGHT PANEL | 8.A2
AF0091:V+ | SC | AU0090P | WHT | 20 | 8.B2 | AU0090:V+ | 2 BAY BACK RIGHT PANEL | 8.A2
AF0092:03 | SC | 009203 | WHT | 20 | 39.A7 | KA0923:A1 | 2 BAY BACK RIGHT PANEL | 39.A5
AF0092:04 | SC | 009204 | WHT | 20 | 39.A7 | KA0924:A1 | 2 BAY BACK RIGHT PANEL | 39.B5
AF0092:05 | SC | 009205 | WHT | 20 | 39.B7 | KA0925:A1 | 2 BAY BACK RIGHT PANEL | 39.B5
AF0092:07 | SC | 009207 | WHT | 20 | 39.C7 | KA0927:A1 | 2 BAY BACK RIGHT PANEL | 39.C5
AF0092:09 | SC | 009209 | WHT | 20 | 39.D7 | KA0929:A1 | 2 BAY BACK RIGHT PANEL | 39.D5
AF0092:19 | SC | 009219 | WHT | 20 | 39.A7 | KA0923:A2 | 2 BAY BACK RIGHT PANEL | 39.A5
AF0092:20 | SC | 009220 | WHT | 20 | 39.A7 | KA0924:A2 | 2 BAY BACK RIGHT PANEL | 39.B5
AF0092:21 | SC | 009221 | WHT | 20 | 39.B7 | KA0925:A2 | 2 BAY BACK RIGHT PANEL | 39.B5
AF0092:23 | SC | 009223 | WHT | 20 | 39.C7 | KA0927:A2 | 2 BAY BACK RIGHT PANEL | 39.C5
AF0092:25 | SC | 009225 | WHT | 20 | 39.D7 | KA0929:A2 | 2 BAY BACK RIGHT PANEL | 39.D5
AF0092:COM | SC | 0V | WHT | 16 | 8.B3 | XT0090:2 | 2 BAY BACK RIGHT PANEL | 8.B1
AF0092:J | SC | * |  |  | 8.B3 | AF0093:P | 2 BAY BACK RIGHT PANEL | 8.B3
AF0092:V+ | SC | FU0091 | WHT | 20 | 8.B3 | FU0091:LD | 2 BAY BACK RIGHT PANEL | 8.B1
AF0093:04 | SC | 009304 | WHT | 20 | 117.C7 | XT0171:2 | 2 BAY BACK RIGHT PANEL | 117.C5
AF0093:05 | SC | 009305 | WHT | 20 | 118.C7 | XT0171:6 | 2 BAY BACK RIGHT PANEL | 118.C5
AF0093:06 | SC | 009306 | WHT | 20 | 40.A7 | KA0936:A1 | 2 BAY BACK RIGHT PANEL | 40.A5
AF0093:07 | SC | 009307 | WHT | 20 | 40.A7 | KA0937:A1 | 2 BAY BACK RIGHT PANEL | 40.B5
AF0093:08 | SC | 009308 | WHT | 20 | 40.B7 | KA0938:A1 | 2 BAY BACK RIGHT PANEL | 40.B5
AF0093:09 | SC | 009309 | WHT | 20 | 40.C7 | KA0939:A1 | 2 BAY BACK RIGHT PANEL | 40.C5
AF0093:10 | SC | 009310 | WHT | 20 | 40.D7 | KA093A:A1 | 2 BAY BACK RIGHT PANEL | 40.D5
AF0093:22 | SC | 009322 | WHT | 20 | 40.A7 | KA0936:A2 | 2 BAY BACK RIGHT PANEL | 40.A5
AF0093:23 | SC | 009323 | WHT | 20 | 40.A7 | KA0937:A2 | 2 BAY BACK RIGHT PANEL | 40.B5
AF0093:24 | SC | 009324 | WHT | 20 | 40.B7 | KA0938:A2 | 2 BAY BACK RIGHT PANEL | 40.B5
AF0093:25 | SC | 009325 | WHT | 20 | 40.C7 | KA0939:A2 | 2 BAY BACK RIGHT PANEL | 40.C5
AF0093:26 | SC | 009326 | WHT | 20 | 40.D7 | KA093A:A2 | 2 BAY BACK RIGHT PANEL | 40.D5
AF0093:36 | SC | 009336 | WHT | 20 | 117.C7 | KA0176:14 | 2 BAY BACK RIGHT PANEL | 117.C6
AF0093:37 | SC | 009337 | WHT | 20 | 118.C7 | KA0177:14 | 2 BAY BACK RIGHT PANEL | 118.C6
AF0093:COM | SC | 0V | WHT | 16 | 8.B3 | XT0090:2 | 2 BAY BACK RIGHT PANEL | 8.B1
AF0093:J | SC | * |  |  | 8.B3 | AF0094:P | 2 BAY BACK RIGHT PANEL | 8.B4
AF0093:V+ | SC | FU0092 | WHT | 14 | 8.B3 | FU0092:LD | 2 BAY BACK RIGHT PANEL | 8.B1
AF0094:02 | SC | 009402 | WHT | 16 | 59.A7 | KA0221:14 | 2 BAY BACK RIGHT PANEL | 59.A6
AF0094:04 | SC | 009404 | WHT | 20 | 41.A7 | KA0942:A1 | 2 BAY BACK RIGHT PANEL | 41.A5
AF0094:06 | SC | 009406 | WHT | 20 | 41.A7 | KA0943:A1 | 2 BAY BACK RIGHT PANEL | 41.B5
AF0094:08 | SC | 009408 | WHT | 20 | 41.B7 | KA0944:A1 | 2 BAY BACK RIGHT PANEL | 41.B5
AF0094:18 | SC | SV2120-2 | WHT | 16 | 59.A7 | XT-9330:4 | 2 BAY BACK RIGHT PANEL | 59.A4
AF0094:20 | SC | 009420 | WHT | 20 | 41.A7 | KA0942:A2 | 2 BAY BACK RIGHT PANEL | 41.A5
AF0094:22 | SC | 009422 | WHT | 20 | 41.A7 | KA0943:A2 | 2 BAY BACK RIGHT PANEL | 41.B5
AF0094:24 | SC | 009424 | WHT | 20 | 41.B7 | KA0944:A2 | 2 BAY BACK RIGHT PANEL | 41.B5
AF0094:COM | SC | AF0095N | WHT | 16 | 8.B4 | AF0095:COM | 2 BAY BACK RIGHT PANEL | 8.A5
AF0094:COM | SC | 0V | WHT | 16 | 8.B4 | XT0090:2 | 2 BAY BACK RIGHT PANEL | 8.B1
AF0094:J | SC | * |  |  | 8.B4 | AF0095:P | 2 BAY BACK RIGHT PANEL | 8.A5
AF0094:V+ | SC | FU0093 | WHT | 14 | 8.B4 | FU0093:LD | 2 BAY BACK RIGHT PANEL | 8.B1
AF0094:V+ | SC | AF0095P | WHT | 16 | 8.B4 | AF0095:V+ | 2 BAY BACK RIGHT PANEL | 8.A5
AR0600:IE1 | SC | UV0600G | GRN | 14 | 7.A1 | UV0600:GND | 2 BAY BACK RIGHT PANEL | 7.B2
AR0600:IE2 | SC | IEG8230-3 | GRN | 12 | 7.A1 | IEG8230:3 | 2 BAY BACK RIGHT PANEL | 7.B4
AU0080:COM | SC | 0V | WHT | 16 | 8.C2 | XT0080:1 | 2 BAY BACK RIGHT PANEL | 8.D1
AU0080:V+ | SC | FU0080 | WHT | 14 | 8.C2 | FU0080:LD | 2 BAY BACK RIGHT PANEL | 8.D1
AU0090:COM | SC | 0V | WHT | 16 | 8.A2 | XT0090:1 | 2 BAY BACK RIGHT PANEL | 8.B1
AU0090:V+ | SC | FU0090 | WHT | 14 | 8.A2 | FU0090:LD | 2 BAY BACK RIGHT PANEL | 8.B1
FU0080:LI | SC | FU0137 | WHT | 14 | 8.D1 | FU0081:LI | 2 BAY BACK RIGHT PANEL | 8.D1
FU0081:LI | SC | FU0137 | WHT | 14 | 8.D1 | FU0082:LI | 2 BAY BACK RIGHT PANEL | 8.D1
FU0090:LI | SC | FU0137 | WHT | 14 | 8.B1 | FU0091:LI | 2 BAY BACK RIGHT PANEL | 8.B1
FU0091:LI | SC | FU0137 | WHT | 14 | 8.B1 | FU0092:LI | 2 BAY BACK RIGHT PANEL | 8.B1
FU0092:LI | SC | FU0137 | WHT | 14 | 8.B1 | FU0093:LI | 2 BAY BACK RIGHT PANEL | 8.B1
GR8231: | SC | IEG8230-1 | GRN | 14 | 4.D4 | IEG8230:1 | 2 BAY BACK RIGHT PANEL | 4.D3
GR8232: | SC | IEG8230-2 | GRN | 14 | 4.D4 | IEG8230:2 | 2 BAY BACK RIGHT PANEL | 4.D4
GR9231: | SC | GR9231 | GRN/YEL | 14 | 4.D4 | FG0005:1 | 2 BAY BACK RIGHT PANEL | 4.D3
GR9232: | SC | GR9232 | GRN/YEL | 14 | 4.D4 | FG0006:1 | 2 BAY BACK RIGHT PANEL | 4.D4
GR9233: | SC | GR9233 | GRN/YEL | 14 | 4.D5 | FG0006:2 | 2 BAY BACK RIGHT PANEL | 4.D5
KA0130:A1 | SC | UA1200J26 | WHT | 20 | 19.C5 | XT-9326:3 | 2 BAY BACK RIGHT PANEL | 19.C4
KA0130:A2 | SC | 008135 | WHT | 20 | 19.C5 | KA0130:11 | 2 BAY BACK RIGHT PANEL | 19.C6
KA0176:11 | SC | KA017611 | WHT | 20 | 117.C6 | XT0171:1 | 2 BAY BACK RIGHT PANEL | 117.C5
KA0176:A1 | SC | KA014422 | WHT | 20 | 117.B5 | KA0177:A1 | 2 BAY BACK RIGHT PANEL | 117.B5
KA0176:A2 | SC | 0V | WHT | 20 | 117.B5 | KA0177:A2 | 2 BAY BACK RIGHT PANEL | 117.B5
KA0177:11 | SC | KA017711 | WHT | 20 | 118.C6 | XT0171:5 | 2 BAY BACK RIGHT PANEL | 118.C5
KA0817:A1 | SC | SB7512-1 | WHT | 20 | 37.A5 | XT-9300:21 | 2 BAY BACK RIGHT PANEL | 37.A4
KA0817:A2 | SC | SB7512-2 | WHT | 20 | 37.A5 | XT-9300:22 | 2 BAY BACK RIGHT PANEL | 37.A4
KA0870:A1 | SC | XK7516-1 | WHT | 20 | 37.B5 | XT-9300:23 | 2 BAY BACK RIGHT PANEL | 37.B4
KA0870:A2 | SC | XK7516-2 | WHT | 20 | 37.B5 | XT-9300:24 | 2 BAY BACK RIGHT PANEL | 37.B4
KA0871:A1 | SC | XK7617-1 | WHT | 20 | 37.C5 | XT-9300:25 | 2 BAY BACK RIGHT PANEL | 37.C4
KA0871:A2 | SC | XK7517-2 | WHT | 20 | 37.C5 | XT-9300:26 | 2 BAY BACK RIGHT PANEL | 37.C4
KA0923:11 | SC | YK7565-1 | WHT | 20 | 39.A5 | XT-9300:31 | 2 BAY BACK RIGHT PANEL | 39.A4
KA0923:14 | SC | YK7565-2 | WHT | 20 | 39.A5 | XT-9300:32 | 2 BAY BACK RIGHT PANEL | 39.A4
KA0924:11 | SC | YK7501-1 | WHT | 20 | 39.B5 | XT-9300:33 | 2 BAY BACK RIGHT PANEL | 39.B4
KA0924:14 | SC | YK7501-2 | WHT | 20 | 39.B5 | XT-9300:34 | 2 BAY BACK RIGHT PANEL | 39.B4
KA0925:11 | SC | YK7502-1 | WHT | 20 | 39.C5 | XT-9311:9 | 2 BAY BACK RIGHT PANEL | 39.B4
KA0925:14 | SC | YK7502-2 | WHT | 20 | 39.C5 | XT-9311:10 | 2 BAY BACK RIGHT PANEL | 39.C4
KA0927:11 | SC | YK7503-1 | WHT | 20 | 39.C5 | XT-9311:11 | 2 BAY BACK RIGHT PANEL | 39.C4
KA0927:14 | SC | YK7503-2 | WHT | 20 | 39.C5 | XT-9311:12 | 2 BAY BACK RIGHT PANEL | 39.C4
KA0929:11 | SC | YK7504-1 | WHT | 20 | 39.D5 | XT-9300:39 | 2 BAY BACK RIGHT PANEL | 39.D4
KA0929:14 | SC | YK7504-2 | WHT | 20 | 39.D5 | XT-9300:40 | 2 BAY BACK RIGHT PANEL | 39.D4
KA0936:11 | SC | YK7505-1 | WHT | 20 | 40.A5 | XT-9300A:1 | 2 BAY BACK RIGHT PANEL | 40.A4
KA0936:14 | SC | YK7505-2 | WHT | 20 | 40.A5 | XT-9300A:2 | 2 BAY BACK RIGHT PANEL | 40.A4
KA0937:11 | SC | YK7509-1 | WHT | 20 | 40.B5 | XT-9300A:3 | 2 BAY BACK RIGHT PANEL | 40.B4
KA0937:14 | SC | YK7509-2 | WHT | 20 | 40.B5 | XT-9300A:4 | 2 BAY BACK RIGHT PANEL | 40.B4
KA0938:11 | SC | YK7512-1 | WHT | 20 | 40.C5 | XT-9311:13 | 2 BAY BACK RIGHT PANEL | 40.B4
KA0938:14 | SC | YK7512-2 | WHT | 20 | 40.C5 | XT-9311:14 | 2 BAY BACK RIGHT PANEL | 40.C4
KA0939:11 | SC | YK7513-1 | WHT | 20 | 40.C5 | XT-9311:15 | 2 BAY BACK RIGHT PANEL | 40.C4
KA0939:14 | SC | YK7513-2 | WHT | 20 | 40.C5 | XT-9311:16 | 2 BAY BACK RIGHT PANEL | 40.C4
KA093A:11 | SC | YK7518-1 | WHT | 20 | 40.D5 | XT-9300A:9 | 2 BAY BACK RIGHT PANEL | 40.D4
KA093A:14 | SC | YK7518-2 | WHT | 20 | 40.D5 | XT-9300A:10 | 2 BAY BACK RIGHT PANEL | 40.D4
KA0942:11 | SC | YK7524-1 | WHT | 20 | 41.A5 | XT-9300A:11 | 2 BAY BACK RIGHT PANEL | 41.A4
KA0942:14 | SC | YK7524-2 | WHT | 20 | 41.A5 | XT-9300A:12 | 2 BAY BACK RIGHT PANEL | 41.A4
KA0943:11 | SC | YK7525-1 | WHT | 20 | 41.B5 | XT-9300A:13 | 2 BAY BACK RIGHT PANEL | 41.B4
KA0943:14 | SC | YK7525-2 | WHT | 20 | 41.B5 | XT-9300A:14 | 2 BAY BACK RIGHT PANEL | 41.B4
KA0944:11 | SC | YK7150-1 | WHT | 20 | 41.C5 | XT-9300A:15 | 2 BAY BACK RIGHT PANEL | 41.B4
KA0944:14 | SC | YK7150-2 | WHT | 20 | 41.C5 | XT-9300A:16 | 2 BAY BACK RIGHT PANEL | 41.C4
KA1020:11 | SC | LZ1020-B | WHT | 14 | 44.A5 | XT-9328:1 | 2 BAY BACK RIGHT PANEL | 44.A4
KA1020:21 | SC | LZ1020-A | WHT | 14 | 44.A5 | XT-9328:2 | 2 BAY BACK RIGHT PANEL | 44.A4
KA9982:A1 | SC | CC9982-1 | WHT | 20 | 38.A5 | XT-9300:27 | 2 BAY BACK RIGHT PANEL | 38.A4
KA9982:A2 | SC | CC9982-2 | WHT | 20 | 38.A5 | XT-9300:28 | 2 BAY BACK RIGHT PANEL | 38.A4
KA9984:A1 | SC | CC9984-1 | WHT | 20 | 38.A5 | XT-9300:29 | 2 BAY BACK RIGHT PANEL | 38.A4
KA9984:A2 | SC | CC9984-2 | WHT | 20 | 38.A5 | XT-9300:30 | 2 BAY BACK RIGHT PANEL | 38.A4
VD6211:--1N4007 | SC | KA017611 | LEAD | --- | 117.C5 | XT0171:1 | 2 BAY BACK RIGHT PANEL | 117.C5
VD6211:+-1N4007 | SC | 009304 | LEAD | --- | 117.C5 | XT0171:2 | 2 BAY BACK RIGHT PANEL | 117.C5
VD6212:--1N4007 | SC | KA017711 | LEAD | --- | 118.C5 | XT0171:5 | 2 BAY BACK RIGHT PANEL | 118.C5
VD6212:+-1N4007 | SC | 009305 | LEAD | --- | 118.C5 | XT0171:6 | 2 BAY BACK RIGHT PANEL | 118.C5
AP0602:L2 | WC0001 | AP0602L2 | ENET | CABLE | 3.A2 | AP0603:L1 | 2 BAY BACK RIGHT PANEL | 3.A3
AP0603:L2 | WC0003 | AP0603L2 | ENET | CABLE | 3.A3 | AU0090:L1 | 2 BAY BACK RIGHT PANEL | 3.A4
AU0080:L1 | WC0009 | AU0090L2 | ENET | CABLE | 3.A4 | AU0090:L2 | 2 BAY BACK RIGHT PANEL | 3.A4
AF0093:20 | SC | 009320 | WHT | 20 | 117.C7 | KA6211:A2 | 1 BAY BACK WALL | 117.C6
AF0093:21 | SC | 009321 | WHT | 20 | 118.C7 | KA6212:A2 | 1 BAY BACK WALL | 118.C6
XT-9300:1 | SC | YK7580-1 | WHT | 20 | 30.A4 | KA121A:21 | 1 BAY BACK WALL | 30.A5
XT-9300:2 | SC | YK7580-2 | WHT | 20 | 30.A4 | KA121A:24 | 1 BAY BACK WALL | 30.A5
XT-9326A:2 | SC | KA9602NC | WHT | 16 | 28.C2 | XT0343:3 | 1 BAY LEFT WALL | 20.C5
XT-9326A:3 | SC | KA0330A1 | WHT | 20 | 28.B2 | XT0343:4 | 1 BAY LEFT WALL | 20.C5
XT-9300:7 | SC | 012239 | WHT | 20 | 31.B4 | AF0122:38 | 1 BAY RIGHT WALL | 31.B7
XT-9300:8 | SC | 012207 | WHT | 20 | 31.B4 | AF0122:06 | 1 BAY RIGHT WALL | 31.B7
XT-9326A:1 | SC | FU0333 | WHT | 20 | 28.B2 | XT0337:1 | 1 BAY RIGHT WALL | 28.B3
XT-9326A:3 | SC | KA0330A1 | WHT | 20 | 28.B2 | KA0330:A1 | 1 BAY RIGHT WALL | 28.B6
XT-9326A:4 | SC | KA96001 | WHT | 20 | 28.A2 | AF0122:35 | 1 BAY RIGHT WALL | 28.A7
XT-9326A:5 | SC | KA96002 | WHT | 20 | 28.A2 | AF0122:03 | 1 BAY RIGHT WALL | 28.A7
XT-9326A:6 | SC | KA96011 | WHT | 20 | 28.A2 | AF0122:36 | 1 BAY RIGHT WALL | 28.A7
XT-9326A:7 | SC | KA96012 | WHT | 20 | 28.A2 | AF0122:04 | 1 BAY RIGHT WALL | 28.A7
XT-9326A:8 | SC | KA0331A1 | WHT | 20 | 28.C2 | KA0331:A1 | 1 BAY RIGHT WALL | 28.C6
XT-9326A:9 | SC | FU0333 | WHT | 20 | 28.C2 | XT0337:3 | 1 BAY RIGHT WALL | 28.C3
AF0081:04 | SC | 008104 | WHT | 20 | 34.C7 | UAI9216-3:8 | 2 BAY BACK LEFT WALL | 34.C5
AF0081:06 | SC | 008106 | WHT | 20 | 34.B7 | UAI9216-1:8 | 2 BAY BACK LEFT WALL | 34.B5
AF0081:10 | SC | 008110 | WHT | 20 | 70.A7 | UAI9291-1:8 | 2 BAY BACK LEFT WALL | 70.A5
AF0081:36 | SC | 008136 | WHT | 20 | 34.C7 | UAI9216-3:7 | 2 BAY BACK LEFT WALL | 34.C5
AF0081:38 | SC | 008138 | WHT | 20 | 34.B7 | UAI9216-1:7 | 2 BAY BACK LEFT WALL | 34.B5
AF0081:42 | SC | 008142 | WHT | 20 | 70.A7 | UAI9291-1:7 | 2 BAY BACK LEFT WALL | 70.A5
AF0082:00 | SC | 008200 | WHT | 20 | 93.A7 | UAI9214-3:8 | 2 BAY BACK LEFT WALL | 93.A5
AF0082:01 | SC | 008201 | WHT | 20 | 93.B7 | UAI9214-3:11 | 2 BAY BACK LEFT WALL | 93.B5
AF0082:10 | SC | 008210 | WHT | 20 | 34.A7 | UAI9214-1:8 | 2 BAY BACK LEFT WALL | 34.A5
AF0082:11 | SC | 008211 | WHT | 20 | 34.A7 | UAI9214-1:11 | 2 BAY BACK LEFT WALL | 34.A5
AF0082:32 | SC | 008232 | WHT | 20 | 93.A7 | UAI9214-3:7 | 2 BAY BACK LEFT WALL | 93.A5
AF0082:33 | SC | 008233 | WHT | 20 | 93.B7 | UAI9214-3:10 | 2 BAY BACK LEFT WALL | 93.B5
AF0082:42 | SC | 008242 | WHT | 20 | 34.A7 | UAI9214-1:7 | 2 BAY BACK LEFT WALL | 34.A5
AF0082:43 | SC | 008243 | WHT | 20 | 34.A7 | UAI9214-1:10 | 2 BAY BACK LEFT WALL | 34.A5
AF0087:10 | SC | 008710 | WHT | 20 | 111.A7 | UAI9220-1:8 | 2 BAY BACK LEFT WALL | 111.A5
AF0087:42 | SC | 008742 | WHT | 20 | 111.A7 | UAI9220-1:7 | 2 BAY BACK LEFT WALL | 111.A5
AF0091:00 | SC | 009100 | WHT | 20 | 99.C7 | UAI9222-1:8 | 2 BAY BACK LEFT WALL | 99.C5
AF0091:03 | SC | 009103 | WHT | 20 | 75.B7 | UAI9271-1:11 | 2 BAY BACK LEFT WALL | 75.B5
AF0091:14 | SC | 009114 | WHT | 20 | 76.A7 | UAI9270-1:8 | 2 BAY BACK LEFT WALL | 76.A5
AF0091:15 | SC | 009115 | WHT | 20 | 76.B7 | UAI9270-1:11 | 2 BAY BACK LEFT WALL | 76.B5
AF0091:32 | SC | 009132 | WHT | 20 | 99.C7 | UAI9222-1:7 | 2 BAY BACK LEFT WALL | 99.C5
AF0091:35 | SC | 009135 | WHT | 20 | 75.B7 | UAI9271-1:10 | 2 BAY BACK LEFT WALL | 75.B5
AF0091:46 | SC | 009146 | WHT | 20 | 76.A7 | UAI9270-1:7 | 2 BAY BACK LEFT WALL | 76.A5
AF0091:47 | SC | 009147 | WHT | 20 | 76.B7 | UAI9270-1:10 | 2 BAY BACK LEFT WALL | 76.B5
IEG8230:00 | SC | IEG8230-G | GRN | 8 | 4.C2 | IEG8220:0 | 2 BAY BACK LEFT WALL | 4.C2
AF0083:21 | W0832 | 008321 | RED | 20 | 85.A7 | UAI9221-1:-7 | 2 BAY BACK LEFT WALL | 85.A5
AF0083:05 | W0832 | 008305 | WHT | 20 | 85.A7 | UAI9221-1:-5 | 2 BAY BACK LEFT WALL | 85.A5
AF0083:04 | W0832 | 008304 | BLK | 20 | 85.A7 | UAI9221-1:+6 | 2 BAY BACK LEFT WALL | 85.A5
AF0083:52 | W0832 | 008352 | SH | 20 | 85.A7 | FW1208:1 | 2 BAY BACK LEFT WALL | 85.A6
AF0083:25 | W0834 | 008325 | RED | 20 | 85.C7 | UAI9221-3:-7 | 2 BAY BACK LEFT WALL | 85.C5
AF0083:09 | W0834 | 008309 | WHT | 20 | 85.C7 | UAI9221-3:-5 | 2 BAY BACK LEFT WALL | 85.C5
AF0083:08 | W0834 | 008308 | BLK | 20 | 85.C7 | UAI9221-3:+6 | 2 BAY BACK LEFT WALL | 85.C5
AF0083:56 | W0834 | 008356 | SH | 20 | 85.C7 | FW1208:3 | 2 BAY BACK LEFT WALL | 85.D6
AF0083:31 | W0837 | 008331 | RED | 20 | 85.B7 | UAI9221-2:-7 | 2 BAY BACK LEFT WALL | 85.B5
AF0083:15 | W0837 | 008315 | WHT | 20 | 85.B7 | UAI9221-2:-5 | 2 BAY BACK LEFT WALL | 85.B5
AF0083:14 | W0837 | 008314 | BLK | 20 | 85.B7 | UAI9221-2:+6 | 2 BAY BACK LEFT WALL | 85.B5
AF0083:62 | W0837 | 008362 | SH | 20 | 85.B7 | FW1208:2 | 2 BAY BACK LEFT WALL | 85.C6
AF0084:23 | W0843 | 012323 | RED | 20 | 99.A7 | UAI9222A-1:-7 | 2 BAY BACK LEFT WALL | 99.A5
AF0084:07 | W0843 | 012307 | WHT | 20 | 99.A7 | UAI9222A-1:-5 | 2 BAY BACK LEFT WALL | 99.A5
AF0084:06 | W0843 | 012306 | BLK | 20 | 99.A7 | UAI9222A-1:+6 | 2 BAY BACK LEFT WALL | 99.A5
AF0084:54 | W0843 | 012354 | SH | 20 | 99.A7 | FW1215:1 | 2 BAY BACK LEFT WALL | 99.A6
AF0084:25 | W0844 | 012325 | RED | 20 | 99.B7 | UAI9221A-1:-7 | 2 BAY BACK LEFT WALL | 99.B5
AF0084:09 | W0844 | 012309 | WHT | 20 | 99.B7 | UAI9221A-1:-5 | 2 BAY BACK LEFT WALL | 99.B5
AF0084:08 | W0844 | 012308 | BLK | 20 | 99.B7 | UAI9221A-1:+6 | 2 BAY BACK LEFT WALL | 99.B5
AF0084:56 | W0844 | 012356 | SH | 20 | 99.B7 | FW1215:2 | 2 BAY BACK LEFT WALL | 99.B6
AF0084:27 | W0845 | 008427 | RED | 20 | 86.B7 | UAI9221-4:-7 | 2 BAY BACK LEFT WALL | 86.B5
AF0084:11 | W0845 | 008411 | WHT | 20 | 86.B7 | UAI9221-4:-5 | 2 BAY BACK LEFT WALL | 86.B5
AF0084:10 | W0845 | 008410 | BLK | 20 | 86.B7 | UAI9221-4:+6 | 2 BAY BACK LEFT WALL | 86.B5
AF0084:58 | W0845 | 008458 | SH | 20 | 86.B7 | FW-W0845:1 | 2 BAY BACK LEFT WALL | 86.C6
AF0084:29 | W0846 | 008429 | RED | 20 | 86.A7 | UAI9221-5:-7 | 2 BAY BACK LEFT WALL | 86.A5
AF0084:13 | W0846 | 008413 | WHT | 20 | 86.A7 | UAI9221-5:-5 | 2 BAY BACK LEFT WALL | 86.A5
AF0084:12 | W0846 | 008412 | BLK | 20 | 86.A7 | UAI9221-5:+6 | 2 BAY BACK LEFT WALL | 86.A5
AF0084:60 | W0846 | 008460 | SH | 20 | 86.A7 | FW-W0846:1 | 2 BAY BACK LEFT WALL | 86.A6
AF0085:02 | W0851 | 008502 | RED | 20 | 95.A7 | UAI9210-2:+8 | 2 BAY BACK LEFT WALL | 95.A5
AF0085:18 | W0851 | 008518 | BLK | 20 | 95.A7 | UAI9210-2:-7 | 2 BAY BACK LEFT WALL | 95.A5
AF0085:04 | W0852 | 008504 | RED | 20 | 116.A7 | UAI9217-2:+8 | 2 BAY BACK LEFT WALL | 116.A5
AF0085:20 | W0852 | 008520 | BLK | 20 | 116.A7 | UAI9217-2:-7 | 2 BAY BACK LEFT WALL | 116.A5
AF0085:52 | W0852 | 008552 | SH | 20 | 116.A7 | FW0870:1 | 2 BAY BACK LEFT WALL | 116.A6
AF0085:06 | W0853 | 008506 | RED | 20 | 91.C7 | UAI9210-4:+8 | 2 BAY BACK LEFT WALL | 91.C5
AF0085:22 | W0853 | 008522 | BLK | 20 | 91.C7 | UAI9210-4:-7 | 2 BAY BACK LEFT WALL | 91.C5
AF0085:54 | W0853 | 008554 | SH | 20 | 91.C7 | FW0884:1 | 2 BAY BACK LEFT WALL | 91.C6
AF0085:08 | W0854 | 008508 | RED | 20 | 98.A7 | UAI9210-3:+8 | 2 BAY BACK LEFT WALL | 98.A5
AF0085:24 | W0854 | 008524 | BLK | 20 | 98.A7 | UAI9210-3:-7 | 2 BAY BACK LEFT WALL | 98.A5
AF0085:56 | W0854 | 008556 | SH | 20 | 98.A7 | FW0885:1 | 2 BAY BACK LEFT WALL | 98.A6
AF0085:10 | W0855 | 008510 | RED | 20 | 51.A7 | UAI9210-7:+8 | 2 BAY BACK LEFT WALL | 51.A5
AF0085:26 | W0855 | 008526 | BLK | 20 | 51.A7 | UAI9210-7:-7 | 2 BAY BACK LEFT WALL | 51.A5
AF0085:58 | W0855 | 008558 | SH | 20 | 51.A7 | FW0886:1 | 2 BAY BACK LEFT WALL | 51.A6
AF0085:12 | W0856 | 008512 | RED | 20 | 91.B7 | UAI9210-5:+8 | 2 BAY BACK LEFT WALL | 91.B5
AF0085:28 | W0856 | 008528 | BLK | 20 | 91.B7 | UAI9210-5:-7 | 2 BAY BACK LEFT WALL | 91.B5
AF0085:60 | W0856 | 008560 | SH | 20 | 91.B7 | FW0883:1 | 2 BAY BACK LEFT WALL | 91.B6
AF0086:02 | W0861 | 008602 | RED | 20 | 119.B7 | UAI9290-1:+8 | 2 BAY BACK LEFT WALL | 119.B5
AF0086:18 | W0861 | 008618 | BLK | 20 | 119.B7 | UAI9290-1:-7 | 2 BAY BACK LEFT WALL | 119.B5
AF0086:50 | W0861 | 008650 | SH | 20 | 119.B7 | FW7:1 | 2 BAY BACK LEFT WALL | 119.B6
AF0086:06 | W0863 | 008606 | RED | 20 | 112.B7 | UAI9210-6:+8 | 2 BAY BACK LEFT WALL | 112.B5
AF0086:22 | W0863 | 008622 | BLK | 20 | 112.B7 | UAI9210-6:-7 | 2 BAY BACK LEFT WALL | 112.B5
AF0086:54 | W0863 | 008654 | SH | 20 | 112.B7 | FW1203:1 | 2 BAY BACK LEFT WALL | 112.B6
AF0086:08 | W0864 | 008608 | RED | 20 | 119.B7 | UAI9290-2:+8 | 2 BAY BACK LEFT WALL | 119.B5
AF0086:24 | W0864 | 008624 | BLK | 20 | 119.B7 | UAI9290-2:-7 | 2 BAY BACK LEFT WALL | 119.B5
AF0086:56 | W0864 | 008656 | SH | 20 | 119.B7 | FW8:1 | 2 BAY BACK LEFT WALL | 119.B6
AF0081:00 | SC | 008100 | WHT | 20 | 120.B7 | KA0810:14 | 2 BAY LEFT WALL | 120.B5
AF0081:01 | SC | 008101 | WHT | 20 | 120.C7 | KA0811:14 | 2 BAY LEFT WALL | 120.C5
AF0081:32 | SC | 008132 | WHT | 20 | 120.B7 | KA0810:11 | 2 BAY LEFT WALL | 120.B5
AF0081:33 | SC | 008133 | WHT | 20 | 120.C7 | KA0811:11 | 2 BAY LEFT WALL | 120.C5
AF0082:02 | SC | 008202 | WHT | 20 | 120.A7 | KA0822:14 | 2 BAY LEFT WALL | 120.A5
AF0082:03 | SC | 008203 | WHT | 20 | 120.B7 | KA0823:14 | 2 BAY LEFT WALL | 120.B5
AF0082:34 | SC | 008234 | WHT | 20 | 120.A7 | KA0822:11 | 2 BAY LEFT WALL | 120.A5
AF0082:35 | SC | 008235 | WHT | 20 | 120.B7 | KA0823:11 | 2 BAY LEFT WALL | 120.B5
AF0087:07 | SC | 008707 | WHT | 20 | 31.A7 | KA0877:14 | 2 BAY LEFT WALL | 31.A5
AF0087:08 | SC | 008708 | WHT | 20 | 31.B7 | KA0878:14 | 2 BAY LEFT WALL | 31.B5
AF0087:11 | SC | 008711 | WHT | 20 | 36.A7 | KA1820:14 | 2 BAY LEFT WALL | 36.A5
AF0087:12 | SC | 008712 | WHT | 20 | 36.B7 | KA1821:14 | 2 BAY LEFT WALL | 36.B5
AF0087:39 | SC | 008739 | WHT | 20 | 31.A7 | KA0877:11 | 2 BAY LEFT WALL | 31.A5
AF0087:40 | SC | 008740 | WHT | 20 | 31.B7 | KA0878:11 | 2 BAY LEFT WALL | 31.B5
AF0087:43 | SC | 008743 | WHT | 20 | 36.A7 | KA1820:11 | 2 BAY LEFT WALL | 36.A5
AF0087:44 | SC | 008744 | WHT | 20 | 36.B7 | KA1821:11 | 2 BAY LEFT WALL | 36.B5
AF0091:04 | SC | KA013724 | WHT | 20 | 17.C4 | KA0137:24 | 2 BAY LEFT WALL | 17.D3
AF0091:07 | SC | KA014114 | WHT | 20 | 17.C2 | KA0141:14 | 2 BAY LEFT WALL | 17.C2
AF0091:11 | SC | KA013624 | WHT | 20 | 17.B4 | KA0136:24 | 2 BAY LEFT WALL | 17.B3
AF0091:12 | SC | KA0134A1 | WHT | 20 | 94.A7 | KA0134:A1 | 2 BAY LEFT WALL | 17.C6
AF0091:39 | SC | KA014111 | WHT | 20 | 17.C2 | KA0141:11 | 2 BAY LEFT WALL | 17.C2
AF0091:43 | SC | KA013621 | WHT | 20 | 17.B4 | KA0136:21 | 2 BAY LEFT WALL | 17.B3
AF0092:02 | SC | KA0133A1 | WHT | 20 | 92.A7 | KA0133:A1 | 2 BAY LEFT WALL | 17.C6
AF0092:06 | SC | KA013114 | WHT | 20 | 92.A7 | KA0131:14 | 2 BAY LEFT WALL | 17.D4
AF0093:12 | SC | 009312 | WHT | 20 | 35.C7 | PC0470:INP_A | 2 BAY LEFT WALL | 35.C5
AF0093:28 | SC | 009328 | WHT | 20 | 35.C7 | PC0470:PWR_COM | 2 BAY LEFT WALL | 35.C5
AF0093:44 | SC | 009344 | WHT | 20 | 35.C7 | PC0470:(9-28) VDC | 2 BAY LEFT WALL | 35.C5
AF0094:10 | SC | KA0134A1 | WHT | 20 | 94.A7 | KA0134:A1 | 2 BAY LEFT WALL | 17.C6
AF0095:00 | SC | UA1200J21 | WHT | 20 | 18.A7 | KA0241:11 | 2 BAY LEFT WALL | 18.A5
AF0095:01 | SC | KA024314 | WHT | 20 | 18.B7 | KA0243:14 | 2 BAY LEFT WALL | 18.B6
AF0095:02 | SC | KA024524 | WHT | 20 | 18.B7 | KA0245:24 | 2 BAY LEFT WALL | 18.B6
AF0095:06 | SC | KA023924 | WHT | 20 | 18.A7 | KA0239:24 | 2 BAY LEFT WALL | 18.B6
AF0095:11 | SC | KA024214 | WHT | 20 | 18.C7 | KA0242:14 | 2 BAY LEFT WALL | 18.C6
AF0095:33 | SC | KA024311 | WHT | 20 | 18.B7 | KA0243:11 | 2 BAY LEFT WALL | 18.B6
AF0095:34 | SC | KA024521 | WHT | 20 | 18.B7 | KA0245:21 | 2 BAY LEFT WALL | 18.B6
AF0095:38 | SC | KA023921 | WHT | 20 | 18.A7 | KA0239:21 | 2 BAY LEFT WALL | 18.B6
FU0080:LI | SC | FU0137 | WHT | 14 | 8.D1 | XT0139:2 | 2 BAY LEFT WALL | 16.A5
FU0090:LI | SC | FU0137 | WHT | 14 | 8.B1 | XT0139:2 | 2 BAY LEFT WALL | 16.A5
KA0176:A1 | SC | KA014422 | WHT | 20 | 117.B5 | KA0144:22 | 2 BAY LEFT WALL | 117.A6
KA0176:A2 | SC | 0V | WHT | 16 | 117.B5 | XT0235:4 | 2 BAY LEFT WALL | 16.D5
KA0220:14 | SC | KA022014 | WHT | 16 | 64.C5 | KA0250:11 | 2 BAY LEFT WALL | 64.C6
KA0221:11 | SC | 022111 | WHT | 16 | 59.A6 | KA0235:24 | 2 BAY LEFT WALL | 59.A5
KA0222:11 | SC | 022211 | WHT | 16 | 59.B6 | KA0236:24 | 2 BAY LEFT WALL | 59.B5
KA0224:14 | SC | KA024024 | WHT | 20 | 70.B6 | KA0240:14 | 2 BAY LEFT WALL | 70.B5
KA0225:14 | SC | KA023814 | WHT | 20 | 71.B6 | KA0238:14 | 2 BAY LEFT WALL | 71.B5
KA0817:21 | SC | ESTOPB | WHT | 20 | 37.A5 | XT0240:2 | 2 BAY LEFT WALL | 18.A3
KA0817:24 | SC | ESTOPC | WHT | 20 | 37.A5 | XT0240:1 | 2 BAY LEFT WALL | 18.A3
KA1020:14 | SC | FU0211 | WHT | 14 | 44.A5 | FU0211:LD | 2 BAY LEFT WALL | 16.A5
KA1020:24 | SC | 0V | WHT | 14 | 44.A5 | XT0135:5 | 2 BAY LEFT WALL | 16.C5
KA9982:11 | SC | FU0139 | WHT | 20 | 38.A5 | XT0240:12 | 2 BAY LEFT WALL | 18.C4
KA9982:14 | SC | KA0243A1 | WHT | 20 | 38.A5 | XT0240:7 | 2 BAY LEFT WALL | 18.C3
KA9984:11 | SC | FU0139 | WHT | 20 | 38.B5 | XT0240:12 | 2 BAY LEFT WALL | 18.C4
KA9984:14 | SC | KA0245A1 | WHT | 20 | 38.B5 | XT0240:8 | 2 BAY LEFT WALL | 18.D3
UV0600:(-) | SC | 0V | WHT | 14 | 7.B2 | XT0135:1 | 2 BAY LEFT WALL | 16.B5
UV0600:(+) | SC | FU0010 | WHT | 14 | 7.B2 | FU0010:LD | 2 BAY LEFT WALL | 16.A6
XT0080:1 | SC | 0V | WHT | 16 | 8.D1 | XT0135:2 | 2 BAY LEFT WALL | 16.B5
XT0090:1 | SC | 0V | WHT | 16 | 8.B1 | XT0135:2 | 2 BAY LEFT WALL | 16.B5
XT0171:1 | SC | KA017611 | WHT | 20 | 117.C5 | KA0246:11 | 2 BAY LEFT WALL | 117.C5
XT0171:5 | SC | KA017711 | WHT | 20 | 118.C5 | KA0247:11 | 2 BAY LEFT WALL | 118.C5
XT-9300:10 | SC | SB7510-2 | WHT | 20 | 36.A4 | KA1820:A2 | 2 BAY LEFT WALL | 36.A5
XT-9300:11 | SC | SB7511-1 | WHT | 20 | 36.A4 | KA1821:A1 | 2 BAY LEFT WALL | 36.A5
XT-9300:12 | SC | SB7511-2 | WHT | 20 | 36.B4 | KA1821:A2 | 2 BAY LEFT WALL | 36.A5
XT-9300:3 | SC | KA7500-1 | WHT | 20 | 31.A4 | KA0877:A1 | 2 BAY LEFT WALL | 31.A5
XT-9300:4 | SC | KA7500-2 | WHT | 20 | 31.A4 | KA0877:A2 | 2 BAY LEFT WALL | 31.A5
XT-9300:5 | SC | KA7505-1 | WHT | 20 | 31.A4 | KA0878:A1 | 2 BAY LEFT WALL | 31.A5
XT-9300:6 | SC | KA7505-2 | WHT | 20 | 31.B4 | KA0878:A2 | 2 BAY LEFT WALL | 31.A5
XT-9300:9 | SC | SB7510-1 | WHT | 20 | 36.A4 | KA1820:A1 | 2 BAY LEFT WALL | 36.A5
XT-9319:1 | SC | FU0139 | WHT | 16 | 94.C4 | XT0136:1 | 2 BAY LEFT WALL | 17.A2
XT-9319:2 | SC | KM3170-EN | WHT | 16 | 94.C4 | KA0138:11 | 2 BAY LEFT WALL | 94.C6
XT-9324:1 | SC | SV22221 | WHT | 20 | 71.B4 | KA0238:11 | 2 BAY LEFT WALL | 71.B5
XT-9326:2 | SC | UA1200J15 | WHT | 20 | 19.C4 | XT0237:1 B1 | 2 BAY LEFT WALL | 19.C5
XT-9326:5 | SC | UA1200J21 | WHT | 20 | 19.D4 | KA0235:11 | 2 BAY LEFT WALL | 18.A5
XT-9326:6 | SC | FU0212 | WHT | 16 | 19.D4 | FU0212:LD | 2 BAY LEFT WALL | 16.C6
XT-9326:7 | SC | 0V | WHT | 16 | 19.D4 | XT0235:2 | 2 BAY LEFT WALL | 16.D5
XT-9329:7 | SC | FCE21307 | WHT | 20 | 55.B5 | KA0237:11 | 2 BAY LEFT WALL | 55.B5
XT-9330:3 | SC | SV2120-1 | WHT | 16 | 59.A4 | KA0235:21 | 2 BAY LEFT WALL | 59.A5
XT-9330:7 | SC | SV2124-1 | WHT | 16 | 59.B4 | KA0236:21 | 2 BAY LEFT WALL | 59.B5
AF0083:19 | W0831 | 008319 | RED | 20 | 82.A7 | UAI9207-2:-7 | 2 BAY LEFT WALL | 82.A5
AF0083:03 | W0831 | 008303 | WHT | 20 | 82.A7 | UAI9207-2:-5 | 2 BAY LEFT WALL | 82.A5
AF0083:02 | W0831 | 008302 | BLK | 20 | 82.A7 | UAI9207-2:+6 | 2 BAY LEFT WALL | 82.A5
AF0083:50 | W0831 | 008350 | SH | 20 | 82.A7 | FLOATING | 2 BAY LEFT WALL | 82.A6
AF0083:23 | W0833 | 008323 | RED | 20 | 90.A7 | UAI9207-1:-7 | 2 BAY LEFT WALL | 90.A5
AF0083:07 | W0833 | 008307 | WHT | 20 | 90.A7 | UAI9207-1:-5 | 2 BAY LEFT WALL | 90.A5
AF0083:06 | W0833 | 008306 | BLK | 20 | 90.A7 | UAI9207-1:+6 | 2 BAY LEFT WALL | 90.A5
AF0083:54 | W0833 | 008354 | SH | 20 | 90.A7 | FLOATING | 2 BAY LEFT WALL | 90.B6
AF0083:27 | W0835 | 008327 | RED | 20 | 47.A7 | UAI9205-2:-7 | 2 BAY LEFT WALL | 47.A5
AF0083:11 | W0835 | 008311 | WHT | 20 | 47.A7 | UAI9205-2:-5 | 2 BAY LEFT WALL | 47.A5
AF0083:10 | W0835 | 008310 | BLK | 20 | 47.A7 | UAI9205-2:+6 | 2 BAY LEFT WALL | 47.A5
AF0083:58 | W0835 | 008358 | SH | 20 | 47.A7 | FLOATING | 2 BAY LEFT WALL | 47.A6
AF0083:29 | W0836 | 008329 | RED | 20 | 115.A7 | UAI9205-5:-7 | 2 BAY LEFT WALL | 115.A5
AF0083:13 | W0836 | 008313 | WHT | 20 | 115.A7 | UAI9205-5:-5 | 2 BAY LEFT WALL | 115.A5
AF0083:12 | W0836 | 008312 | BLK | 20 | 115.A7 | UAI9205-5:+6 | 2 BAY LEFT WALL | 115.A5
AF0083:60 | W0836 | 008360 | SH | 20 | 115.A7 | FW1201:1 | 2 BAY LEFT WALL | 115.A6
AF0084:17 | W0840 | 008417 | RED | 20 | 91.A7 | UAI9205-3:-7 | 2 BAY LEFT WALL | 91.A5
AF0084:01 | W0840 | 008401 | WHT | 20 | 91.A7 | UAI9205-3:-5 | 2 BAY LEFT WALL | 91.A5
AF0084:00 | W0840 | 008400 | BLK | 20 | 91.A7 | UAI9205-3:+6 | 2 BAY LEFT WALL | 91.A5
AF0084:48 | W0840 | 008448 | SH | 20 | 91.A7 | FW1?:1 | 2 BAY LEFT WALL | 91.A6
AF0084:19 | W0841 | 008419 | RED | 20 | 97.A7 | UAI9205-4:-7 | 2 BAY LEFT WALL | 97.A5
AF0084:03 | W0841 | 008403 | WHT | 20 | 97.A7 | UAI9205-4:-5 | 2 BAY LEFT WALL | 97.A5
AF0084:02 | W0841 | 008402 | BLK | 20 | 97.A7 | UAI9205-4:+6 | 2 BAY LEFT WALL | 97.A5
AF0084:50 | W0841 | 008450 | SH | 20 | 97.A7 | FLOATING | 2 BAY LEFT WALL | 97.A6
AF0084:21 | W0842 | 008421 | RED | 20 | 77.A7 | UAI9205-6:-7 | 2 BAY LEFT WALL | 77.A5
AF0084:05 | W0842 | 008405 | WHT | 20 | 77.A7 | UAI9205-6:-5 | 2 BAY LEFT WALL | 77.A5
AF0084:04 | W0842 | 008404 | BLK | 20 | 77.A7 | UAI9205-6:+6 | 2 BAY LEFT WALL | 77.A5
AF0084:52 | W0842 | 008452 | SH | 20 | 77.A7 | FW1202:1 | 2 BAY LEFT WALL | 77.A6
AF0087:05 | SC | SB6200-24 | WHT | 20 | 35.A7 | XT-9381:17 | 2 BAY RIGHT WALL | 35.A4
AF0087:37 | SC | SB6200-23 | WHT | 20 | 35.A7 | XT-9381:16 | 2 BAY RIGHT WALL | 35.A4
AF0092:01 | SC | SV6431-1 | WHT | 16 | 75.C7 | XT-9370:7 | 2 BAY RIGHT WALL | 75.C4
AF0092:13 | SC | SV6432-1 | WHT | 16 | 76.C7 | XT-9370:1 | 2 BAY RIGHT WALL | 76.C4
AF0092:14 | SC | SV6433-1 | WHT | 16 | 76.D7 | XT-9370:3 | 2 BAY RIGHT WALL | 76.D4
AF0092:15 | SC | SV6434-1 | WHT | 16 | 76.D7 | XT-9370:5 | 2 BAY RIGHT WALL | 76.D4
AF0092:17 | SC | SV6431-2 | WHT | 16 | 75.C7 | XT-9370:8 | 2 BAY RIGHT WALL | 75.C4
AF0092:29 | SC | SV6432-2 | WHT | 16 | 76.C7 | XT-9370:2 | 2 BAY RIGHT WALL | 76.C4
AF0092:30 | SC | SV6433-2 | WHT | 16 | 76.D7 | XT-9370:4 | 2 BAY RIGHT WALL | 76.D4
AF0092:31 | SC | SV6434-2 | WHT | 16 | 76.D7 | XT-9370:6 | 2 BAY RIGHT WALL | 76.D4
AF0093:15 | SC | HL6200-1 | WHT | 20 | 35.A7 | XT-9381:19 | 2 BAY RIGHT WALL | 35.B4
AF0093:31 | SC | HL6200-2 | WHT | 20 | 35.A7 | XT-9381:20 | 2 BAY RIGHT WALL | 35.B4
AF0094:00 | SC | HA1300-2 | WHT | 16 | 106.A7 | XT-9381:13 | 2 BAY RIGHT WALL | 106.A4
AF0094:16 | SC | HA1300-1 | WHT | 16 | 106.A7 | XT-9381:14 | 2 BAY RIGHT WALL | 106.A4
IEG8230:0 | SC | IEG8240-G | GRN | 8 | 4.D2 | IEG8240:00 | 2 BAY RIGHT WALL | 4.D2
KA0220:11 | SC | FCE2225-5 | WHT | 16 | 64.C5 | XT-9338:1 | 2 BAY RIGHT WALL | 64.C4
KA0220:A1 | SC | 007603 | WHT | 20 | 64.C5 | AF0076:03 | 2 BAY RIGHT WALL | 64.C7
KA0220:A2 | SC | 007619 | WHT | 20 | 64.C5 | AF0076:19 | 2 BAY RIGHT WALL | 64.C7
KA0221:A1 | SC | 007602 | WHT | 20 | 59.A6 | AF0076:02 | 2 BAY RIGHT WALL | 59.A7
KA0221:A2 | SC | 007618 | WHT | 20 | 59.A6 | AF0076:18 | 2 BAY RIGHT WALL | 59.A7
KA0222:14 | SC | 006200 | WHT | 16 | 59.B6 | AF0067:02 | 2 BAY RIGHT WALL | 59.B7
KA0222:A1 | SC | 007604 | WHT | 20 | 59.B6 | AF0076:04 | 2 BAY RIGHT WALL | 59.B7
KA0222:A2 | SC | 007620 | WHT | 20 | 59.B6 | AF0076:20 | 2 BAY RIGHT WALL | 59.B7
KA0224:11 | SC | 006706 | WHT | 20 | 70.B6 | AF0067:06 | 2 BAY RIGHT WALL | 70.B7
KA0224:A1 | SC | 007605 | WHT | 20 | 70.B6 | AF0076:05 | 2 BAY RIGHT WALL | 70.B7
KA0224:A2 | SC | 007621 | WHT | 20 | 70.B6 | AF0076:21 | 2 BAY RIGHT WALL | 70.B7
KA0225:11 | SC | 005204 | WHT | 20 | 71.B6 | AF0052:04 | 2 BAY RIGHT WALL | 71.B7
KA0225:A1 | SC | 007606 | WHT | 20 | 71.B6 | AF0076:06 | 2 BAY RIGHT WALL | 71.B7
KA0225:A2 | SC | 007622 | WHT | 20 | 71.B6 | AF0076:22 | 2 BAY RIGHT WALL | 71.B7
KA0701:A1 | SC | 006106 | WHT | 20 | 23.D5 | AF0061:06 | 2 BAY RIGHT WALL | 23.D6
KA0701:A2 | SC | 006122 | WHT | 20 | 23.D5 | AF0061:22 | 2 BAY RIGHT WALL | 23.D6
KA076E:11 | SC | YK7175-1 | WHT | 20 | 121.B5 | XT-9350:11 | 2 BAY RIGHT WALL | 121.B4
KA076E:14 | SC | YK7175-2 | WHT | 20 | 121.B5 | XT-9350:12 | 2 BAY RIGHT WALL | 121.B4
KA076E:A1 | SC | 007614 | WHT | 20 | 121.B5 | AF0076:14 | 2 BAY RIGHT WALL | 121.B7
KA076E:A2 | SC | 007630 | WHT | 20 | 121.B5 | AF0076:30 | 2 BAY RIGHT WALL | 121.B7
KA1020:A1 | SC | 007607 | WHT | 20 | 35.B5 | AF0076:07 | 2 BAY RIGHT WALL | 35.B7
KA1020:A2 | SC | 007623 | WHT | 20 | 35.B5 | AF0076:23 | 2 BAY RIGHT WALL | 35.B7
XT-9324:10 | SC | SV2614-2 | WHT | 16 | 78.D4 | AF0053:24 | 2 BAY RIGHT WALL | 78.D7
XT-9324:2 | SC | SV22222 | WHT | 16 | 71.B4 | AF0052:20 | 2 BAY RIGHT WALL | 71.B7
XT-9324:3 | SC | SV2260-1 | WHT | 16 | 80.C4 | AF0052:02 | 2 BAY RIGHT WALL | 80.C7
XT-9324:4 | SC | SV2260-2 | WHT | 16 | 80.C4 | AF0052:18 | 2 BAY RIGHT WALL | 80.C7
XT-9324:5 | SC | SV1720-1 | WHT | 20 | 53.D5 | AF0067:08 | 2 BAY RIGHT WALL | 53.D7
XT-9324:6 | SC | SV1720-2 | WHT | 20 | 53.D5 | AF0067:24 | 2 BAY RIGHT WALL | 53.D7
XT-9324:7 | SC | SV2610-1 | WHT | 16 | 62.B4 | AF0053:06 | 2 BAY RIGHT WALL | 62.B7
XT-9324:8 | SC | SV2610-2 | WHT | 16 | 62.B4 | AF0053:22 | 2 BAY RIGHT WALL | 62.B7
XT-9324:9 | SC | SV2614-1 | WHT | 16 | 78.D4 | AF0053:08 | 2 BAY RIGHT WALL | 78.D7
XT-9326:1 | SC | UA1200J14 | WHT | 20 | 19.C4 | AF0076:11 | 2 BAY RIGHT WALL | 19.C7
XT-9327:1 | SC | SV2250-1 | WHT | 16 | 72.C4 | AF0052:08 | 2 BAY RIGHT WALL | 72.C7
XT-9327:10 | SC | SV2647-2 | WHT | 16 | 77.C4 | AF0051:24 | 2 BAY RIGHT WALL | 77.C7
XT-9327:2 | SC | SV2250-2 | WHT | 16 | 72.C4 | AF0052:24 | 2 BAY RIGHT WALL | 72.C7
XT-9327:3 | SC | SV2251-1 | WHT | 16 | 72.D4 | AF0052:10 | 2 BAY RIGHT WALL | 72.C7
XT-9327:4 | SC | SV2251-2 | WHT | 16 | 72.D4 | AF0052:26 | 2 BAY RIGHT WALL | 72.C7
XT-9327:5 | SC | SV2645-1 | WHT | 16 | 77.B4 | AF0051:04 | 2 BAY RIGHT WALL | 77.B7
XT-9327:6 | SC | SV2645-2 | WHT | 16 | 77.B4 | AF0051:20 | 2 BAY RIGHT WALL | 77.B7
XT-9327:7 | SC | SV2646-1 | WHT | 16 | 77.C4 | AF0051:06 | 2 BAY RIGHT WALL | 77.C7
XT-9327:8 | SC | SV2646-2 | WHT | 16 | 77.C4 | AF0051:22 | 2 BAY RIGHT WALL | 77.C7
XT-9327:9 | SC | SV2647-1 | WHT | 16 | 77.C4 | AF0051:08 | 2 BAY RIGHT WALL | 77.C7
XT-9329:10 | SC | FCE21309 | WHT | 20 | 55.B5 | AF0061:04 | 2 BAY RIGHT WALL | 55.C7
XT-9329:11 | SC | FCE213010 | WHT | 20 | 55.B5 | AF0061:20 | 2 BAY RIGHT WALL | 55.C7
XT-9329:13 | SC | FCE213011 | WHT | 20 | 55.C5 | AF0063:35 | 2 BAY RIGHT WALL | 55.C7
XT-9329:14 | SC | FCE213012 | WHT | 20 | 55.C5 | AF0063:03 | 2 BAY RIGHT WALL | 55.C7
XT-9329:16 | SC | FCE213013 | WHT | 20 | 55.C5 | AF0063:34 | 2 BAY RIGHT WALL | 55.D7
XT-9329:17 | SC | FCE213014 | WHT | 20 | 55.C5 | AF0063:02 | 2 BAY RIGHT WALL | 55.D7
XT-9329:8 | SC | FCE21308 | WHT | 20 | 55.B5 | AF0076:16 | 2 BAY RIGHT WALL | 55.B7
XT-9330:1 | SC | SV6430-1 | WHT | 16 | 75.B4 | AF0053:02 | 2 BAY RIGHT WALL | 75.B7
XT-9330:2 | SC | SV6430-2 | WHT | 16 | 75.C4 | AF0053:18 | 2 BAY RIGHT WALL | 75.B7
XT-9330:5 | SC | SV2121-1 | WHT | 16 | 59.C4 | AF0067:04 | 2 BAY RIGHT WALL | 59.C7
XT-9330:6 | SC | SV2121-2 | WHT | 16 | 59.C4 | AF0067:20 | 2 BAY RIGHT WALL | 59.C7
XT-9330:8 | SC | SV2124-2 | WHT | 16 | 59.C4 | AF0067:18 | 2 BAY RIGHT WALL | 59.B7
XT-9312:4 | W0570 | SM7632-1 | RED | 20 | 42.A4 | AF0057:00 | 2 BAY RIGHT WALL | 42.A7
XT-9312:5 | W0570 | SM7632-2 | BLK | 20 | 42.A4 | AF0057:16 | 2 BAY RIGHT WALL | 42.A7
XT-9312:6 | W0570 | SM7632-S | SH | 20 | 42.A4 | AF0057:48 | 2 BAY RIGHT WALL | 42.A7
XT-9312:1 | W0571 | SM7633-1 | RED | 20 | 42.A4 | AF0057:02 | 2 BAY RIGHT WALL | 42.A7
XT-9312:2 | W0571 | SM7633-2 | BLK | 20 | 42.A4 | AF0057:18 | 2 BAY RIGHT WALL | 42.A7
XT-9312:3 | W0571 | SM7633-S | SH | 20 | 42.B4 | AF0057:50 | 2 BAY RIGHT WALL | 42.A7
XT-9312:21 | W0572 | SM7634-1 | RED | 20 | 42.B4 | AF0057:04 | 2 BAY RIGHT WALL | 42.B7
XT-9312:22 | W0572 | SM7634-2 | BLK | 20 | 42.B4 | AF0057:20 | 2 BAY RIGHT WALL | 42.B7
XT-9312:23 | W0572 | SM7634-S | SH | 20 | 42.B4 | AF0057:52 | 2 BAY RIGHT WALL | 42.B7
XT-9312:28 | W0573 | SM7635-1 | RED | 20 | 42.B4 | AF0057:06 | 2 BAY RIGHT WALL | 42.B7
XT-9312:29 | W0573 | SM7635-2 | BLK | 20 | 42.C4 | AF0057:22 | 2 BAY RIGHT WALL | 42.B7
XT-9312:30 | W0573 | SM7635-S | SH | 20 | 42.C4 | AF0057:54 | 2 BAY RIGHT WALL | 42.B7
XT-9325A:1 | W0710 | SE1260-1 | RED | 20 | 81.A5 | AF0071:04 | 2 BAY RIGHT WALL | 81.A7
XT-9325A:2 | W0710 | SE1260-2 | BLK | 20 | 81.A5 | AF0071:20 | 2 BAY RIGHT WALL | 81.A7
XT-9325A:3 | W0710 | SE1260-S1 | SH | 20 | 81.A5 | AF0071:52 | 2 BAY RIGHT WALL | 81.A7
AF0085:14 | W0857 | FCE1440-3 | RED | 20 | 46.A7 | XT-9336:4 | 2 BAY RIGHT WALL | 46.A5
AF0085:30 | W0857 | FCE1440-4 | BLK | 20 | 46.A7 | XT-9336:5 | 2 BAY RIGHT WALL | 46.A5
AF0085:62 | W0857 | FCE1440-S2 | SH | 20 | 46.A7 | XT-9336:6 | 2 BAY RIGHT WALL | 46.A5
AF0086:00 | W0860 | FCE1440-5 | RED | 20 | 46.B7 | XT-9336:7 | 2 BAY RIGHT WALL | 46.B5
AF0086:16 | W0860 | FCE1440-6 | BLK | 20 | 46.B7 | XT-9336:8 | 2 BAY RIGHT WALL | 46.B5
AF0086:48 | W0860 | FCE1440-S3 | SH | 20 | 46.B7 | XT-9336:9 | 2 BAY RIGHT WALL | 46.B5
AF0086:12 | W0866 | FT2108-1 | RED | 20 | 61.C7 | XT-9380:4 | 2 BAY RIGHT WALL | 61.C4
AF0086:28 | W0866 | FT2108-2 | BLK | 20 | 61.C7 | XT-9380:5 | 2 BAY RIGHT WALL | 61.C4
AF0086:60 | W0866 | FT2108-S1 | SH | 20 | 61.C7 | XT-9380:6 | 2 BAY RIGHT WALL | 61.C4
AU0080:L2 | WC0008 | AU0080L2 | ENET | CABLE | 3.A4 | AU0070:L1 | 2 BAY RIGHT WALL | 3.A5
AF0085:00 | WC4191 | FCE1420-5 | RED | 20 | 45.B7 | XT-9335:4 | 2 BAY RIGHT WALL | 45.B5
AF0085:16 | WC4191 | FCE1420-6 | BLK | 20 | 45.B7 | XT-9335:5 | 2 BAY RIGHT WALL | 45.B5
AF0085:48 | WC4191 | FCE1420-S2 | SH | 20 | 45.B7 | XT-9335:6 | 2 BAY RIGHT WALL | 45.B5
XT-9329:1 | WC4681 | FCE21301 | RED | 20 | 55.A5 | AF0066:04 | 2 BAY RIGHT WALL | 55.A7
XT-9329:2 | WC4681 | FCE21302 | BLK | 20 | 55.A5 | AF0066:20 | 2 BAY RIGHT WALL | 55.A7
XT-9329:3 | WC4681 | FCE2130S1 | SH | 20 | 55.A5 | AF0066:52 | 2 BAY RIGHT WALL | 55.A7
XT-9329:4 | WC4682 | FCE21305 | RED | 20 | 55.A5 | AF0074:00 | 2 BAY RIGHT WALL | 55.B7
XT-9329:5 | WC4682 | FCE21306 | BLK | 20 | 55.B5 | AF0074:16 | 2 BAY RIGHT WALL | 55.B7
XT-9329:6 | WC4682 | FCE2130S2 | SH | 20 | 55.B5 | AF0074:48 | 2 BAY RIGHT WALL | 55.B7
AF0081:05 | SC | TCP18B2 | WHT | 20 | 14.D6 | SB0400:22 | ASSEMBLY^CONTROL PANEL | 14.D5
AF0081:37 | SC | TCP18B1 | WHT | 20 | 14.D6 | SB0400:21 | ASSEMBLY^CONTROL PANEL | 14.D5
AF0082:06 | SC | 0612NO | WHT | 20 | 23.D2 | AP0612:NO | ORBIT 60^DOOR PANEL | 23.D2
AF0082:07 | SC | 0628NO1 | WHT | 20 | 23.D1 | AP0628:NO1 | ORBIT 60^DOOR PANEL | 23.D1
AF0082:08 | SC | 0628NO2 | WHT | 20 | 23.D3 | AP0628:NO2 | ORBIT 60^DOOR PANEL | 23.D3
AF0082:09 | SC | 0628NO3 | WHT | 20 | 23.D4 | AP0628:NO3 | ORBIT 60^DOOR PANEL | 23.D4
AF0082:38 | SC | 0612ARM | WHT | 20 | 23.D2 | AP0612:ARM | ORBIT 60^DOOR PANEL | 23.D2
AF0082:39 | SC | 0628ARM1 | WHT | 20 | 23.D1 | AP0628:ARM1 | ORBIT 60^DOOR PANEL | 23.D1
AF0082:40 | SC | 0628ARM2 | WHT | 20 | 23.D3 | AP0628:ARM2 | ORBIT 60^DOOR PANEL | 23.D3
AF0082:41 | SC | 0628ARM3 | WHT | 20 | 23.D4 | AP0628:ARM3 | ORBIT 60^DOOR PANEL | 23.D4
KA0701:11 | SC | 0612TM | WHT | 20 | 23.D6 | AP0612:TM | ORBIT 60^DOOR PANEL | 23.D6
KA0701:14 | SC | 0612COM | WHT | 20 | 23.D6 | AP0612:COM | ORBIT 60^DOOR PANEL | 23.D6
AP0605:ENET | WC0609 | AP0605ENET | ENET | CABLE | 23.C4 | AP0615:PORT A | ORBIT 60^DOOR PANEL | 23.C2
AP0606:L1 | WC0680 | AP0606L1 | ENET | CABLE | 5.C4 | AT0680:LAN1 | PWR,DISTRIBUTION RAIL^LEFT DOOR | 5.A4
SolarTools ver. 24.0.84.26264 (Jun 3, 2025)
Report date: 7/10/2025 2:57 PM

## 2 BAY LEFT WALL
2 BAY LEFT WALL
Project # | G9440
Project Name | NOC AL SHAHEEN T130
Revision | A.5
Controls DE | G. Colby
Phone:
Controls ME | R. Duran
Phone:
From | [5 empty] | To
Device ID | Cable (W) Conductor (SC) Jumper Clip (JC) | Wire No. | Wire ID | Gauge/Size | Page/Zone | Device ID | Location | Page/Zone
XT0134:1 | JC | 0V | CLIP | --- | 16.B4 | XT0134:2 | 2 BAY LEFT WALL | 16.B4
XT0134:2 | JC | 0V | CLIP | --- | 16.B4 | XT0134:3 | 2 BAY LEFT WALL | 16.B4
XT0134:3 | JC | 0V | CLIP | --- | 16.B4 | XT0134:4 | 2 BAY LEFT WALL | 16.B4
XT0135:1 | JC | 0V | CLIP | --- | 16.B5 | XT0135:2 | 2 BAY LEFT WALL | 16.B5
XT0135:2 | JC | 0V | CLIP | --- | 16.B5 | XT0135:3 | 2 BAY LEFT WALL | 16.B5
XT0135:3 | JC | 0V | CLIP | --- | 16.B5 | XT0135:4 | 2 BAY LEFT WALL | 16.B5
XT0135:4 | JC | 0V | CLIP | --- | 16.B5 | XT0135:5 | 2 BAY LEFT WALL | 16.C5
XT0136:1 | JC | FU0139 | CLIP | --- | 17.A2 | XT0136:2 | 2 BAY LEFT WALL | 17.A2
XT0138:1 | JC | FU0136 | CLIP | --- | 16.A4 | XT0138:2 | 2 BAY LEFT WALL | 16.A4
XT0138:2 | JC | FU0136 | CLIP | --- | 16.A4 | XT0138:3 | 2 BAY LEFT WALL | 16.A4
XT0138:3 | JC | FU0136 | CLIP | --- | 16.A4 | XT0138:4 | 2 BAY LEFT WALL | 16.A4
XT0139:1 | JC | FU0137 | CLIP | --- | 16.A5 | XT0139:2 | 2 BAY LEFT WALL | 16.A5
XT0139:2 | JC | FU0137 | CLIP | --- | 16.A5 | XT0139:3 | 2 BAY LEFT WALL | 16.A5
XT0139:3 | JC | FU0137 | CLIP | --- | 16.A5 | XT0139:4 | 2 BAY LEFT WALL | 16.A5
XT0139:4 | JC | FU0137 | CLIP | --- | 16.A5 | XT0139:5 | 2 BAY LEFT WALL | 16.B5
XT0233:1 | JC | FU0210 | CLIP | --- | 16.C5 | XT0233:2 | 2 BAY LEFT WALL | 16.C5
XT0233:2 | JC | FU0210 | CLIP | --- | 16.C5 | XT0233:3 | 2 BAY LEFT WALL | 16.C5
XT0235:1 | JC | 0V | CLIP | --- | 16.D5 | XT0235:2 | 2 BAY LEFT WALL | 16.D5
XT0235:2 | JC | 0V | CLIP | --- | 16.D5 | XT0235:3 | 2 BAY LEFT WALL | 16.D5
XT0240:11 | JC | FU0139 | CLIP | --- | 18.C4 | XT0240:12 | 2 BAY LEFT WALL | 18.C4
XT0240:9 | JC | 0V | CLIP | --- | 18.D3 | XT0240:10 | 2 BAY LEFT WALL | 18.D3
XT0240:2 | SC | JP0 | VIO | 20 | 18.A3 | XT0240:1 | 2 BAY LEFT WALL | 18.A3
FU0010:LI | SC | FU0137 | WHT | 14 | 16.A6 | XT0139:1 | 2 BAY LEFT WALL | 16.A5
FU0136:LD | SC | FU0136 | WHT | 10 | 16.A4 | XT0138:1 | 2 BAY LEFT WALL | 16.A4
FU0137:LD | SC | FU0137 | WHT | 12 | 16.A4 | XT0139:1 | 2 BAY LEFT WALL | 16.A5
FU0137:LI | SC | FU0136 | WHT | 12 | 16.A4 | XT0138:1 | 2 BAY LEFT WALL | 16.A4
FU0139:LD | SC | FU0139 | WHT | 14 | 16.A6 | XT0136:1 | 2 BAY LEFT WALL | 17.A2
FU0139:LI | SC | FU0137 | WHT | 14 | 16.A6 | XT0139:1 | 2 BAY LEFT WALL | 16.A5
FU0170:LD | SC | FU0170 | WHT | 16 | 16.C6 | KA0232:21 | 2 BAY LEFT WALL | 117.A6
FU0170:LI | SC | FU0210 | WHT | 12 | 16.C6 | XT0233:4 | 2 BAY LEFT WALL | 16.C5
FU0210:LD | SC | FU0210 | WHT | 12 | 16.C4 | XT0233:1 | 2 BAY LEFT WALL | 16.C5
FU0210:LI | SC | FU0136 | WHT | 12 | 16.C4 | XT0138:4 | 2 BAY LEFT WALL | 16.A4
FU0211:LI | SC | FU0137 | WHT | 12 | 16.A5 | XT0139:3 | 2 BAY LEFT WALL | 16.A5
FU0212:LD | SC | FU0212 | WHT | 16 | 16.C6 | KA0248:11 | 2 BAY LEFT WALL | 19.C6
FU0212:LI | SC | FU0210 | WHT | 14 | 16.C6 | XT0233:1 | 2 BAY LEFT WALL | 16.C5
FU0271:LD | SC | UV0271P | WHT | 16 | 16.B2 | UV0271:8+ | 2 BAY LEFT WALL | 16.B1
FU0271:LI | SC | FU0137 | WHT | 14 | 16.B2 | XT0139:3 | 2 BAY LEFT WALL | 16.A5
FU0281:LI | SC | FU0137 | WHT | 14 | 16.C2 | XT0139:3 | 2 BAY LEFT WALL | 16.A5
FU0291:LI | SC | FU0137 | WHT | 14 | 16.D2 | XT0139:4 | 2 BAY LEFT WALL | 16.A5
GR9211: | SC | GR9211 | GRN/YEL | 14 | 4.B4 | FRAME | 2 BAY LEFT WALL | 4.B3
GR9212: | SC | GR9212 | GRN/YEL | 14 | 4.B4 | FRAME | 2 BAY LEFT WALL | 4.B4
GR9213: | SC | GR9213 | GRN/YEL | 14 | 4.B5 | FRAME | 2 BAY LEFT WALL | 4.B5
HIEG8210:1 | SC | HIEG8210-1 | GRN | 14 | 16.B1 | UV0271:IE | 2 BAY LEFT WALL | 16.B1
HIEG8210:2 | SC | HIEG8210-2 | GRN | 14 | 16.C1 | UV0272:IE | 2 BAY LEFT WALL | 16.B1
KA0131:12 | SC | KA013724 | WHT | 20 | 17.D4 | KA0137:24 | 2 BAY LEFT WALL | 17.D3
KA0131:A1 | SC | KA0231A1 | WHT | 20 | 17.B6 | KA0132:A1 | 2 BAY LEFT WALL | 17.B6
KA0131:A1 | SC | KA0231A1 | WHT | 20 | 17.B6 | XT0136:10 | 2 BAY LEFT WALL | 17.B5
KA0131:A2 | SC | 0V | WHT | 20 | 17.B6 | KT0145:A2 | 2 BAY LEFT WALL | 17.B6
KA0131:A2 | SC | 0V | WHT | 20 | 17.B6 | KA0132:A2 | 2 BAY LEFT WALL | 17.B6
KA0132:11 | SC | FU0139 | WHT | 20 | 17.A3 | KA0133:11 | 2 BAY LEFT WALL | 17.A3
KA0132:11 | SC | FU0139 | WHT | 20 | 17.A3 | KT0145:15 | 2 BAY LEFT WALL | 17.D2
KA0132:12 | SC | KT0141A1 | WHT | 20 | 17.A3 | KT0142:A1 | 2 BAY LEFT WALL | 17.A6
KA0132:12 | SC | KT0141A1 | WHT | 20 | 17.A3 | KA0133:12 | 2 BAY LEFT WALL | 17.A3
KA0132:21 | SC | KA0138A1 | WHT | 20 | 17.D4 | KA0138:A1 | 2 BAY LEFT WALL | 17.D6
KA0132:22 | SC | KA013222 | WHT | 20 | 17.D4 | KA0137:14 | 2 BAY LEFT WALL | 17.D3
KA0132:22 | SC | KA013222 | WHT | 20 | 17.D4 | KT0141:18 | 2 BAY LEFT WALL | 17.D2
KA0132:24 | SC | KA013224 | WHT | 20 | 17.D4 | KA0134:14 | 2 BAY LEFT WALL | 17.D3
KA0132:A1 | SC | KA0231A1 | WHT | 20 | 17.B6 | KA0141:A1 | 2 BAY LEFT WALL | 17.C6
KA0132:A2 | SC | 0V | WHT | 20 | 17.B6 | KA0141:A2 | 2 BAY LEFT WALL | 17.C6
KA0133:11 | SC | FU0139 | WHT | 20 | 17.A3 | KA0134:11 | 2 BAY LEFT WALL | 17.D3
KA0133:A2 | SC | 0V | WHT | 20 | 17.C6 | KA0141:A2 | 2 BAY LEFT WALL | 17.C6
KA0133:A2 | SC | 0V | WHT | 20 | 17.C6 | KA0134:A2 | 2 BAY LEFT WALL | 17.C6
KA0134:11 | SC | FU0139 | WHT | 20 | 17.D3 | KA0136:11 | 2 BAY LEFT WALL | 17.B4
KA0134:A2 | SC | 0V | WHT | 20 | 17.C6 | KA0144:A2 | 2 BAY LEFT WALL | 17.C6
KA0136:11 | SC | FU0139 | WHT | 20 | 17.B4 | KA0137:21 | 2 BAY LEFT WALL | 17.D3
KA0136:14 | SC | KA013821 | WHT | 20 | 17.B4 | KA0138:21 | 2 BAY LEFT WALL | 17.B5
KA0136:A2 | SC | 0V | WHT | 20 | 17.D6 | KA0137:A2 | 2 BAY LEFT WALL | 17.D6
KA0137:11 | SC | FU0139 | WHT | 20 | 17.D3 | KA0137:21 | 2 BAY LEFT WALL | 17.D3
KA0137:A1 | SC | KA0137A1 | WHT | 20 | 17.D6 | KT0142:18 | 2 BAY LEFT WALL | 17.D2
KA0137:A2 | SC | 0V | WHT | 20 | 17.D6 | KA0138:A2 | 2 BAY LEFT WALL | 17.D6
KA0138:14 | SC | 0V | WHT | 16 | 94.C6 | XT0136:3 | 2 BAY LEFT WALL | 17.A2
KA0138:24 | SC | KT0144B1 | WHT | 20 | 17.B5 | KT0144:B1 | 2 BAY LEFT WALL | 17.B6
KA0141:21 | SC | KT0146A1 | WHT | 20 | 17.B2 | KT0146:A1 | 2 BAY LEFT WALL | 17.B2
KA0141:21 | SC | KT0146A1 | WHT | 20 | 17.B2 | KA0241:21 | 2 BAY LEFT WALL | 17.B2
KA0141:24 | SC | FU0139 | WHT | 20 | 17.B2 | KA0241:24 | 2 BAY LEFT WALL | 17.B2
KA0141:24 | SC | FU0139 | WHT | 20 | 17.B2 | XT0136:2 | 2 BAY LEFT WALL | 17.A2
KA0144:22 | SC | KA014422 | WHT | 20 | 117.A6 | KA0249:12 | 2 BAY LEFT WALL | 117.B6
KA0231:11 | SC | KA0231A1 | WHT | 20 | 18.C6 | KA0231:A1 | 2 BAY LEFT WALL | 18.C6
KA0231:11 | SC | KA0231A1 | WHT | 20 | 18.C6 | KA0242:11 | 2 BAY LEFT WALL | 18.C6
KA0231:14 | SC | KA024214 | WHT | 20 | 18.C6 | KA0242:14 | 2 BAY LEFT WALL | 18.C6
KA0231:14 | SC | KA024214 | WHT | 20 | 18.C6 | KT0146:18 | 2 BAY LEFT WALL | 18.C6
KA0231:21 | SC | KA023121 | WHT | 20 | 18.A4 | KA0245:14 | 2 BAY LEFT WALL | 18.A4
KA0231:A1 | SC | KA0231A1 | WHT | 20 | 18.C6 | KA0232:A1 | 2 BAY LEFT WALL | 18.D6
KA0231:A2 | SC | KA0231A2 | WHT | 20 | 18.C6 | KA0232:A2 | 2 BAY LEFT WALL | 18.D6
KA0232:22 | SC | KA023222 | WHT | 20 | 117.A6 | KA0144:21 | 2 BAY LEFT WALL | 117.A6
KA0232:22 | SC | KA023222 | WHT | 20 | 117.A6 | KA0249:11 | 2 BAY LEFT WALL | 117.B6
KA0232:A1 | SC | KA0231A1 | WHT | 20 | 18.D6 | KA0233:A1 | 2 BAY LEFT WALL | 18.D6
KA0232:A2 | SC | KA0231A2 | WHT | 20 | 18.D6 | KA0233:A2 | 2 BAY LEFT WALL | 18.D6
KA0233:A1 | SC | KA0231A1 | WHT | 20 | 18.D6 | KA0234:A1 | 2 BAY LEFT WALL | 18.D6
KA0233:A2 | SC | KA0231A2 | WHT | 20 | 18.D6 | KA0234:A2 | 2 BAY LEFT WALL | 18.D6
KA0235:11 | SC | UA1200J21 | WHT | 20 | 18.A5 | KA0241:11 | 2 BAY LEFT WALL | 18.A5
KA0235:14 | SC | KA024114 | WHT | 20 | 18.A5 | KA0241:14 | 2 BAY LEFT WALL | 18.A5
KA0235:A1 | SC | ESTOP | WHT | 20 | 18.A2 | KA0236:A1 | 2 BAY LEFT WALL | 18.B2
KA0235:A1 | SC | ESTOP | WHT | 20 | 18.A2 | XT0240:4 | 2 BAY LEFT WALL | 18.A3
KA0236:11 | SC | FU0139 | WHT | 20 | 18.D4 | KA0244:11 | 2 BAY LEFT WALL | 18.D4
KA0236:11 | SC | FU0139 | WHT | 20 | 18.D4 | XT0240:12 | 2 BAY LEFT WALL | 18.C4
KA0236:12 | SC | KA023612 | WHT | 20 | 18.D4 | XT0240:13 | 2 BAY LEFT WALL | 18.D4
KA0236:A1 | SC | ESTOP | WHT | 20 | 18.B2 | KA0237:A1 | 2 BAY LEFT WALL | 18.B2
KA0236:A2 | SC | 0V | WHT | 20 | 18.B2 | KA0235:A2 | 2 BAY LEFT WALL | 18.A2
KA0236:A2 | SC | 0V | WHT | 20 | 18.B2 | KA0237:A2 | 2 BAY LEFT WALL | 18.B2
KA0237:A1 | SC | ESTOP | WHT | 20 | 18.B2 | KA0238:A1 | 2 BAY LEFT WALL | 18.B2
KA0237:A2 | SC | 0V | WHT | 20 | 18.B2 | KA0238:A2 | 2 BAY LEFT WALL | 18.B2
KA0238:A1 | SC | ESTOP | WHT | 20 | 18.B2 | KA0239:A1 | 2 BAY LEFT WALL | 18.B2
KA0238:A2 | SC | 0V | WHT | 20 | 18.B2 | KA0239:A2 | 2 BAY LEFT WALL | 18.B2
KA0239:A1 | SC | ESTOP | WHT | 20 | 18.B2 | KA0240:A1 | 2 BAY LEFT WALL | 18.B2
KA0239:A2 | SC | 0V | WHT | 20 | 18.B2 | KA0240:A2 | 2 BAY LEFT WALL | 18.B2
KA0240:A1 | SC | ESTOP | WHT | 20 | 18.B2 | KA0248:A1 | 2 BAY LEFT WALL | 18.B2
KA0240:A2 | SC | 0V | WHT | 20 | 18.B2 | KA0248:A2 | 2 BAY LEFT WALL | 18.B2
KA0241:14 | SC | KA024114 | WHT | 20 | 18.A5 | KA0231:24 | 2 BAY LEFT WALL | 18.A4
KA0241:A1 | SC | KA0241A1 | WHT | 20 | 18.C2 | KA0242:A1 | 2 BAY LEFT WALL | 18.C2
KA0241:A1 | SC | KA0241A1 | WHT | 20 | 18.C2 | XT0240:6 | 2 BAY LEFT WALL | 18.C3
KA0241:A2 | SC | 0V | WHT | 20 | 18.C2 | KA0242:A2 | 2 BAY LEFT WALL | 18.C2
KA0241:A2 | SC | 0V | WHT | 20 | 18.C2 | KA0250:A2 | 2 BAY LEFT WALL | 18.C2
KA0242:11 | SC | KA0231A1 | WHT | 20 | 18.C6 | XT0136:10 | 2 BAY LEFT WALL | 17.B5
KA0242:21 | SC | 024221 | WHT | 20 | 19.C6 | XT0237:1 T2 | 2 BAY LEFT WALL | 19.C5
KA0242:24 | SC | KA024812 | WHT | 20 | 19.C6 | KA0248:12 | 2 BAY LEFT WALL | 19.C6
KA0242:A2 | SC | 0V | WHT | 20 | 18.C2 | KA0243:A2 | 2 BAY LEFT WALL | 18.C2
KA0243:21 | SC | ESTOPC | WHT | 20 | 18.A3 | XT0240:1 | 2 BAY LEFT WALL | 18.A3
KA0243:24 | SC | KA024511 | WHT | 20 | 18.A3 | KA0245:11 | 2 BAY LEFT WALL | 18.A4
KA0243:A1 | SC | KA0243A1 | WHT | 20 | 18.C2 | KA0244:A1 | 2 BAY LEFT WALL | 18.D2
KA0243:A1 | SC | KA0243A1 | WHT | 20 | 18.C2 | XT0240:7 | 2 BAY LEFT WALL | 18.C3
KA0243:A2 | SC | 0V | WHT | 20 | 18.C2 | KA0244:A2 | 2 BAY LEFT WALL | 18.D2
KA0244:12 | SC | KA024412 | WHT | 20 | 18.D4 | KT0145:A1 | 2 BAY LEFT WALL | 17.B6
KA0244:A1 | SC | KA0243A1 | WHT | 20 | 18.D2 | KA0246:A1 | 2 BAY LEFT WALL | 18.D2
KA0244:A2 | SC | 0V | WHT | 20 | 18.D2 | KA0246:A2 | 2 BAY LEFT WALL | 18.D2
KA0245:A1 | SC | KA0245A1 | WHT | 20 | 18.D2 | KA0249:A1 | 2 BAY LEFT WALL | 18.D2
KA0245:A1 | SC | KA0245A1 | WHT | 20 | 18.D2 | XT0240:8 | 2 BAY LEFT WALL | 18.D3
KA0245:A2 | SC | 0V | WHT | 20 | 18.D2 | KA0249:A2 | 2 BAY LEFT WALL | 18.D2
KA0245:A2 | SC | 0V | WHT | 20 | 18.D2 | KA0247:A2 | 2 BAY LEFT WALL | 18.D2
KA0246:A1 | SC | KA0243A1 | WHT | 20 | 18.D2 | KA0247:A1 | 2 BAY LEFT WALL | 18.D2
KA0246:A2 | SC | 0V | WHT | 20 | 18.D2 | KA0247:A2 | 2 BAY LEFT WALL | 18.D2
KA0248:A1 | SC | ESTOP | WHT | 20 | 18.B2 | KA0250:A1 | 2 BAY LEFT WALL | 18.C2
KA0248:A2 | SC | 0V | WHT | 20 | 18.B2 | KA0250:A2 | 2 BAY LEFT WALL | 18.C2
KA0249:A2 | SC | 0V | WHT | 20 | 18.D2 | XT0240:10 | 2 BAY LEFT WALL | 18.D3
KT0140:15 | SC | FU0139 | WHT | 16 | 17.A2 | XT0136:2 | 2 BAY LEFT WALL | 17.A2
KT0140:15 | SC | FU0139 | WHT | 20 | 17.D1 | KT0142:15 | 2 BAY LEFT WALL | 17.D2
KT0140:16 | SC | KT014115 | WHT | 20 | 17.D1 | KT0141:15 | 2 BAY LEFT WALL | 17.D2
KT0140:18 | SC | KT0143A1 | WHT | 20 | 17.A2 | KT0143:A1 | 2 BAY LEFT WALL | 17.A6
KT0140:A1 | SC | KT0140A1 | WHT | 20 | 17.A6 | KT0143:16 | 2 BAY LEFT WALL | 17.A5
KT0140:A2 | SC | 0V | WHT | 20 | 17.A6 | XT0136:3 | 2 BAY LEFT WALL | 17.A2
KT0140:A2 | SC | 0V | WHT | 20 | 17.A6 | KT0141:A2 | 2 BAY LEFT WALL | 17.A6
KT0141:18 | SC | KA013222 | WHT | 20 | 17.D2 | KT0144:18 | 2 BAY LEFT WALL | 17.D2
KT0141:A1 | SC | KT0141A1 | WHT | 20 | 17.A6 | KT0143:15 | 2 BAY LEFT WALL | 17.A5
KT0141:A1 | SC | KT0141A1 | WHT | 20 | 17.A6 | KT0142:A1 | 2 BAY LEFT WALL | 17.A6
KT0141:A2 | SC | 0V | WHT | 20 | 17.A6 | KT0142:A2 | 2 BAY LEFT WALL | 17.A6
KT0142:15 | SC | FU0139 | WHT | 20 | 17.D2 | KT0144:A1 | 2 BAY LEFT WALL | 17.B6
KT0142:18 | SC | KA0137A1 | WHT | 20 | 17.D2 | KT0145:18 | 2 BAY LEFT WALL | 17.D2
KT0142:A2 | SC | 0V | WHT | 20 | 17.A6 | KT0143:A2 | 2 BAY LEFT WALL | 17.A6
KT0143:A2 | SC | 0V | WHT | 20 | 17.A6 | KT0144:A2 | 2 BAY LEFT WALL | 17.B6
KT0144:15 | SC | FU0139 | WHT | 20 | 17.D2 | KT0145:15 | 2 BAY LEFT WALL | 17.D2
KT0144:15 | SC | FU0139 | WHT | 20 | 17.D2 | KT0144:A1 | 2 BAY LEFT WALL | 17.B6
KT0144:A2 | SC | 0V | WHT | 20 | 17.B6 | KT0145:A2 | 2 BAY LEFT WALL | 17.B6
PC0470:INP_A | SC | 009312 | WHT | 20 | 35.C5 | PC0470:INP_B | 2 BAY LEFT WALL | 35.C5
UAI9205-1:1 | SC | TE2120-3 | WHT | 20 | 54.D5 | UAI9205-1:2 | 2 BAY LEFT WALL | 54.D5
UAI9205-2:1 | SC | TE1110-3 | WHT | 20 | 47.A5 | UAI9205-2:2 | 2 BAY LEFT WALL | 47.A5
UAI9205-3:1 | SC | TE3200-3 | WHT | 20 | 91.A5 | UAI9205-3:2 | 2 BAY LEFT WALL | 91.A5
UAI9205-4:1 | SC | TE31003 | WHT | 20 | 97.A5 | UAI9205-4:2 | 2 BAY LEFT WALL | 97.A5
UAI9205-5:1 | SC | TE6110-3 | WHT | 20 | 115.A5 | UAI9205-5:2 | 2 BAY LEFT WALL | 115.A5
UAI9205-6:1 | SC | TE2645-3 | WHT | 20 | 77.A5 | UAI9205-6:2 | 2 BAY LEFT WALL | 77.A5
UAI9206-1:1 | SC | AP1100-3 | WHT | 20 | 48.A5 | UAI9206-1:2 | 2 BAY LEFT WALL | 48.A5
UAI9207-1:1 | SC | TE3520-3 | WHT | 20 | 90.A5 | UAI9207-1:2 | 2 BAY LEFT WALL | 90.A5
UAI9207-2:1 | SC | TE1260-3 | WHT | 20 | 82.A5 | UAI9207-2:2 | 2 BAY LEFT WALL | 82.A5
UV0271:11+ | SC | UV02718 | WHT | 16 | 16.B1 | UV0272:8+ | 2 BAY LEFT WALL | 16.B1
UV0271:12- | SC | UV02719 | WHT | 16 | 16.B1 | UV0272:9- | 2 BAY LEFT WALL | 16.B1
UV0271:9- | SC | 0V | WHT | 16 | 16.B1 | XT0135:3 | 2 BAY LEFT WALL | 16.B5
XT0134:1 | SC | 0V | WHT | 16 | 16.B4 | XT0135:1 | 2 BAY LEFT WALL | 16.B5
XT0134:4 | SC | 0V | WHT | 14 | 16.B4 | XT0235:1 | 2 BAY LEFT WALL | 16.D5
XT0135:1 | SC | 0V | WHT | 14 | 16.B5 | XT0136:3 | 2 BAY LEFT WALL | 17.A2
XT0136:1 | SC | FU0139 | WHT | 16 | 17.A2 | XT0240:12 | 2 BAY LEFT WALL | 18.C4
XT0136:3 | SC | 0V | WHT | 14 | 17.A2 | XT0240:10 | 2 BAY LEFT WALL | 18.D3
XT0233:3 | SC | FU0210 | WHT | 12 | 16.C5 | XT0233:4 | 2 BAY LEFT WALL | 16.C5
XT0233:4 | SC | FU0210 | WHT | 12 | 16.C5 | XT0233:5 | 2 BAY LEFT WALL | 16.C5
XT0235:3 | SC | 0V | WHT | 14 | 16.D5 | XT0235:4 | 2 BAY LEFT WALL | 16.D5
XT0235:4 | SC | 0V | WHT | 14 | 16.D5 | XT0235:5 | 2 BAY LEFT WALL | 16.D5
XT0240:5 | SC | ESTOP | WHT | 20 | 18.B3 | XT0240:4 | 2 BAY LEFT WALL | 18.A3
UAI9201-1:4+ | WI0680 | AP1100-P1 | RED | 20 | 48.B5 | XT-9201:1 | 2 BAY LEFT WALL | 48.B4
UAI9201-1:5- | WI0680 | AP1100-N1 | BLK | 20 | 48.B5 | XT-9201:2 | 2 BAY LEFT WALL | 48.B4
UAI9201-1:IE | WI0680 | AP1100-S1 | SH | 20 | 48.B5 | XT-9201:3 | 2 BAY LEFT WALL | 48.B4
UAI9201-3:4+ | WI0681 | AP1100-P3 | RED | 20 | 48.C5 | XT-9201:7 | 2 BAY LEFT WALL | 48.C4
UAI9201-3:5- | WI0681 | AP1100-N3 | BLK | 20 | 48.C5 | XT-9201:8 | 2 BAY LEFT WALL | 48.C4
UAI9201-3:IE | WI0681 | AP1100-S3 | SH | 20 | 48.C5 | XT-9201:9 | 2 BAY LEFT WALL | 48.C4
UAI9201-5:4+ | WI0682 | AP1100-P5 | RED | 20 | 48.D5 | XT-9201:13 | 2 BAY LEFT WALL | 48.D4
UAI9201-5:5- | WI0682 | AP1100-N5 | BLK | 20 | 48.D5 | XT-9201:14 | 2 BAY LEFT WALL | 48.D4
UAI9201-5:IE | WI0682 | AP1100-S5 | SH | 20 | 48.D5 | XT-9201:15 | 2 BAY LEFT WALL | 48.D4
UAI9201-7:4+ | WI0683 | AP1100-P7 | RED | 20 | 49.B5 | XT-9201:19 | 2 BAY LEFT WALL | 49.B4
UAI9201-7:5- | WI0683 | AP1100-N7 | BLK | 20 | 49.B5 | XT-9201:20 | 2 BAY LEFT WALL | 49.B4
UAI9201-7:IE | WI0683 | AP1100-S7 | SH | 20 | 49.B5 | XT-9201:21 | 2 BAY LEFT WALL | 49.B4
UAI9201-9:4+ | WI0684 | AP1100-P9 | RED | 20 | 49.B5 | XT-9201:25 | 2 BAY LEFT WALL | 49.B4
UAI9201-9:5- | WI0684 | AP1100-N9 | BLK | 20 | 49.B5 | XT-9201:26 | 2 BAY LEFT WALL | 49.C4
UAI9201-9:IE | WI0684 | AP1100-S9 | SH | 20 | 49.B5 | XT-9201:27 | 2 BAY LEFT WALL | 49.C4
UAI9202-1:4+ | WI0685 | AP1100-P11 | RED | 20 | 49.C5 | XT-9202:1 | 2 BAY LEFT WALL | 49.C4
UAI9202-1:5- | WI0685 | AP1100-N11 | BLK | 20 | 49.C5 | XT-9202:2 | 2 BAY LEFT WALL | 49.C4
UAI9202-1:IE | WI0685 | AP1100-S11 | SH | 20 | 49.C5 | XT-9202:3 | 2 BAY LEFT WALL | 49.D4
UAI9206-1:4 | WI0686 | AP1100-1 | RED | 20 | 48.A5 | XT-9206:1 | 2 BAY LEFT WALL | 48.A4
UAI9206-1:3 | WI0686 | AP1100-2 | WHT | 20 | 48.A5 | XT-9206:2 | 2 BAY LEFT WALL | 48.A4
UAI9206-1:2 | WI0686 | AP1100-3 | BLK | 20 | 48.A5 | XT-9206:3 | 2 BAY LEFT WALL | 48.A4
UAI9206-1:IE | WI0686 | AP1100-S | SH | 20 | 48.A5 | XT-9206:4 | 2 BAY LEFT WALL | 48.A4
UAI9201-2:4+ | WI0730 | AP1100-P2 | RED | 20 | 48.B5 | XT-9201:4 | 2 BAY LEFT WALL | 48.B4
UAI9201-2:5- | WI0730 | AP1100-N2 | BLK | 20 | 48.B5 | XT-9201:5 | 2 BAY LEFT WALL | 48.B4
UAI9201-2:IE | WI0730 | AP1100-S2 | SH | 20 | 48.B5 | XT-9201:6 | 2 BAY LEFT WALL | 48.B4
UAI9201-4:4+ | WI0731 | AP1100-P4 | RED | 20 | 48.C5 | XT-9201:10 | 2 BAY LEFT WALL | 48.C4
UAI9201-4:5- | WI0731 | AP1100-N4 | BLK | 20 | 48.C5 | XT-9201:11 | 2 BAY LEFT WALL | 48.C4
UAI9201-4:IE | WI0731 | AP1100-S4 | SH | 20 | 48.C5 | XT-9201:12 | 2 BAY LEFT WALL | 48.C4
UAI9201-6:4+ | WI0732 | AP1100-P6 | RED | 20 | 48.D5 | XT-9201:16 | 2 BAY LEFT WALL | 48.D4
UAI9201-6:5- | WI0732 | AP1100-N6 | BLK | 20 | 48.D5 | XT-9201:17 | 2 BAY LEFT WALL | 48.D4
UAI9201-6:IE | WI0732 | AP1100-S6 | SH | 20 | 48.D5 | XT-9201:18 | 2 BAY LEFT WALL | 48.D4
UAI9201-8:4+ | WI0733 | AP1100-P8 | RED | 20 | 49.B5 | XT-9201:22 | 2 BAY LEFT WALL | 49.B4
UAI9201-8:5- | WI0733 | AP1100-N8 | BLK | 20 | 49.B5 | XT-9201:23 | 2 BAY LEFT WALL | 49.B4
UAI9201-8:IE | WI0733 | AP1100-S8 | SH | 20 | 49.B5 | XT-9201:24 | 2 BAY LEFT WALL | 49.B4
UAI9201-10:4+ | WI0734 | AP1100-P10 | RED | 20 | 49.C5 | XT-9201:28 | 2 BAY LEFT WALL | 49.C4
UAI9201-10:5- | WI0734 | AP1100-N10 | BLK | 20 | 49.C5 | XT-9201:29 | 2 BAY LEFT WALL | 49.C4
UAI9201-10:IE | WI0734 | AP1100-S10 | SH | 20 | 49.C5 | XT-9201:30 | 2 BAY LEFT WALL | 49.C4
UAI9202-2:4+ | WI0735 | AP1100-P12 | RED | 20 | 49.D5 | XT-9202:4 | 2 BAY LEFT WALL | 49.D4
UAI9202-2:5- | WI0735 | AP1100-N12 | BLK | 20 | 49.D5 | XT-9202:5 | 2 BAY LEFT WALL | 49.D4
UAI9202-2:IE | WI0735 | AP1100-S12 | SH | 20 | 49.D5 | XT-9202:6 | 2 BAY LEFT WALL | 49.D4
UAI9205-1:4 | WI0736 | TE2120-1 | RED | 20 | 54.D5 | XT-9205:1 | 2 BAY LEFT WALL | 54.D4
UAI9205-1:3 | WI0736 | TE2120-2 | WHT | 20 | 54.D5 | XT-9205:2 | 2 BAY LEFT WALL | 54.D4
UAI9205-1:2 | WI0736 | TE2120-3 | BLK | 20 | 54.D5 | XT-9205:3 | 2 BAY LEFT WALL | 54.D4
UAI9205-1:IE | WI0736 | TE2120-S | SH | 20 | 54.D5 | XT-9205:4 | 2 BAY LEFT WALL | 54.D4
UAI9204-1:1+ | WI0746 | PT2610-1 | RED | 20 | 78.A5 | XT-9204:1 | 2 BAY LEFT WALL | 78.A4
UAI9204-1:3 | WI0746 | PT2610-2 | BLK | 20 | 78.A5 | XT-9204:2 | 2 BAY LEFT WALL | 78.A4
UAI9204-1:IE | WI0746 | PT2610-S | SH | 20 | 78.A5 | XT-9204:3 | 2 BAY LEFT WALL | 78.A4
UAI9203-1:1+ | WI0747 | PDT6310-1 | RED | 20 | 119.A5 | XT-9203:1 | 2 BAY LEFT WALL | 119.A4
UAI9203-1:3 | WI0747 | PDT6310-2 | BLK | 20 | 119.A5 | XT-9203:2 | 2 BAY LEFT WALL | 119.A4
UAI9203-1:IE | WI0747 | PDT6310-S | SH | 20 | 119.A5 | XT-9203:3 | 2 BAY LEFT WALL | 119.A4
UAI9207-2:4 | WI0831 | TE1260-1 | RED | 20 | 82.A5 | XT-9207:5 | 2 BAY LEFT WALL | 82.A4
UAI9207-2:3 | WI0831 | TE1260-2 | WHT | 20 | 82.A5 | XT-9207:6 | 2 BAY LEFT WALL | 82.A4
UAI9207-2:2 | WI0831 | TE1260-3 | BLK | 20 | 82.A5 | XT-9207:7 | 2 BAY LEFT WALL | 82.A4
UAI9207-2:IE | WI0831 | TE1260-S | SH | 20 | 82.A5 | XT-9207:8 | 2 BAY LEFT WALL | 82.A4
UAI9207-1:4 | WI0833 | TE3520-1 | RED | 20 | 90.A5 | XT-9207:1 | 2 BAY LEFT WALL | 90.A4
UAI9207-1:3 | WI0833 | TE3520-2 | WHT | 20 | 90.A5 | XT-9207:2 | 2 BAY LEFT WALL | 90.B4
UAI9207-1:2 | WI0833 | TE3520-3 | BLK | 20 | 90.A5 | XT-9207:3 | 2 BAY LEFT WALL | 90.B4
UAI9207-1:IE | WI0833 | TE3520-S | SH | 20 | 90.A5 | XT-9207:4 | 2 BAY LEFT WALL | 90.B4
UAI9205-2:4 | WI0835 | TE1110-1 | RED | 20 | 47.A5 | XT-9205:5 | 2 BAY LEFT WALL | 47.A4
UAI9205-2:3 | WI0835 | TE1110-2 | WHT | 20 | 47.A5 | XT-9205:6 | 2 BAY LEFT WALL | 47.A4
UAI9205-2:2 | WI0835 | TE1110-3 | BLK | 20 | 47.A5 | XT-9205:7 | 2 BAY LEFT WALL | 47.A4
UAI9205-2:IE | WI0835 | TE1110-S | SH | 20 | 47.A5 | XT-9205:8 | 2 BAY LEFT WALL | 47.A4
UAI9205-5:4 | WI0836 | TE6110-1 | RED | 20 | 115.A5 | XT-9205:17 | 2 BAY LEFT WALL | 115.A4
UAI9205-5:3 | WI0836 | TE6110-2 | WHT | 20 | 115.A5 | XT-9205:18 | 2 BAY LEFT WALL | 115.A4
UAI9205-5:2 | WI0836 | TE6110-3 | BLK | 20 | 115.A5 | XT-9205:19 | 2 BAY LEFT WALL | 115.A4
UAI9205-5:IE | WI0836 | TE6110-S | SH | 20 | 115.A5 | XT-9205:20 | 2 BAY LEFT WALL | 115.A4
UAI9205-3:4 | WI0840 | TE3200-1 | RED | 20 | 91.A5 | XT-9205:9 | 2 BAY LEFT WALL | 91.A4
UAI9205-3:3 | WI0840 | TE3200-2 | WHT | 20 | 91.A5 | XT-9205:10 | 2 BAY LEFT WALL | 91.A4
UAI9205-3:2 | WI0840 | TE3200-3 | BLK | 20 | 91.A5 | XT-9205:11 | 2 BAY LEFT WALL | 91.A4
UAI9205-3:IE | WI0840 | TE3200-S | SH | 20 | 91.A5 | XT-9205:12 | 2 BAY LEFT WALL | 91.A4
UAI9205-4:4 | WI0841 | TE31001 | RED | 20 | 97.A5 | XT-9205:13 | 2 BAY LEFT WALL | 97.A4
UAI9205-4:3 | WI0841 | TE31002 | WHT | 20 | 97.A5 | XT-9205:14 | 2 BAY LEFT WALL | 97.A4
UAI9205-4:2 | WI0841 | TE31003 | BLK | 20 | 97.A5 | XT-9205:15 | 2 BAY LEFT WALL | 97.A4
UAI9205-4:IE | WI0841 | TE3100S | SH | 20 | 97.A5 | XT-9205:16 | 2 BAY LEFT WALL | 97.A4
UAI9205-6:4 | WI0842 | TE2645-1 | RED | 20 | 77.A5 | XT-9205:21 | 2 BAY LEFT WALL | 77.A4
UAI9205-6:3 | WI0842 | TE2645-2 | WHT | 20 | 77.A5 | XT-9205:22 | 2 BAY LEFT WALL | 77.A4
UAI9205-6:2 | WI0842 | TE2645-3 | BLK | 20 | 77.A5 | XT-9205:23 | 2 BAY LEFT WALL | 77.A4
UAI9205-6:IE | WI0842 | TE2645-S | SH | 20 | 77.A5 | XT-9205:24 | 2 BAY LEFT WALL | 77.A4
UAI9208-1:5 | WI6161 | UA1263-1 | RED | 20 | 83.A5 | XT-9208:1 | 2 BAY LEFT WALL | 83.A4
UAI9208-1:6 | WI6161 | UA1263-2 | WHT | 20 | 83.A5 | XT-9208:2 | 2 BAY LEFT WALL | 83.A4
UAI9208-1:4 | WI6161 | UA1263-3 | BLK | 20 | 83.A5 | XT-9208:3 | 2 BAY LEFT WALL | 83.A4
UAI9208-1:IE | WI6161 | UA1263-S | SH | 20 | 83.A5 | XT-9208:4 | 2 BAY LEFT WALL | 83.A4
UAI9208-2:5 | WI6171 | UA1211-1 | RED | 20 | 83.B5 | XT-9208:5 | 2 BAY LEFT WALL | 83.B4
UAI9208-2:6 | WI6171 | UA1211-2 | WHT | 20 | 83.B5 | XT-9208:6 | 2 BAY LEFT WALL | 83.B4
UAI9208-2:4 | WI6171 | UA1211-3 | BLK | 20 | 83.B5 | XT-9208:7 | 2 BAY LEFT WALL | 83.B4
UAI9208-2:IE | WI6171 | UA1211-S | SH | 20 | 83.B5 | XT-9208:8 | 2 BAY LEFT WALL | 83.B4
UAI9208-3:5 | WI6172 | UA1210-1 | RED | 20 | 83.B5 | XT-9208:9 | 2 BAY LEFT WALL | 83.B4
UAI9208-3:6 | WI6172 | UA1210-2 | WHT | 20 | 83.B5 | XT-9208:10 | 2 BAY LEFT WALL | 83.B4
UAI9208-3:4 | WI6172 | UA1210-3 | BLK | 20 | 83.B5 | XT-9208:11 | 2 BAY LEFT WALL | 83.B4
UAI9208-3:IE | WI6172 | UA1210-S | SH | 20 | 83.B5 | XT-9208:12 | 2 BAY LEFT WALL | 83.B4
UAI9208-4:5 | WI6173 | UA1221-1 | RED | 20 | 83.C5 | XT-9208:13 | 2 BAY LEFT WALL | 83.C4
UAI9208-4:6 | WI6173 | UA1221-2 | WHT | 20 | 83.C5 | XT-9208:14 | 2 BAY LEFT WALL | 83.C4
UAI9208-4:4 | WI6173 | UA1221-3 | BLK | 20 | 83.C5 | XT-9208:15 | 2 BAY LEFT WALL | 83.C4
UAI9208-4:IE | WI6173 | UA1221-S | SH | 20 | 83.C5 | XT-9208:16 | 2 BAY LEFT WALL | 83.C4
UAI9208-5:5 | WI6174 | UA1220-1 | RED | 20 | 83.C5 | XT-9208:17 | 2 BAY LEFT WALL | 83.C4
UAI9208-5:6 | WI6174 | UA1220-2 | WHT | 20 | 83.C5 | XT-9208:18 | 2 BAY LEFT WALL | 83.C4
UAI9208-5:4 | WI6174 | UA1220-3 | BLK | 20 | 83.C5 | XT-9208:19 | 2 BAY LEFT WALL | 83.C4
UAI9208-5:IE | WI6174 | UA1220-S | SH | 20 | 83.C5 | XT-9208:20 | 2 BAY LEFT WALL | 83.C4
UAI9208-6:5 | WI6181 | UA1231-1 | RED | 20 | 83.C5 | XT-9208:21 | 2 BAY LEFT WALL | 83.C4
UAI9208-6:6 | WI6181 | UA1231-2 | WHT | 20 | 83.C5 | XT-9208:22 | 2 BAY LEFT WALL | 83.C4
UAI9208-6:4 | WI6181 | UA1231-3 | BLK | 20 | 83.C5 | XT-9208:23 | 2 BAY LEFT WALL | 83.C4
UAI9208-6:IE | WI6181 | UA1231-S | SH | 20 | 83.C5 | XT-9208:24 | 2 BAY LEFT WALL | 83.D4
UAI9208-7:5 | WI6182 | UA1230-1 | RED | 20 | 83.D5 | XT-9208:25 | 2 BAY LEFT WALL | 83.D4
UAI9208-7:6 | WI6182 | UA1230-2 | WHT | 20 | 83.D5 | XT-9208:26 | 2 BAY LEFT WALL | 83.D4
UAI9208-7:4 | WI6182 | UA1230-3 | BLK | 20 | 83.D5 | XT-9208:27 | 2 BAY LEFT WALL | 83.D4
UAI9208-7:IE | WI6182 | UA1230-S | SH | 20 | 83.D5 | XT-9208:28 | 2 BAY LEFT WALL | 83.D4
UAI9209-1:6 | WI6211 | VE4765-2 | RED | 20 | 84.A5 | XT-9209:2 | 2 BAY LEFT WALL | 84.A4
UAI9209-1:4 | WI6211 | VE4765-3 | WHT | 20 | 84.A5 | XT-9209:3 | 2 BAY LEFT WALL | 84.A4
UAI9209-1:5 | WI6211 | VE4765-1 | BLK | 20 | 84.A5 | XT-9209:1 | 2 BAY LEFT WALL | 84.A4
UAI9209-1:IE | WI6211 | VE4765-S | SH | 20 | 84.A5 | XT-9209:4 | 2 BAY LEFT WALL | 84.A4
UAI9208-8:5 | WI6213 | UA1262-1 | RED | 20 | 83.D5 | XT-9208:29 | 2 BAY LEFT WALL | 83.D4
UAI9208-8:6 | WI6213 | UA1262-2 | WHT | 20 | 83.D5 | XT-9208:30 | 2 BAY LEFT WALL | 83.D4
UAI9208-8:4 | WI6213 | UA1262-3 | BLK | 20 | 83.D5 | XT-9208:31 | 2 BAY LEFT WALL | 83.D4
UAI9208-8:IE | WI6213 | UA1262-S | SH | 20 | 83.D5 | XT-9208:32 | 2 BAY LEFT WALL | 83.D4
KA0131:11 | SC | KA0135A1 | WHT | 20 | 17.D4 | KA0135:A1 | 1 BAY BACK WALL | 17.D6
KA0136:A2 | SC | 0V | WHT | 20 | 17.D6 | KA0135:A2 | 1 BAY BACK WALL | 17.D6
KA0144:A1 | SC | KA0135A1 | WHT | 20 | 17.C6 | KA0135:A1 | 1 BAY BACK WALL | 17.D6
KA0144:A2 | SC | 0V | WHT | 20 | 17.C6 | KA0135:A2 | 1 BAY BACK WALL | 17.D6
KA0239:14 | SC | KA0239-14 | WHT | 20 | 63.C5 | KA121C:A1 | 1 BAY BACK WALL | 63.C6
KA0246:14 | SC | KA6211A1 | WHT | 20 | 117.C5 | KA6211:A1 | 1 BAY BACK WALL | 117.C6
KA0247:14 | SC | KA6212A1 | WHT | 20 | 118.C5 | KA6212:A1 | 1 BAY BACK WALL | 118.C6
FU0136:LI | SC | 24V | WHT | 10 | 16.A4 | XT0031:2 | 1 BAY RIGHT WALL | 15.D5
IEG8210:00 | SC | IEG8210-G | GRN | 8 | 4.B2 | IEG8130:0 | 1 BAY RIGHT WALL | 4.B2
KA0239:11 | SC | 012112 | WHT | 20 | 63.C5 | AF0121:12 | 1 BAY RIGHT WALL | 63.C7
XT0134:1 | SC | 0V | WHT | 10 | 16.B4 | XT0031:3 | 1 BAY RIGHT WALL | 15.D5
XT0134:3 | SC | 0V | WHT | 16 | 16.B4 | XT0334:1 | 1 BAY RIGHT WALL | 24.C2
XT0136:10 | SC | KA0231A1 | WHT | 14 | 17.B5 | XT0334:2 | 1 BAY RIGHT WALL | 24.C2
XT0138:3 | SC | FU0136 | WHT | 12 | 16.A4 | XT0332:1 | 1 BAY RIGHT WALL | 24.B2
XT0240:5 | SC | ESTOP | WHT | 20 | 18.B3 | XT0336:1 | 1 BAY RIGHT WALL | 24.C4
FU0281:LD | SC | UV0281P | WHT | 16 | 16.C2 | UV0281:8+ | 2 BAY BACK LEFT WALL | 16.C1
FU0291:LD | SC | UV0291P | WHT | 16 | 16.D2 | UV0291:8+ | 2 BAY BACK LEFT WALL | 16.D1
HIEG8210:0 | SC | HIEG8220-HG | GRN | 8 | 4.C2 | HIEG8220:00 | 2 BAY BACK LEFT WALL | 4.C2
IEG8210:0 | SC | IEG8220-G | GRN | 8 | 4.B2 | IEG8220:00 | 2 BAY BACK LEFT WALL | 4.B2
KA0136:A1 | SC | PS32002 | WHT | 20 | 17.D6 | UAI9215-1:8 | 2 BAY BACK LEFT WALL | 91.D5
KA0248:21 | SC | KA024821 | WHT | 20 | 91.D6 | UAI9215-1:10 | 2 BAY BACK LEFT WALL | 91.D5
XT0135:3 | SC | 0V | WHT | 16 | 16.B5 | UV0281:9- | 2 BAY BACK LEFT WALL | 16.C1
XT0135:4 | SC | 0V | WHT | 16 | 16.B5 | UV0291:9- | 2 BAY BACK LEFT WALL | 16.D1
XT0136:1 | SC | FU0139 | WHT | 20 | 17.A2 | UAI9215-1:7 | 2 BAY BACK LEFT WALL | 91.D5
XT0240:3 | SC | ESTOPA | WHT | 20 | 18.A3 | UAI9216-1:10 | 2 BAY BACK LEFT WALL | 34.C5
XT0240:4 | SC | ESTOP | WHT | 20 | 18.A3 | UAI9216-1:11 | 2 BAY BACK LEFT WALL | 34.C5
FU0010:LD | SC | FU0010 | WHT | 14 | 16.A6 | UV0600:(+) | 2 BAY BACK RIGHT PANEL | 7.B2
FU0211:LD | SC | FU0211 | WHT | 14 | 16.A5 | KA1020:14 | 2 BAY BACK RIGHT PANEL | 44.A5
FU0212:LD | SC | FU0212 | WHT | 16 | 16.C6 | XT-9326:6 | 2 BAY BACK RIGHT PANEL | 19.D4
KA0131:14 | SC | KA013114 | WHT | 20 | 17.D4 | AF0092:06 | 2 BAY BACK RIGHT PANEL | 92.A7
KA0133:A1 | SC | KA0133A1 | WHT | 20 | 17.C6 | AF0092:02 | 2 BAY BACK RIGHT PANEL | 92.A7
KA0134:A1 | SC | KA0134A1 | WHT | 20 | 17.C6 | AF0094:10 | 2 BAY BACK RIGHT PANEL | 94.A7
KA0134:A1 | SC | KA0134A1 | WHT | 20 | 17.C6 | AF0091:12 | 2 BAY BACK RIGHT PANEL | 94.A7
KA0136:21 | SC | KA013621 | WHT | 20 | 17.B3 | AF0091:43 | 2 BAY BACK RIGHT PANEL | 17.B4
KA0136:24 | SC | KA013624 | WHT | 20 | 17.B3 | AF0091:11 | 2 BAY BACK RIGHT PANEL | 17.B4
KA0137:24 | SC | KA013724 | WHT | 20 | 17.D3 | AF0091:04 | 2 BAY BACK RIGHT PANEL | 17.C4
KA0138:11 | SC | KM3170-EN | WHT | 16 | 94.C6 | XT-9319:2 | 2 BAY BACK RIGHT PANEL | 94.C4
KA0141:11 | SC | KA014111 | WHT | 20 | 17.C2 | AF0091:39 | 2 BAY BACK RIGHT PANEL | 17.C2
KA0141:14 | SC | KA014114 | WHT | 20 | 17.C2 | AF0091:07 | 2 BAY BACK RIGHT PANEL | 17.C2
KA0144:22 | SC | KA014422 | WHT | 20 | 117.A6 | KA0176:A1 | 2 BAY BACK RIGHT PANEL | 117.B5
KA0235:11 | SC | UA1200J21 | WHT | 20 | 18.A5 | XT-9326:5 | 2 BAY BACK RIGHT PANEL | 19.D4
KA0235:21 | SC | SV2120-1 | WHT | 16 | 59.A5 | XT-9330:3 | 2 BAY BACK RIGHT PANEL | 59.A4
KA0235:24 | SC | 022111 | WHT | 16 | 59.A5 | KA0221:11 | 2 BAY BACK RIGHT PANEL | 59.A6
KA0236:21 | SC | SV2124-1 | WHT | 16 | 59.B5 | XT-9330:7 | 2 BAY BACK RIGHT PANEL | 59.B4
KA0236:24 | SC | 022211 | WHT | 16 | 59.B5 | KA0222:11 | 2 BAY BACK RIGHT PANEL | 59.B6
KA0237:11 | SC | FCE21307 | WHT | 20 | 55.B5 | XT-9329:7 | 2 BAY BACK RIGHT PANEL | 55.B5
KA0238:11 | SC | SV22221 | WHT | 20 | 71.B5 | XT-9324:1 | 2 BAY BACK RIGHT PANEL | 71.B4
KA0238:14 | SC | KA023814 | WHT | 20 | 71.B5 | KA0225:14 | 2 BAY BACK RIGHT PANEL | 71.B6
KA0239:21 | SC | KA023921 | WHT | 20 | 18.B6 | AF0095:38 | 2 BAY BACK RIGHT PANEL | 18.A7
KA0239:24 | SC | KA023924 | WHT | 20 | 18.B6 | AF0095:06 | 2 BAY BACK RIGHT PANEL | 18.A7
KA0240:14 | SC | KA024024 | WHT | 20 | 70.B5 | KA0224:14 | 2 BAY BACK RIGHT PANEL | 70.B6
KA0241:11 | SC | UA1200J21 | WHT | 20 | 18.A5 | AF0095:00 | 2 BAY BACK RIGHT PANEL | 18.A7
KA0242:14 | SC | KA024214 | WHT | 20 | 18.C6 | AF0095:11 | 2 BAY BACK RIGHT PANEL | 18.C7
KA0243:11 | SC | KA024311 | WHT | 20 | 18.B6 | AF0095:33 | 2 BAY BACK RIGHT PANEL | 18.B7
KA0243:14 | SC | KA024314 | WHT | 20 | 18.B6 | AF0095:01 | 2 BAY BACK RIGHT PANEL | 18.B7
KA0245:21 | SC | KA024521 | WHT | 20 | 18.B6 | AF0095:34 | 2 BAY BACK RIGHT PANEL | 18.B7
KA0245:24 | SC | KA024524 | WHT | 20 | 18.B6 | AF0095:02 | 2 BAY BACK RIGHT PANEL | 18.B7
KA0246:11 | SC | KA017611 | WHT | 20 | 117.C5 | XT0171:1 | 2 BAY BACK RIGHT PANEL | 117.C5
KA0247:11 | SC | KA017711 | WHT | 20 | 118.C5 | XT0171:5 | 2 BAY BACK RIGHT PANEL | 118.C5
KA0250:11 | SC | KA022014 | WHT | 16 | 64.C6 | KA0220:14 | 2 BAY BACK RIGHT PANEL | 64.C5
KA0810:11 | SC | 008132 | WHT | 20 | 120.B5 | AF0081:32 | 2 BAY BACK RIGHT PANEL | 120.B7
KA0810:14 | SC | 008100 | WHT | 20 | 120.B5 | AF0081:00 | 2 BAY BACK RIGHT PANEL | 120.B7
KA0811:11 | SC | 008133 | WHT | 20 | 120.C5 | AF0081:33 | 2 BAY BACK RIGHT PANEL | 120.C7
KA0811:14 | SC | 008101 | WHT | 20 | 120.C5 | AF0081:01 | 2 BAY BACK RIGHT PANEL | 120.C7
KA0822:11 | SC | 008234 | WHT | 20 | 120.A5 | AF0082:34 | 2 BAY BACK RIGHT PANEL | 120.A7
KA0822:14 | SC | 008202 | WHT | 20 | 120.A5 | AF0082:02 | 2 BAY BACK RIGHT PANEL | 120.A7
KA0823:11 | SC | 008235 | WHT | 20 | 120.B5 | AF0082:35 | 2 BAY BACK RIGHT PANEL | 120.B7
KA0823:14 | SC | 008203 | WHT | 20 | 120.B5 | AF0082:03 | 2 BAY BACK RIGHT PANEL | 120.B7
KA0877:11 | SC | 008739 | WHT | 20 | 31.A5 | AF0087:39 | 2 BAY BACK RIGHT PANEL | 31.A7
KA0877:14 | SC | 008707 | WHT | 20 | 31.A5 | AF0087:07 | 2 BAY BACK RIGHT PANEL | 31.A7
KA0877:A1 | SC | KA7500-1 | WHT | 20 | 31.A5 | XT-9300:3 | 2 BAY BACK RIGHT PANEL | 31.A4
KA0877:A2 | SC | KA7500-2 | WHT | 20 | 31.A5 | XT-9300:4 | 2 BAY BACK RIGHT PANEL | 31.A4
KA0878:11 | SC | 008740 | WHT | 20 | 31.B5 | AF0087:40 | 2 BAY BACK RIGHT PANEL | 31.B7
KA0878:14 | SC | 008708 | WHT | 20 | 31.B5 | AF0087:08 | 2 BAY BACK RIGHT PANEL | 31.B7
KA0878:A1 | SC | KA7505-1 | WHT | 20 | 31.A5 | XT-9300:5 | 2 BAY BACK RIGHT PANEL | 31.A4
KA0878:A2 | SC | KA7505-2 | WHT | 20 | 31.A5 | XT-9300:6 | 2 BAY BACK RIGHT PANEL | 31.B4
KA1820:11 | SC | 008743 | WHT | 20 | 36.A5 | AF0087:43 | 2 BAY BACK RIGHT PANEL | 36.A7
KA1820:14 | SC | 008711 | WHT | 20 | 36.A5 | AF0087:11 | 2 BAY BACK RIGHT PANEL | 36.A7
KA1820:A1 | SC | SB7510-1 | WHT | 20 | 36.A5 | XT-9300:9 | 2 BAY BACK RIGHT PANEL | 36.A4
KA1820:A2 | SC | SB7510-2 | WHT | 20 | 36.A5 | XT-9300:10 | 2 BAY BACK RIGHT PANEL | 36.A4
KA1821:11 | SC | 008744 | WHT | 20 | 36.B5 | AF0087:44 | 2 BAY BACK RIGHT PANEL | 36.B7
KA1821:14 | SC | 008712 | WHT | 20 | 36.B5 | AF0087:12 | 2 BAY BACK RIGHT PANEL | 36.B7
KA1821:A1 | SC | SB7511-1 | WHT | 20 | 36.A5 | XT-9300:11 | 2 BAY BACK RIGHT PANEL | 36.A4
KA1821:A2 | SC | SB7511-2 | WHT | 20 | 36.A5 | XT-9300:12 | 2 BAY BACK RIGHT PANEL | 36.B4
PC0470:(9-28) VDC | SC | 009344 | WHT | 20 | 35.C5 | AF0093:44 | 2 BAY BACK RIGHT PANEL | 35.C7
PC0470:INP_A | SC | 009312 | WHT | 20 | 35.C5 | AF0093:12 | 2 BAY BACK RIGHT PANEL | 35.C7
PC0470:PWR_COM | SC | 009328 | WHT | 20 | 35.C5 | AF0093:28 | 2 BAY BACK RIGHT PANEL | 35.C7
XT0135:1 | SC | 0V | WHT | 14 | 16.B5 | UV0600:(-) | 2 BAY BACK RIGHT PANEL | 7.B2
XT0135:2 | SC | 0V | WHT | 16 | 16.B5 | XT0080:1 | 2 BAY BACK RIGHT PANEL | 8.D1
XT0135:2 | SC | 0V | WHT | 16 | 16.B5 | XT0090:1 | 2 BAY BACK RIGHT PANEL | 8.B1
XT0135:5 | SC | 0V | WHT | 14 | 16.C5 | KA1020:24 | 2 BAY BACK RIGHT PANEL | 44.A5
XT0136:1 | SC | FU0139 | WHT | 16 | 17.A2 | XT-9319:1 | 2 BAY BACK RIGHT PANEL | 94.C4
XT0139:2 | SC | FU0137 | WHT | 14 | 16.A5 | FU0080:LI | 2 BAY BACK RIGHT PANEL | 8.D1
XT0139:2 | SC | FU0137 | WHT | 14 | 16.A5 | FU0090:LI | 2 BAY BACK RIGHT PANEL | 8.B1
XT0235:2 | SC | 0V | WHT | 16 | 16.D5 | XT-9326:7 | 2 BAY BACK RIGHT PANEL | 19.D4
XT0235:4 | SC | 0V | WHT | 16 | 16.D5 | KA0176:A2 | 2 BAY BACK RIGHT PANEL | 117.B5
XT0237:1 B1 | SC | UA1200J15 | WHT | 20 | 19.C5 | XT-9326:2 | 2 BAY BACK RIGHT PANEL | 19.C4
XT0240:1 | SC | ESTOPC | WHT | 20 | 18.A3 | KA0817:24 | 2 BAY BACK RIGHT PANEL | 37.A5
XT0240:12 | SC | FU0139 | WHT | 20 | 18.C4 | KA9984:11 | 2 BAY BACK RIGHT PANEL | 38.B5
XT0240:12 | SC | FU0139 | WHT | 20 | 18.C4 | KA9982:11 | 2 BAY BACK RIGHT PANEL | 38.A5
XT0240:2 | SC | ESTOPB | WHT | 20 | 18.A3 | KA0817:21 | 2 BAY BACK RIGHT PANEL | 37.A5
XT0240:7 | SC | KA0243A1 | WHT | 20 | 18.C3 | KA9982:14 | 2 BAY BACK RIGHT PANEL | 38.A5
XT0240:8 | SC | KA0245A1 | WHT | 20 | 18.D3 | KA9984:14 | 2 BAY BACK RIGHT PANEL | 38.B5
UAI9207-2:-7 | W0831 | 008319 | RED | 20 | 82.A5 | AF0083:19 | 2 BAY BACK RIGHT PANEL | 82.A7
UAI9207-2:-5 | W0831 | 008303 | WHT | 20 | 82.A5 | AF0083:03 | 2 BAY BACK RIGHT PANEL | 82.A7
UAI9207-2:+6 | W0831 | 008302 | BLK | 20 | 82.A5 | AF0083:02 | 2 BAY BACK RIGHT PANEL | 82.A7
FLOATING | W0831 | 008350 | SH | 20 | 82.A6 | AF0083:50 | 2 BAY BACK RIGHT PANEL | 82.A7
UAI9207-1:-7 | W0833 | 008323 | RED | 20 | 90.A5 | AF0083:23 | 2 BAY BACK RIGHT PANEL | 90.A7
UAI9207-1:-5 | W0833 | 008307 | WHT | 20 | 90.A5 | AF0083:07 | 2 BAY BACK RIGHT PANEL | 90.A7
UAI9207-1:+6 | W0833 | 008306 | BLK | 20 | 90.A5 | AF0083:06 | 2 BAY BACK RIGHT PANEL | 90.A7
FLOATING | W0833 | 008354 | SH | 20 | 90.B6 | AF0083:54 | 2 BAY BACK RIGHT PANEL | 90.A7
UAI9205-2:-7 | W0835 | 008327 | RED | 20 | 47.A5 | AF0083:27 | 2 BAY BACK RIGHT PANEL | 47.A7
UAI9205-2:-5 | W0835 | 008311 | WHT | 20 | 47.A5 | AF0083:11 | 2 BAY BACK RIGHT PANEL | 47.A7
UAI9205-2:+6 | W0835 | 008310 | BLK | 20 | 47.A5 | AF0083:10 | 2 BAY BACK RIGHT PANEL | 47.A7
FLOATING | W0835 | 008358 | SH | 20 | 47.A6 | AF0083:58 | 2 BAY BACK RIGHT PANEL | 47.A7
UAI9205-5:-7 | W0836 | 008329 | RED | 20 | 115.A5 | AF0083:29 | 2 BAY BACK RIGHT PANEL | 115.A7
UAI9205-5:-5 | W0836 | 008313 | WHT | 20 | 115.A5 | AF0083:13 | 2 BAY BACK RIGHT PANEL | 115.A7
UAI9205-5:+6 | W0836 | 008312 | BLK | 20 | 115.A5 | AF0083:12 | 2 BAY BACK RIGHT PANEL | 115.A7
FW1201:1 | W0836 | 008360 | SH | 20 | 115.A6 | AF0083:60 | 2 BAY BACK RIGHT PANEL | 115.A7
UAI9205-3:-7 | W0840 | 008417 | RED | 20 | 91.A5 | AF0084:17 | 2 BAY BACK RIGHT PANEL | 91.A7
UAI9205-3:-5 | W0840 | 008401 | WHT | 20 | 91.A5 | AF0084:01 | 2 BAY BACK RIGHT PANEL | 91.A7
UAI9205-3:+6 | W0840 | 008400 | BLK | 20 | 91.A5 | AF0084:00 | 2 BAY BACK RIGHT PANEL | 91.A7
FW1?:1 | W0840 | 008448 | SH | 20 | 91.A6 | AF0084:48 | 2 BAY BACK RIGHT PANEL | 91.A7
UAI9205-4:-7 | W0841 | 008419 | RED | 20 | 97.A5 | AF0084:19 | 2 BAY BACK RIGHT PANEL | 97.A7
UAI9205-4:-5 | W0841 | 008403 | WHT | 20 | 97.A5 | AF0084:03 | 2 BAY BACK RIGHT PANEL | 97.A7
UAI9205-4:+6 | W0841 | 008402 | BLK | 20 | 97.A5 | AF0084:02 | 2 BAY BACK RIGHT PANEL | 97.A7
FLOATING | W0841 | 008450 | SH | 20 | 97.A6 | AF0084:50 | 2 BAY BACK RIGHT PANEL | 97.A7
UAI9205-6:-7 | W0842 | 008421 | RED | 20 | 77.A5 | AF0084:21 | 2 BAY BACK RIGHT PANEL | 77.A7
UAI9205-6:-5 | W0842 | 008405 | WHT | 20 | 77.A5 | AF0084:05 | 2 BAY BACK RIGHT PANEL | 77.A7
UAI9205-6:+6 | W0842 | 008404 | BLK | 20 | 77.A5 | AF0084:04 | 2 BAY BACK RIGHT PANEL | 77.A7
FW1202:1 | W0842 | 008452 | SH | 20 | 77.A6 | AF0084:52 | 2 BAY BACK RIGHT PANEL | 77.A7
KA0231:A2 | SC | KA0231A2 | WHT | 20 | 18.C6 | AF0076:26 | 2 BAY RIGHT WALL | 18.C7
KA0233:11 | SC | FCE1420-7 | WHT | 20 | 45.B6 | XT-9335:7 | 2 BAY RIGHT WALL | 45.B5
KA0233:14 | SC | 006102 | WHT | 20 | 45.B6 | AF0061:02 | 2 BAY RIGHT WALL | 45.B7
KA0234:11 | SC | FCE1440-7 | WHT | 20 | 46.B6 | XT-9336:10 | 2 BAY RIGHT WALL | 46.B5
KA0234:14 | SC | 006114 | WHT | 20 | 46.B6 | AF0061:14 | 2 BAY RIGHT WALL | 46.B7
KA0237:14 | SC | 007600 | WHT | 20 | 55.B5 | AF0076:00 | 2 BAY RIGHT WALL | 55.B7
KA0237:21 | SC | FCE2140-7 | WHT | 20 | 57.B5 | XT-9334:7 | 2 BAY RIGHT WALL | 57.B5
KA0237:24 | SC | 007601 | WHT | 20 | 57.B5 | AF0076:01 | 2 BAY RIGHT WALL | 57.B7
KA0240:11 | SC | SV2220-1 | WHT | 16 | 70.B5 | XT-9381:10 | 2 BAY RIGHT WALL | 70.B4
KA0248:24 | SC | UF1300-DI2 | WHT | 20 | 91.D6 | XT-9355:1 | 2 BAY RIGHT WALL | 43.A5
KA0250:14 | SC | FU0054 | WHT | 16 | 64.C6 | XT0050:4 | 2 BAY RIGHT WALL | 64.C7
KA0621:11 | SC | YK7174-1 | WHT | 20 | 121.A5 | XT-9350:9 | 2 BAY RIGHT WALL | 121.A4
KA0621:14 | SC | YK7174-2 | WHT | 20 | 121.A5 | XT-9350:10 | 2 BAY RIGHT WALL | 121.A4
KA0621:A1 | SC | 006202 | WHT | 20 | 121.A5 | AF0062:02 | 2 BAY RIGHT WALL | 121.A7
KA0621:A2 | SC | 006218 | WHT | 20 | 121.A5 | AF0062:18 | 2 BAY RIGHT WALL | 121.A7
KA0622:11 | SC | YK7176-1 | WHT | 20 | 121.C5 | XT-9350:13 | 2 BAY RIGHT WALL | 121.B4
KA0622:14 | SC | YK7176-2 | WHT | 20 | 121.C5 | XT-9350:14 | 2 BAY RIGHT WALL | 121.C4
KA0622:A1 | SC | 006204 | WHT | 20 | 121.B5 | AF0062:04 | 2 BAY RIGHT WALL | 121.B7
KA0622:A2 | SC | 006220 | WHT | 20 | 121.B5 | AF0062:20 | 2 BAY RIGHT WALL | 121.B7
KA0810:A1 | SC | XK7171-1 | WHT | 20 | 120.A5 | XT-9350:3 | 2 BAY RIGHT WALL | 120.A4
KA0810:A2 | SC | XK7171-2 | WHT | 20 | 120.A5 | XT-9350:4 | 2 BAY RIGHT WALL | 120.B4
KA0811:A1 | SC | XK7173-1 | WHT | 20 | 120.C5 | XT-9350:7 | 2 BAY RIGHT WALL | 120.C4
KA0811:A2 | SC | XK7173-2 | WHT | 20 | 120.C5 | XT-9350:8 | 2 BAY RIGHT WALL | 120.C4
KA0822:A1 | SC | XK7170-1 | WHT | 20 | 120.A5 | XT-9350:1 | 2 BAY RIGHT WALL | 120.A4
KA0822:A2 | SC | XK7170-2 | WHT | 20 | 120.A5 | XT-9350:2 | 2 BAY RIGHT WALL | 120.A4
KA0823:A1 | SC | XK7172-1 | WHT | 20 | 120.B5 | XT-9350:5 | 2 BAY RIGHT WALL | 120.B4
KA0823:A2 | SC | XK7172-2 | WHT | 20 | 120.B5 | XT-9350:6 | 2 BAY RIGHT WALL | 120.B4
KT0146:15 | SC | KT014615 | WHT | 20 | 18.C6 | AF0076:10 | 2 BAY RIGHT WALL | 18.C7
KT0146:A2 | SC | KT0146A2 | WHT | 20 | 17.B2 | AF0076:29 | 2 BAY RIGHT WALL | 17.B2
KT0146:B1 | SC | KT0146B1 | WHT | 20 | 17.B2 | AF0076:13 | 2 BAY RIGHT WALL | 17.B2
PC0471:+PWR | SC | 005344 | WHT | 20 | 35.C5 | AF0053:44 | 2 BAY RIGHT WALL | 35.C7
PC0471:INP_A | SC | 005312 | WHT | 20 | 35.C5 | AF0053:12 | 2 BAY RIGHT WALL | 35.C7
PC0471:INP_B | SC | 005314 | WHT | 20 | 35.C5 | AF0053:14 | 2 BAY RIGHT WALL | 35.D7
PC0471:-PWR | SC | 005330 | WHT | 20 | 35.C5 | AF0053:30 | 2 BAY RIGHT WALL | 35.D7
XT0134:3 | SC | 0V | WHT | 16 | 16.B4 | XT0450:2 | 2 BAY RIGHT WALL | 22.A5
XT0134:4 | SC | 0V | WHT | 14 | 16.B4 | XT0110:2 | 2 BAY RIGHT WALL | 23.A6
XT0138:3 | SC | FU0136 | WHT | 14 | 16.A4 | XT0450:1 | 2 BAY RIGHT WALL | 22.A5
XT0138:4 | SC | FU0136 | WHT | 14 | 16.A4 | XT0110:1 | 2 BAY RIGHT WALL | 23.A6
XT0233:1 | SC | FU0210 | WHT | 14 | 16.C5 | FU0060:LI | 2 BAY RIGHT WALL | 9.C1
XT0233:2 | SC | FU0210 | WHT | 14 | 16.C5 | FU0050:LI | 2 BAY RIGHT WALL | 10.B1
XT0233:2 | SC | FU0210 | WHT | 14 | 16.C5 | FU0070:LI | 2 BAY RIGHT WALL | 9.B1
XT0233:2 | SC | FU0210 | WHT | 16 | 16.C5 | XT-9381:4 | 2 BAY RIGHT WALL | 68.C4
XT0233:2 | SC | FU0210 | WHT | 16 | 16.C5 | XT-9381:7 | 2 BAY RIGHT WALL | 67.C4
XT0233:3 | SC | FU0210 | WHT | 16 | 16.C5 | XT-9381:1 | 2 BAY RIGHT WALL | 61.C4
XT0235:1 | SC | 0V | WHT | 14 | 16.D5 | XT0050:1 | 2 BAY RIGHT WALL | 10.B1
XT0235:3 | SC | 0V | WHT | 16 | 16.D5 | XT-9381:2 | 2 BAY RIGHT WALL | 61.C4
XT0237:1 B2 | SC | 007612 | WHT | 20 | 19.C5 | AF0076:12 | 2 BAY RIGHT WALL | 19.C7
UAI9201-1:+7 | W0680 | 006800 | RED | 20 | 48.B5 | AF0068:00 | 2 BAY RIGHT WALL | 48.B7
UAI9201-1:-8 | W0680 | 006801 | BLK | 20 | 48.B5 | AF0068:01 | 2 BAY RIGHT WALL | 48.B7
FLOATING | W0680 | 006848 | SH | 20 | 48.B6 | AF0068:48 | 2 BAY RIGHT WALL | 48.B7
UAI9201-3:+7 | W0681 | 006802 | RED | 20 | 48.C5 | AF0068:02 | 2 BAY RIGHT WALL | 48.C7
UAI9201-3:-8 | W0681 | 006803 | BLK | 20 | 48.C5 | AF0068:03 | 2 BAY RIGHT WALL | 48.C7
FLOATING | W0681 | 006850 | SH | 20 | 48.C6 | AF0068:50 | 2 BAY RIGHT WALL | 48.C7
UAI9201-5:+7 | W0682 | 006804 | RED | 20 | 48.D5 | AF0068:04 | 2 BAY RIGHT WALL | 48.D7
UAI9201-5:-8 | W0682 | 006805 | BLK | 20 | 48.D5 | AF0068:05 | 2 BAY RIGHT WALL | 48.D7
FLOATING | W0682 | 006852 | SH | 20 | 48.D6 | AF0068:52 | 2 BAY RIGHT WALL | 48.D7
UAI9201-7:+7 | W0683 | 006806 | RED | 20 | 49.B5 | AF0068:06 | 2 BAY RIGHT WALL | 49.B7
UAI9201-7:-8 | W0683 | 006807 | BLK | 20 | 49.B5 | AF0068:07 | 2 BAY RIGHT WALL | 49.B7
FW0751:1 | W0683 | 006854 | SH | 20 | 49.B6 | AF0068:54 | 2 BAY RIGHT WALL | 49.B7
UAI9201-9:+7 | W0684 | 006808 | RED | 20 | 49.B5 | AF0068:08 | 2 BAY RIGHT WALL | 49.B7
UAI9201-9:-8 | W0684 | 006809 | BLK | 20 | 49.B5 | AF0068:09 | 2 BAY RIGHT WALL | 49.B7
FW0753:1 | W0684 | 006856 | SH | 20 | 49.C6 | AF0068:56 | 2 BAY RIGHT WALL | 49.B7
UAI9202-1:+7 | W0685 | 006810 | RED | 20 | 49.C5 | AF0068:10 | 2 BAY RIGHT WALL | 49.C7
UAI9202-1:-8 | W0685 | 006811 | BLK | 20 | 49.C5 | AF0068:11 | 2 BAY RIGHT WALL | 49.C7
FW0755:1 | W0685 | 006858 | SH | 20 | 49.D6 | AF0068:58 | 2 BAY RIGHT WALL | 49.C7
UAI9206-1:-7 | W0686 | 006845 | RED | 20 | 48.A5 | AF0068:45 | 2 BAY RIGHT WALL | 48.A7
UAI9206-1:-5 | W0686 | 006829 | WHT | 20 | 48.A5 | AF0068:29 | 2 BAY RIGHT WALL | 48.A7
UAI9206-1:+6 | W0686 | 006828 | BLK | 20 | 48.A5 | AF0068:28 | 2 BAY RIGHT WALL | 48.A7
FLOATING | W0686 | 006860 | SH | 20 | 48.A6 | AF0068:60 | 2 BAY RIGHT WALL | 48.A7
UAI9201-2:+7 | W0730 | 007300 | RED | 20 | 48.B5 | AF0073:00 | 2 BAY RIGHT WALL | 48.B7
UAI9201-2:-8 | W0730 | 007301 | BLK | 20 | 48.B5 | AF0073:01 | 2 BAY RIGHT WALL | 48.B7
FLOATING | W0730 | 007348 | SH | 20 | 48.B6 | AF0073:48 | 2 BAY RIGHT WALL | 48.B7
UAI9201-4:+7 | W0731 | 007302 | RED | 20 | 48.C5 | AF0073:02 | 2 BAY RIGHT WALL | 48.C7
UAI9201-4:-8 | W0731 | 007303 | BLK | 20 | 48.C5 | AF0073:03 | 2 BAY RIGHT WALL | 48.C7
FLOATING | W0731 | 007350 | SH | 20 | 48.C6 | AF0073:50 | 2 BAY RIGHT WALL | 48.C7
UAI9201-6:+7 | W0732 | 007304 | RED | 20 | 48.D5 | AF0073:04 | 2 BAY RIGHT WALL | 48.D7
UAI9201-6:-8 | W0732 | 007305 | BLK | 20 | 48.D5 | AF0073:05 | 2 BAY RIGHT WALL | 48.D7
FLOATING | W0732 | 007352 | SH | 20 | 48.D6 | AF0073:52 | 2 BAY RIGHT WALL | 48.D7
UAI9201-8:+7 | W0733 | 007306 | RED | 20 | 49.B5 | AF0073:06 | 2 BAY RIGHT WALL | 49.B7
UAI9201-8:-8 | W0733 | 007307 | BLK | 20 | 49.B5 | AF0073:07 | 2 BAY RIGHT WALL | 49.B7
FW0752:1 | W0733 | 007354 | SH | 20 | 49.B6 | AF0073:54 | 2 BAY RIGHT WALL | 49.B7
UAI9201-10:+7 | W0734 | 007308 | RED | 20 | 49.C5 | AF0073:08 | 2 BAY RIGHT WALL | 49.C7
UAI9201-10:-8 | W0734 | 007309 | BLK | 20 | 49.C5 | AF0073:09 | 2 BAY RIGHT WALL | 49.C7
FW0754:1 | W0734 | 007356 | SH | 20 | 49.C6 | AF0073:56 | 2 BAY RIGHT WALL | 49.C7
UAI9202-2:+7 | W0735 | 007310 | RED | 20 | 49.D5 | AF0073:10 | 2 BAY RIGHT WALL | 49.D7
UAI9202-2:-8 | W0735 | 007311 | BLK | 20 | 49.D5 | AF0073:11 | 2 BAY RIGHT WALL | 49.D7
FW0756:1 | W0735 | 007358 | SH | 20 | 49.D6 | AF0073:58 | 2 BAY RIGHT WALL | 49.D7
UAI9205-1:-7 | W0736 | 007345 | RED | 20 | 54.D5 | AF0073:45 | 2 BAY RIGHT WALL | 54.D7
UAI9205-1:-5 | W0736 | 007329 | WHT | 20 | 54.D5 | AF0073:29 | 2 BAY RIGHT WALL | 54.D7
UAI9205-1:+6 | W0736 | 007328 | BLK | 20 | 54.D5 | AF0073:28 | 2 BAY RIGHT WALL | 54.D7
FW0889:1 | W0736 | 007360 | SH | 20 | 54.D6 | AF0073:60 | 2 BAY RIGHT WALL | 54.D7
UAI9204-1:+8 | W0746 | 007412 | RED | 20 | 78.A5 | AF0074:12 | 2 BAY RIGHT WALL | 78.A7
UAI9204-1:-7 | W0746 | 007428 | BLK | 20 | 78.A5 | AF0074:28 | 2 BAY RIGHT WALL | 78.A7
FW1207:1 | W0746 | 007460 | SH | 20 | 78.A6 | AF0074:60 | 2 BAY RIGHT WALL | 78.A7
UAI9203-1:+8 | W0747 | 007414 | RED | 20 | 119.A5 | AF0074:14 | 2 BAY RIGHT WALL | 119.A7
UAI9203-1:-7 | W0747 | 007430 | BLK | 20 | 119.A5 | AF0074:30 | 2 BAY RIGHT WALL | 119.A7
FW6:1 | W0747 | 007462 | SH | 20 | 119.A6 | AF0074:62 | 2 BAY RIGHT WALL | 119.A7
FU0274:LD | SC | FU0274 | WHT | 14 | 11.C3 | ZS0274:1 | ASSEMBLY CONSOLE | 11.C4
IEG8210:1 | SC | IEG8210-1 | GRN | 14 | 11.A2 | GR0200: | ASSEMBLY^CONTROL PANEL | 11.A3
UAI9208-1:7 | W6161 | 0616SIG1 | RED | 20 | 83.A5 | AP0616:SIG1 | ORBIT 60^DOOR PANEL | 83.A6
UAI9208-1:8 | W6161 | 0616COM1 | BLK | 20 | 83.A5 | AP0616:COM1 | ORBIT 60^DOOR PANEL | 83.A6
FLOATING | W6161 | 0616SHLD1 | SH | 20 | 83.A6 | AP0616:SHLD1 | ORBIT 60^DOOR PANEL | 83.A6
UAI9208-2:7 | W6171 | 0617SIG1 | RED | 20 | 83.B5 | AP0617:SIG1 | ORBIT 60^DOOR PANEL | 83.B6
UAI9208-2:8 | W6171 | 0617COM1 | BLK | 20 | 83.B5 | AP0617:COM1 | ORBIT 60^DOOR PANEL | 83.B6
FLOATING | W6171 | 0617SHLD1 | SH | 20 | 83.B6 | AP0617:SHLD1 | ORBIT 60^DOOR PANEL | 83.B6
UAI9208-3:7 | W6172 | 0617SIG2 | RED | 20 | 83.B5 | AP0617:SIG2 | ORBIT 60^DOOR PANEL | 83.B6
UAI9208-3:8 | W6172 | 0617COM2 | BLK | 20 | 83.B5 | AP0617:COM2 | ORBIT 60^DOOR PANEL | 83.B6
FLOATING | W6172 | 0617SHLD2 | SH | 20 | 83.B6 | AP0617:SHLD2 | ORBIT 60^DOOR PANEL | 83.B6
UAI9208-4:7 | W6173 | 0617SIG3 | RED | 20 | 83.C5 | AP0617:SIG3 | ORBIT 60^DOOR PANEL | 83.C6
UAI9208-4:8 | W6173 | 0617COM3 | BLK | 20 | 83.C5 | AP0617:COM3 | ORBIT 60^DOOR PANEL | 83.C6
FLOATING | W6173 | 0617SHLD3 | SH | 20 | 83.C6 | AP0617:SHLD3 | ORBIT 60^DOOR PANEL | 83.C6
UAI9208-5:7 | W6174 | 0617SIG4 | RED | 20 | 83.C5 | AP0617:SIG4 | ORBIT 60^DOOR PANEL | 83.C6
UAI9208-5:8 | W6174 | 0617COM4 | BLK | 20 | 83.C5 | AP0617:COM4 | ORBIT 60^DOOR PANEL | 83.C6
FLOATING | W6174 | 0617SHLD4 | SH | 20 | 83.C6 | AP0617:SHLD4 | ORBIT 60^DOOR PANEL | 83.C6
UAI9208-6:7 | W6181 | 0618SIG1 | RED | 20 | 83.C5 | AP0618:SIG1 | ORBIT 60^DOOR PANEL | 83.C6
UAI9208-6:8 | W6181 | 0618COM1 | BLK | 20 | 83.C5 | AP0618:COM1 | ORBIT 60^DOOR PANEL | 83.C6
FLOATING | W6181 | 0618SHLD1 | SH | 20 | 83.D6 | AP0618:SHLD1 | ORBIT 60^DOOR PANEL | 83.C6
UAI9208-7:7 | W6182 | 0618SIG2 | RED | 20 | 83.D5 | AP0618:SIG2 | ORBIT 60^DOOR PANEL | 83.D6
UAI9208-7:8 | W6182 | 0618COM2 | BLK | 20 | 83.D5 | AP0618:COM2 | ORBIT 60^DOOR PANEL | 83.D6
FLOATING | W6182 | 0618SHLD2 | SH | 20 | 83.D6 | AP0618:SHLD2 | ORBIT 60^DOOR PANEL | 83.D6
UAI9209-1:7 | W6211 | 0621SIG1 | RED | 20 | 84.A5 | AP0621:SIG1 | ORBIT 60^DOOR PANEL | 84.A6
UAI9209-1:8 | W6211 | 0621COM1 | BLK | 20 | 84.A5 | AP0621:COM1 | ORBIT 60^DOOR PANEL | 84.A6
FW1213:1 | W6211 | 0621SHLD1 | SH | 20 | 84.A6 | AP0621:SHLD1 | ORBIT 60^DOOR PANEL | 84.A6
UAI9208-8:7 | W6213 | 0621SIG3 | RED | 20 | 83.D5 | AP0621:SIG3 | ORBIT 60^DOOR PANEL | 83.D6
UAI9208-8:8 | W6213 | 0621COM3 | BLK | 20 | 83.D5 | AP0621:COM3 | ORBIT 60^DOOR PANEL | 83.D6
FLOATING | W6213 | 0621SHLD3 | SH | 20 | 83.D6 | AP0621:SHLD3 | ORBIT 60^DOOR PANEL | 83.D6
FU0274:LI | SC | FU0200LI | WHT | 14 | 11.C3 | FU0190:LI | PWR,DISTRIBUTION RAIL^LEFT DOOR | 11.D3
FU0274:LI | SC | FU0200LI | WHT | 14 | 11.C3 | FU0273:LI | PWR,DISTRIBUTION RAIL^LEFT DOOR | 11.B3
XT0134:2 | SC | 0V | WHT | 16 | 16.B4 | XT0560:2 | PWR,DISTRIBUTION RAIL^LEFT DOOR | 11.B2
XT0138:2 | SC | FU0136 | WHT | 12 | 16.A4 | XT0560:1 | PWR,DISTRIBUTION RAIL^LEFT DOOR | 11.A2
XT0233:3 | SC | FU0210 | WHT | 14 | 16.C5 | FU0680:LI | PWR,DISTRIBUTION RAIL^LEFT DOOR | 5.B2
XT0235:3 | SC | 0V | WHT | 14 | 16.D5 | XT0680:2 | PWR,DISTRIBUTION RAIL^LEFT DOOR | 5.B3
XT0240:11 | SC | FU0139 | WHT | 20 | 18.C4 | XT0563:6 | PWR,DISTRIBUTION RAIL^LEFT DOOR | 14.C6
XT0240:13 | SC | KA023612 | WHT | 20 | 18.D4 | XT0563:3 | PWR,DISTRIBUTION RAIL^LEFT DOOR | 14.B6
XT0240:2 | SC | ESTOPB | WHT | 20 | 18.A3 | XT0563:1 | PWR,DISTRIBUTION RAIL^LEFT DOOR | 14.D6
XT0240:3 | SC | ESTOPA | WHT | 20 | 18.A3 | XT0563:2 | PWR,DISTRIBUTION RAIL^LEFT DOOR | 14.D6
XT0240:6 | SC | KA0241A1 | WHT | 20 | 18.C3 | XT0563:5 | PWR,DISTRIBUTION RAIL^LEFT DOOR | 14.C6
XT0240:9 | SC | 0V | WHT | 20 | 18.D3 | XT0563:4 | PWR,DISTRIBUTION RAIL^LEFT DOOR | 14.B6
SolarTools ver. 24.0.84.26264 (Jun 3, 2025)
Report date: 7/10/2025 2:57 PM

## 2 BAY RIGHT WALL
2 BAY RIGHT WALL
Project # | G9440
Project Name | NOC AL SHAHEEN T130
Revision | A.5
Controls DE | G. Colby
Phone:
Controls ME | R. Duran
Phone:
From | [5 empty] | To
Device ID | Cable (W) Conductor (SC) Jumper Clip (JC) | Wire No. | Wire ID | Gauge/Size | Page/Zone | Device ID | Location | Page/Zone
XT0050:1 | JC | 0V | CLIP | --- | 10.B1 | XT0050:2 | 2 BAY RIGHT WALL | 10.B1
XT0050:2 | JC | 0V | CLIP | --- | 10.B1 | XT0050:3 | 2 BAY RIGHT WALL | 10.B1
XT0060:1 | JC | 0V | CLIP | --- | 9.D1 | XT0060:2 | 2 BAY RIGHT WALL | 9.D1
XT0110:3 | JC | 0V | CLIP | --- | 23.A6 | XT0110:2 | 2 BAY RIGHT WALL | 23.A6
AF0051:COM | SC | 0V | WHT | 14 | 10.B2 | XT0050:2 | 2 BAY RIGHT WALL | 10.B1
AF0051:J | SC | * |  |  | 10.B2 | AF0052:P | 2 BAY RIGHT WALL | 10.B3
AF0051:P | SC | * |  |  | 10.B2 | AU0050:J | 2 BAY RIGHT WALL | 10.A2
AF0051:V+ | SC | FU0051 | WHT | 14 | 10.B2 | FU0051:LD | 2 BAY RIGHT WALL | 10.B1
AF0052:COM | SC | 0V | WHT | 14 | 10.B3 | XT0050:2 | 2 BAY RIGHT WALL | 10.B1
AF0052:J | SC | * |  |  | 10.B3 | AF0053:P | 2 BAY RIGHT WALL | 10.B3
AF0052:V+ | SC | FU0052 | WHT | 14 | 10.B3 | FU0052:LD | 2 BAY RIGHT WALL | 10.B1
AF0053:COM | SC | 0V | WHT | 14 | 10.B3 | XT0050:3 | 2 BAY RIGHT WALL | 10.B1
AF0053:J | SC | * |  |  | 10.B3 | AF0054:P | 2 BAY RIGHT WALL | 10.B4
AF0053:V+ | SC | FU0053 | WHT | 16 | 10.B3 | FU0053:LD | 2 BAY RIGHT WALL | 10.B1
AF0054:COM | SC | AU0050N | WHT | 16 | 10.B4 | AU0050:COM | 2 BAY RIGHT WALL | 10.A2
AF0054:COM | SC | AF0054N | WHT | 20 | 10.B4 | AF0055:COM | 2 BAY RIGHT WALL | 10.B5
AF0054:J | SC | * |  |  | 10.B4 | AF0055:P | 2 BAY RIGHT WALL | 10.B5
AF0054:V+ | SC | AU0050P | WHT | 14 | 10.B4 | AU0050:V+ | 2 BAY RIGHT WALL | 10.A2
AF0054:V+ | SC | AF0054P | WHT | 20 | 10.B4 | AF0055:V+ | 2 BAY RIGHT WALL | 10.B5
AF0055:COM | SC | AF0055N | WHT | 20 | 10.B5 | AF0056:COM | 2 BAY RIGHT WALL | 10.B5
AF0055:J | SC | * |  |  | 10.B5 | AF0056:P | 2 BAY RIGHT WALL | 10.B5
AF0055:SH | SC | IEG8240-6 | GRN | 14 | 10.B5 | IEG8240:6 | 2 BAY RIGHT WALL | 10.B4
AF0055:SH | SC | AF0055G | GRN | 16 | 10.B5 | AF0056:SH | 2 BAY RIGHT WALL | 10.B5
AF0055:V+ | SC | AF0055P | WHT | 20 | 10.B5 | AF0056:V+ | 2 BAY RIGHT WALL | 10.B5
AF0056:COM | SC | AF0056N | WHT | 20 | 10.B5 | AF0057:COM | 2 BAY RIGHT WALL | 10.B6
AF0056:J | SC | * |  |  | 10.B5 | AF0057:P | 2 BAY RIGHT WALL | 10.B6
AF0056:SH | SC | AF0056G | GRN | 14 | 10.B5 | AF0057:SH | 2 BAY RIGHT WALL | 10.B6
AF0056:V+ | SC | AF0056P | WHT | 20 | 10.B5 | AF0057:V+ | 2 BAY RIGHT WALL | 10.B6
AF0061:00 | SC | FCE1420-9 | WHT | 20 | 45.C7 | XT-9335:10 | 2 BAY RIGHT WALL | 45.C5
AF0061:08 | SC | FCE2140-9 | WHT | 20 | 57.C7 | XT-9334:10 | 2 BAY RIGHT WALL | 57.B5
AF0061:12 | SC | FCE1440-9 | WHT | 20 | 46.C7 | XT-9336:13 | 2 BAY RIGHT WALL | 46.C5
AF0061:16 | SC | FCE1420-10 | WHT | 20 | 45.C7 | XT-9335:11 | 2 BAY RIGHT WALL | 45.C5
AF0061:18 | SC | FCE1420-8 | WHT | 20 | 45.B7 | XT-9335:8 | 2 BAY RIGHT WALL | 45.B5
AF0061:24 | SC | FCE2140-10 | WHT | 20 | 57.C7 | XT-9334:11 | 2 BAY RIGHT WALL | 57.B5
AF0061:28 | SC | FCE1440-10 | WHT | 20 | 46.C7 | XT-9336:14 | 2 BAY RIGHT WALL | 46.C5
AF0061:30 | SC | FCE1440-8 | WHT | 20 | 46.B7 | XT-9336:11 | 2 BAY RIGHT WALL | 46.B5
AF0061:COM | SC | 0V | WHT | 14 | 9.C2 | XT0060:2 | 2 BAY RIGHT WALL | 9.D1
AF0061:J | SC | * |  |  | 9.C2 | AF0062:P | 2 BAY RIGHT WALL | 9.C3
AF0061:P | SC | * |  |  | 9.C2 | AU0060:J | 2 BAY RIGHT WALL | 9.C2
AF0061:V+ | SC | FU0061 | WHT | 14 | 9.C2 | FU0061:LD | 2 BAY RIGHT WALL | 9.D1
AF0062:COM | SC | 0V | WHT | 14 | 9.C3 | XT0060:2 | 2 BAY RIGHT WALL | 9.D1
AF0062:J | SC | * |  |  | 9.C3 | AF0063:P | 2 BAY RIGHT WALL | 9.C3
AF0062:V+ | SC | FU0062 | WHT | 14 | 9.C3 | FU0062:LD | 2 BAY RIGHT WALL | 9.D1
AF0063:00 | SC | FCE1420-14 | WHT | 20 | 45.D7 | XT-9335:17 | 2 BAY RIGHT WALL | 45.D5
AF0063:01 | SC | FCE1420-12 | WHT | 20 | 45.C7 | XT-9335:14 | 2 BAY RIGHT WALL | 45.C5
AF0063:04 | SC | FCE2140-14 | WHT | 20 | 57.D7 | XT-9334:17 | 2 BAY RIGHT WALL | 57.C5
AF0063:05 | SC | FCE2140-12 | WHT | 20 | 57.C7 | XT-9334:14 | 2 BAY RIGHT WALL | 57.C5
AF0063:06 | SC | FCE1440-14 | WHT | 20 | 46.D7 | XT-9336:20 | 2 BAY RIGHT WALL | 46.D5
AF0063:07 | SC | FCE1440-12 | WHT | 20 | 46.C7 | XT-9336:17 | 2 BAY RIGHT WALL | 46.C5
AF0063:32 | SC | FCE1420-13 | WHT | 20 | 45.D7 | XT-9335:16 | 2 BAY RIGHT WALL | 45.D5
AF0063:33 | SC | FCE1420-11 | WHT | 20 | 45.C7 | XT-9335:13 | 2 BAY RIGHT WALL | 45.C5
AF0063:36 | SC | FCE2140-13 | WHT | 20 | 57.D7 | XT-9334:16 | 2 BAY RIGHT WALL | 57.C5
AF0063:37 | SC | FCE2140-11 | WHT | 20 | 57.C7 | XT-9334:13 | 2 BAY RIGHT WALL | 57.C5
AF0063:38 | SC | FCE1440-13 | WHT | 20 | 46.D7 | XT-9336:19 | 2 BAY RIGHT WALL | 46.D5
AF0063:39 | SC | FCE1440-11 | WHT | 20 | 46.C7 | XT-9336:16 | 2 BAY RIGHT WALL | 46.C5
AF0063:COM | SC | AF0063N | WHT | 16 | 9.C3 | AF0064:COM | 2 BAY RIGHT WALL | 9.C4
AF0063:COM | SC | AU0060N | WHT | 16 | 9.C3 | AU0060:COM | 2 BAY RIGHT WALL | 9.C2
AF0063:J | SC | * |  |  | 9.C3 | AF0064:P | 2 BAY RIGHT WALL | 9.C4
AF0063:V+ | SC | AF0063P | WHT | 16 | 9.C3 | AF0064:V+ | 2 BAY RIGHT WALL | 9.C4
AF0063:V+ | SC | AU0060P | WHT | 16 | 9.C3 | AU0060:V+ | 2 BAY RIGHT WALL | 9.C2
AF0064:COM | SC | AF0064N | WHT | 16 | 9.C4 | AF0065:COM | 2 BAY RIGHT WALL | 9.C5
AF0064:J | SC | * |  |  | 9.C4 | AF0065:P | 2 BAY RIGHT WALL | 9.C5
AF0064:SH | SC | AF0064G | GRN | 14 | 9.C4 | AF0065:SH | 2 BAY RIGHT WALL | 9.C5
AF0064:SH | SC | IEG02304 | GRN | 14 | 9.C4 | IEG8240:4 | 2 BAY RIGHT WALL | 9.D4
AF0064:V+ | SC | AF0064P | WHT | 16 | 9.C4 | AF0065:V+ | 2 BAY RIGHT WALL | 9.C5
AF0065:COM | SC | AF0065N | WHT | 16 | 9.C5 | AF0068:COM | 2 BAY RIGHT WALL | 9.C6
AF0065:J | SC | * |  |  | 9.C5 | AF0066:P | 2 BAY RIGHT WALL | 9.C5
AF0065:SH | SC | AF0065G | GRN | 14 | 9.C5 | AF0066:SH | 2 BAY RIGHT WALL | 9.C5
AF0065:V+ | SC | AF0065P | WHT | 16 | 9.C5 | AF0068:V+ | 2 BAY RIGHT WALL | 9.C6
AF0066:COM | SC | 0V | WHT | 14 | 9.C5 | XT0060:2 | 2 BAY RIGHT WALL | 9.D1
AF0066:J | SC | * |  |  | 9.C5 | AF0067:P | 2 BAY RIGHT WALL | 9.C6
AF0066:SH | SC | AF0066G | GRN | 14 | 9.C5 | AF0068:SH | 2 BAY RIGHT WALL | 9.C6
AF0066:V+ | SC | FU0063 | WHT | 16 | 9.C5 | FU0063:LD | 2 BAY RIGHT WALL | 9.D1
AF0067:00 | SC | SV2150-1 | WHT | 16 | 59.D7 | XT-9331:1 | 2 BAY RIGHT WALL | 59.D4
AF0067:16 | SC | SV2150-2 | WHT | 16 | 59.D7 | XT-9331:2 | 2 BAY RIGHT WALL | 59.D4
AF0067:22 | SC | SV2220-2 | WHT | 16 | 70.B7 | XT-9381:11 | 2 BAY RIGHT WALL | 70.B4
AF0067:COM | SC | 0V | WHT | 14 | 9.C6 | XT0060:2 | 2 BAY RIGHT WALL | 9.D1
AF0067:J | SC | * |  |  | 9.C6 | AF0068:P | 2 BAY RIGHT WALL | 9.C6
AF0067:V+ | SC | FU0064 | WHT | 16 | 9.C6 | FU0064:LD | 2 BAY RIGHT WALL | 9.D1
AF0071:COM | SC | AF0071N | WHT | 16 | 9.B2 | AF0072:COM | 2 BAY RIGHT WALL | 9.A3
AF0071:COM | SC | AU0070N | WHT | 16 | 9.B2 | AU0070:COM | 2 BAY RIGHT WALL | 9.A2
AF0071:J | SC | * |  |  | 9.B2 | AF0072:P | 2 BAY RIGHT WALL | 9.A3
AF0071:P | SC | * |  |  | 9.B2 | AU0070:J | 2 BAY RIGHT WALL | 9.A2
AF0071:SH | SC | AF0071G | GRN | 14 | 9.B2 | AF0072:SH | 2 BAY RIGHT WALL | 9.A3
AF0071:SH | SC | IEG02305 | GRN | 14 | 9.B2 | IEG8240:5 | 2 BAY RIGHT WALL | 9.B2
AF0071:V+ | SC | AF0071P | WHT | 16 | 9.B2 | AF0072:V+ | 2 BAY RIGHT WALL | 9.A3
AF0071:V+ | SC | AU0070P | WHT | 16 | 9.B2 | AU0070:V+ | 2 BAY RIGHT WALL | 9.A2
AF0072:COM | SC | AF0072N | WHT | 16 | 9.A3 | AF0073:COM | 2 BAY RIGHT WALL | 9.B3
AF0072:J | SC | * |  |  | 9.A3 | AF0073:P | 2 BAY RIGHT WALL | 9.B3
AF0072:SH | SC | AF0072G | GRN | 14 | 9.A3 | AF0073:SH | 2 BAY RIGHT WALL | 9.B3
AF0072:V+ | SC | AF0072P | WHT | 16 | 9.A3 | AF0073:V+ | 2 BAY RIGHT WALL | 9.B3
AF0073:COM | SC | AF0073N | WHT | 16 | 9.B3 | AF0074:COM | 2 BAY RIGHT WALL | 9.B4
AF0073:J | SC | * |  |  | 9.B3 | AF0074:P | 2 BAY RIGHT WALL | 9.B4
AF0073:SH | SC | AF0073G | GRN | 14 | 9.B3 | AF0074:SH | 2 BAY RIGHT WALL | 9.B4
AF0073:V+ | SC | AF0073P | WHT | 16 | 9.B3 | AF0074:V+ | 2 BAY RIGHT WALL | 9.B4
AF0074:COM | SC | AF0074N | WHT | 16 | 9.B4 | AF0075:COM | 2 BAY RIGHT WALL | 9.A5
AF0074:J | SC | * |  |  | 9.B4 | AF0075:P | 2 BAY RIGHT WALL | 9.A5
AF0074:SH | SC | AF0074G | GRN | 14 | 9.B4 | AF0075:SH | 2 BAY RIGHT WALL | 9.A5
AF0074:V+ | SC | AF0074P | WHT | 16 | 9.B4 | AF0075:V+ | 2 BAY RIGHT WALL | 9.A5
AF0075:J | SC | * |  |  | 9.A5 | AF0076:P | 2 BAY RIGHT WALL | 9.A5
AF0076:17 | SC | FCE2140-8 | WHT | 20 | 57.B7 | XT-9334:8 | 2 BAY RIGHT WALL | 57.B5
AF0076:COM | SC | 0V | WHT | 14 | 9.A5 | XT0070:1 | 2 BAY RIGHT WALL | 9.B1
AF0076:V+ | SC | FU0071 | WHT | 16 | 9.A5 | FU0071:LD | 2 BAY RIGHT WALL | 9.B1
AF0450:32 | SC | * |  |  | 22.B5 | XT0400:2 | 2 BAY RIGHT WALL | 22.C6
AF0450:53 | SC | 0V | WHT | 16 | 22.B5 | XT0450:2 | 2 BAY RIGHT WALL | 22.A5
AF0450:55 | SC | FU0450 | WHT | 16 | 22.B5 | FU0450:LD | 2 BAY RIGHT WALL | 22.A4
AU0050:COM | SC | 0V | WHT | 14 | 10.A2 | XT0050:1 | 2 BAY RIGHT WALL | 10.B1
AU0050:V+ | SC | FU0050 | WHT | 14 | 10.A2 | FU0050:LD | 2 BAY RIGHT WALL | 10.B1
AU0060:COM | SC | 0V | WHT | 14 | 9.C2 | XT0060:1 | 2 BAY RIGHT WALL | 9.D1
AU0060:V+ | SC | FU0060 | WHT | 14 | 9.C2 | FU0060:LD | 2 BAY RIGHT WALL | 9.C1
AU0070:COM | SC | 0V | WHT | 14 | 9.A2 | XT0070:1 | 2 BAY RIGHT WALL | 9.B1
AU0070:V+ | SC | FU0070 | WHT | 16 | 9.A2 | FU0070:LD | 2 BAY RIGHT WALL | 9.B1
FU0050:LI | SC | FU0210 | WHT | 14 | 10.B1 | FU0051:LI | 2 BAY RIGHT WALL | 10.B1
FU0051:LI | SC | FU0210 | WHT | 14 | 10.B1 | FU0052:LI | 2 BAY RIGHT WALL | 10.B1
FU0052:LI | SC | FU0210 | WHT | 14 | 10.B1 | FU0053:LI | 2 BAY RIGHT WALL | 10.B1
FU0053:LI | SC | FU0210 | WHT | 14 | 10.B1 | FU0054:LI | 2 BAY RIGHT WALL | 10.B1
FU0054:LD | SC | FU0054 | WHT | 14 | 10.B1 | XT0050:4 | 2 BAY RIGHT WALL | 64.C7
FU0054:LI | SC | FU0210 | WHT | 14 | 10.B1 | FU0055:LI | 2 BAY RIGHT WALL | 10.B1
FU0055:LD | SC | FU0055 | WHT | 14 | 10.B1 | XT0050:6 | 2 BAY RIGHT WALL | 66.C6
FU0060:LI | SC | FU0210 | WHT | 14 | 9.C1 | FU0061:LI | 2 BAY RIGHT WALL | 9.D1
FU0061:LI | SC | FU0210 | WHT | 14 | 9.D1 | FU0062:LI | 2 BAY RIGHT WALL | 9.D1
FU0062:LI | SC | FU0210 | WHT | 14 | 9.D1 | FU0063:LI | 2 BAY RIGHT WALL | 9.D1
FU0063:LI | SC | FU0210 | WHT | 14 | 9.D1 | FU0064:LI | 2 BAY RIGHT WALL | 9.D1
FU0070:LI | SC | FU0210 | WHT | 14 | 9.B1 | FU0071:LI | 2 BAY RIGHT WALL | 9.B1
FU0110:LI | SC | FU0136 | WHT | 14 | 23.A5 | XT0110:1 | 2 BAY RIGHT WALL | 23.A6
FU0111:LI | SC | FU0110 | WHT | 14 | 23.A5 | FU0110:LD | 2 BAY RIGHT WALL | 23.A5
FU0111:LI | SC | FU0110 | WHT | 14 | 23.A5 | FU0112:LI | 2 BAY RIGHT WALL | 23.A5
FU0450:LI | SC | FU0136 | WHT | 14 | 22.A4 | XT0450:1 | 2 BAY RIGHT WALL | 22.A5
GR8241: | SC | IEG8240-1 | GRN | 14 | 4.D4 | IEG8240:1 | 2 BAY RIGHT WALL | 4.D3
GR8242: | SC | IEG8240-2 | GRN | 14 | 4.D4 | IEG8240:2 | 2 BAY RIGHT WALL | 4.D4
GR8243: | SC | IEG8240-3 | GRN | 14 | 4.D5 | IEG8240:3 | 2 BAY RIGHT WALL | 4.D5
GR9241: | SC | GR9241 | GRN/YEL | 14 | 4.D4 | FG0005:2 | 2 BAY RIGHT WALL | 4.D3
GR9242: | SC | GR9242 | GRN/YEL | 14 | 4.D4 | FG0006:3 | 2 BAY RIGHT WALL | 4.D4
XT0050:3 | SC | 0V | WHT | 14 | 10.B1 | XT0050:7 | 2 BAY RIGHT WALL | 66.C6
XT0050:5 | SC | 0V | WHT | 16 | 64.C7 | XT-9338:4 | 2 BAY RIGHT WALL | 64.C4
XT0050:5 | SC | 0V | WHT | 20 | 64.C7 | XT0050:2 | 2 BAY RIGHT WALL | 10.B1
XT0070:1 | SC | 0V | WHT | 14 | 9.B1 | XT0060:1 | 2 BAY RIGHT WALL | 9.D1
XT-9338:2 | SC | 0V | WHT | 16 | 64.C4 | XT0050:5 | 2 BAY RIGHT WALL | 64.C7
XT-9338:3 | SC | FU0054 | WHT | 20 | 64.C4 | XT0050:4 | 2 BAY RIGHT WALL | 64.C7
XT-9338A:1 | SC | FU0055 | WHT | 16 | 66.C4 | XT0050:6 | 2 BAY RIGHT WALL | 66.C6
XT-9338A:2 | SC | 0V | WHT | 16 | 66.C4 | XT0050:7 | 2 BAY RIGHT WALL | 66.C6
XT-9381:8 | SC | 0V | WHT | 14 | 67.C4 | XT-9381:5 | 2 BAY RIGHT WALL | 68.C4
AF0055:04 | W0552 | FT2220-1 | RED | 20 | 68.C7 | XT-9380:7 | 2 BAY RIGHT WALL | 68.C4
AF0055:20 | W0552 | FT2220-2 | BLK | 20 | 68.C7 | XT-9380:8 | 2 BAY RIGHT WALL | 68.C4
AF0055:52 | W0552 | FT2220-S1 | SH | 20 | 68.C7 | XT-9380:9 | 2 BAY RIGHT WALL | 68.C4
AF0055:06 | W0553 | FT2240-1 | RED | 20 | 67.C7 | XT-9380:10 | 2 BAY RIGHT WALL | 67.C4
AF0055:22 | W0553 | FT2240-2 | BLK | 20 | 67.C7 | XT-9380:11 | 2 BAY RIGHT WALL | 67.C4
AF0055:54 | W0553 | FT2240-S1 | SH | 20 | 67.C7 | XT-9380:12 | 2 BAY RIGHT WALL | 67.C4
AF0066:00 | W0570 | FCE2228-3 | RED | 20 | 66.B7 | XT-9337:7 | 2 BAY RIGHT WALL | 66.B4
AF0066:16 | W0570 | FCE2228-4 | BLK | 20 | 66.B7 | XT-9337:8 | 2 BAY RIGHT WALL | 66.B4
AF0066:48 | W0570 | FCE2228-S1 | SH | 20 | 66.B7 | XT-9337:9 | 2 BAY RIGHT WALL | 66.B4
AF0066:02 | W0571 | FCE2225-1 | RED | 20 | 64.B7 | XT-9337:1 | 2 BAY RIGHT WALL | 64.B4
AF0066:18 | W0571 | FCE2225-2 | BLK | 20 | 64.B7 | XT-9337:2 | 2 BAY RIGHT WALL | 64.B4
AF0066:50 | W0571 | FCE2225-S1 | SH | 20 | 64.B7 | XT-9337:3 | 2 BAY RIGHT WALL | 64.B4
AF0064:44 | W0643 | IT6212-1 | RED | 20 | 118.D7 | XT-9360:4 | 2 BAY RIGHT WALL | 118.D4
AF0064:12 | W0643 | IT6212-2 | BLK | 20 | 118.D7 | XT-9360:5 | 2 BAY RIGHT WALL | 118.D4
AF0064:60 | W0643 | IT6212-S | SH | 20 | 118.D7 | XT-9360:6 | 2 BAY RIGHT WALL | 118.D4
AF0065:12 | W0646 | UA1200-J13 | RED | 20 | 19.A7 | XT-9380:1 | 2 BAY RIGHT WALL | 19.A4
AF0065:28 | W0646 | UA1200-J11 | BLK | 20 | 19.A7 | XT-9380:2 | 2 BAY RIGHT WALL | 19.A4
AF0065:60 | W0646 | UA1200-S | SH | 20 | 19.A7 | XT-9380:3 | 2 BAY RIGHT WALL | 19.A4
AF0066:06 | W0663 | FCE2140-1 | RED | 20 | 57.A7 | XT-9334:1 | 2 BAY RIGHT WALL | 57.A5
AF0066:22 | W0663 | FCE2140-2 | BLK | 20 | 57.A7 | XT-9334:2 | 2 BAY RIGHT WALL | 57.A5
AF0066:54 | W0663 | FCE2140-S1 | SH | 20 | 57.A7 | XT-9334:3 | 2 BAY RIGHT WALL | 57.A5
AF0066:10 | W0665 | FCE1440-1 | RED | 20 | 46.A7 | XT-9336:1 | 2 BAY RIGHT WALL | 46.A5
AF0066:26 | W0665 | FCE1440-2 | BLK | 20 | 46.A7 | XT-9336:2 | 2 BAY RIGHT WALL | 46.A5
AF0066:58 | W0665 | FCE1440-S1 | SH | 20 | 46.A7 | XT-9336:3 | 2 BAY RIGHT WALL | 46.A5
AF0072:32 | W0720 | IT6211-1 | RED | 20 | 117.D7 | XT-9360:1 | 2 BAY RIGHT WALL | 117.D4
AF0072:00 | W0720 | IT6211-2 | BLK | 20 | 117.D7 | XT-9360:2 | 2 BAY RIGHT WALL | 117.D4
AF0072:48 | W0720 | IT6211-S | SH | 20 | 117.D7 | XT-9360:3 | 2 BAY RIGHT WALL | 117.D4
AF0074:02 | W0741 | FCE2140-5 | RED | 20 | 57.B7 | XT-9334:4 | 2 BAY RIGHT WALL | 57.A5
AF0074:18 | W0741 | FCE2140-6 | BLK | 20 | 57.B7 | XT-9334:5 | 2 BAY RIGHT WALL | 57.B5
AF0074:50 | W0741 | FCE2140-S2 | SH | 20 | 57.B7 | XT-9334:6 | 2 BAY RIGHT WALL | 57.B5
AF0074:04 | W0742 | FCE2228-5 | RED | 20 | 66.B7 | XT-9337:10 | 2 BAY RIGHT WALL | 66.B4
AF0074:20 | W0742 | FCE2228-6 | BLK | 20 | 66.B7 | XT-9337:11 | 2 BAY RIGHT WALL | 66.B4
AF0074:52 | W0742 | FCE2228-S2 | SH | 20 | 66.B7 | XT-9337:12 | 2 BAY RIGHT WALL | 66.B4
AF0074:06 | W0743 | FCE2225-3 | RED | 20 | 64.B7 | XT-9337:4 | 2 BAY RIGHT WALL | 64.B4
AF0074:22 | W0743 | FCE2225-4 | BLK | 20 | 64.B7 | XT-9337:5 | 2 BAY RIGHT WALL | 64.B4
AF0074:54 | W0743 | FCE2225-S2 | SH | 20 | 64.B7 | XT-9337:6 | 2 BAY RIGHT WALL | 64.B4
AF0450:L1 | WC0005 | AU0050L2 | ENET | CABLE | 3.A5 | AU0050:L2 | 2 BAY RIGHT WALL | 3.A2
AU0050:L1 | WC0006 | AU0060L2 | ENET | CABLE | 3.A2 | AU0060:L2 | 2 BAY RIGHT WALL | 3.A6
AU0060:L1 | WC0007 | AU0070L2 | ENET | CABLE | 3.A6 | AU0070:L2 | 2 BAY RIGHT WALL | 3.A5
AF0066:08 | WC4190 | FCE1420-1 | RED | 20 | 45.A7 | XT-9335:1 | 2 BAY RIGHT WALL | 45.A5
AF0066:24 | WC4190 | FCE1420-2 | BLK | 20 | 45.A7 | XT-9335:2 | 2 BAY RIGHT WALL | 45.A5
AF0066:56 | WC4190 | FCE1420-S1 | SH | 20 | 45.A7 | XT-9335:3 | 2 BAY RIGHT WALL | 45.A5
AF0450:L2 | WC0045 | AF0450L2 | ENET | CABLE | 3.A5 | AU0120:L1 | 1 BAY RIGHT WALL | 3.B2
FU0450:LD | SC | FU0450 | WHT | 16 | 22.A4 | UAI1520:+24V | 2 BAY BACK LEFT WALL | 52.A5
XT0450:2 | SC | 0V | WHT | 10 | 22.A5 | UAI1520:-24V | 2 BAY BACK LEFT WALL | 52.A5
XT-9355:2 | SC | UF1300-DI2P | WHT | 20 | 43.A5 | UAI9215-1:11 | 2 BAY BACK LEFT WALL | 91.D5
AF0055:08 | W0554 | 005508 | RED | 20 | 78.B7 | UAI9219A-1:+8 | 2 BAY BACK LEFT WALL | 78.B5
AF0055:24 | W0554 | 005524 | BLK | 20 | 78.B7 | UAI9219A-1:-7 | 2 BAY BACK LEFT WALL | 78.B5
AF0055:56 | W0554 | 005556 | SH | 20 | 78.B7 | FW1207:2 | 2 BAY BACK LEFT WALL | 78.C6
AF0055:12 | W0556 | 005512 | RED | 20 | 64.A7 | UAI9212-1:+8 | 2 BAY BACK LEFT WALL | 64.A5
AF0055:28 | W0556 | 005528 | BLK | 20 | 64.A7 | UAI9212-1:-7 | 2 BAY BACK LEFT WALL | 64.A5
AF0055:60 | W0556 | 005560 | SH | 20 | 64.A7 | FW1205:1 | 2 BAY BACK LEFT WALL | 64.A6
AF0055:14 | W0557 | 005514 | RED | 20 | 75.A7 | UAI9242-1:+8 | 2 BAY BACK LEFT WALL | 75.A5
AF0055:30 | W0557 | 005530 | BLK | 20 | 75.A7 | UAI9242-1:-7 | 2 BAY BACK LEFT WALL | 75.A5
AF0055:62 | W0557 | 005562 | SH | 20 | 75.A7 | FW1214:1 | 2 BAY BACK LEFT WALL | 75.A6
AF0056:00 | W0560 | 005600 | RED | 20 | 69.A7 | UAI9212-2:+8 | 2 BAY BACK LEFT WALL | 69.A5
AF0056:16 | W0560 | 005616 | BLK | 20 | 69.A7 | UAI9212-2:-7 | 2 BAY BACK LEFT WALL | 69.A5
AF0056:48 | W0560 | 005648 | SH | 20 | 69.A7 | FW1206:1 | 2 BAY BACK LEFT WALL | 69.A6
AF0056:02 | W0561 | 005602 | RED | 20 | 80.A7 | UAI9218-6:+8 | 2 BAY BACK LEFT WALL | 80.A5
AF0056:18 | W0561 | 005618 | BLK | 20 | 80.A7 | UAI9218-6:-7 | 2 BAY BACK LEFT WALL | 80.A5
AF0056:50 | W0561 | 005650 | SH | 20 | 80.A7 | FW1210:1 | 2 BAY BACK LEFT WALL | 80.A6
AF0056:04 | W0562 | 005604 | RED | 20 | 73.A7 | UAI9218-7:+8 | 2 BAY BACK LEFT WALL | 73.A5
AF0056:20 | W0562 | 005620 | BLK | 20 | 73.A7 | UAI9218-7:-7 | 2 BAY BACK LEFT WALL | 73.A5
AF0056:52 | W0562 | 005652 | SH | 20 | 73.A7 | FW1211:1 | 2 BAY BACK LEFT WALL | 73.A6
AF0056:06 | W0563 | 005606 | RED | 20 | 77.B7 | UAI9211-1:+8 | 2 BAY BACK LEFT WALL | 77.B5
AF0056:22 | W0563 | 005622 | BLK | 20 | 77.B7 | UAI9211-1:-7 | 2 BAY BACK LEFT WALL | 77.B5
AF0056:54 | W0563 | 005654 | SH | 20 | 77.B7 | FW1204:1 | 2 BAY BACK LEFT WALL | 77.B6
AF0056:10 | W0565 | 005610 | RED | 20 | 65.A7 | UAI9219-1:+8 | 2 BAY BACK LEFT WALL | 65.A5
AF0056:26 | W0565 | 005626 | BLK | 20 | 65.A7 | UAI9219-1:-7 | 2 BAY BACK LEFT WALL | 65.A5
AF0056:58 | W0565 | 005658 | SH | 20 | 65.A7 | FW1212:1 | 2 BAY BACK LEFT WALL | 65.A6
AF0064:00 | W0640 | 006400 | RED | 20 | 56.A7 | UAI9217-6:+8 | 2 BAY BACK LEFT WALL | 56.A5
AF0064:16 | W0640 | 006416 | BLK | 20 | 56.A7 | UAI9217-6:-7 | 2 BAY BACK LEFT WALL | 56.A5
AF0064:48 | W0640 | 006448 | SH | 20 | 56.A7 | FW1209:1 | 2 BAY BACK LEFT WALL | 56.A6
AF0064:04 | W0641 | 006404 | RED | 20 | 56.C7 | UAI9290-4:+8 | 2 BAY BACK LEFT WALL | 56.C5
AF0064:20 | W0641 | 006420 | BLK | 20 | 56.C7 | UAI9290-4:-7 | 2 BAY BACK LEFT WALL | 56.C5
AF0064:52 | W0641 | 006452 | SH | 20 | 56.C7 | FW0888:2 | 2 BAY BACK LEFT WALL | 56.C6
AF0064:08 | W0642 | 006408 | RED | 20 | 58.A7 | UAI9290-6:+8 | 2 BAY BACK LEFT WALL | 58.A5
AF0064:24 | W0642 | 006424 | BLK | 20 | 58.A7 | UAI9290-6:-7 | 2 BAY BACK LEFT WALL | 58.A5
AF0064:56 | W0642 | 006456 | SH | 20 | 58.A7 | FW1216:1 | 2 BAY BACK LEFT WALL | 58.A6
AF0065:00 | W0650 | 006500 | RED | 20 | 50.A7 | UAI9217-1:+8 | 2 BAY BACK LEFT WALL | 50.A5
AF0065:16 | W0650 | 006516 | BLK | 20 | 50.A7 | UAI9217-1:-7 | 2 BAY BACK LEFT WALL | 50.A5
AF0065:48 | W0650 | 006548 | SH | 20 | 50.A7 | FW0890:1 | 2 BAY BACK LEFT WALL | 50.A6
AF0072:08 | W0722 | 007208 | RED | 20 | 60.A7 | UAI9217-5:+8 | 2 BAY BACK LEFT WALL | 60.A5
AF0072:24 | W0722 | 007224 | BLK | 20 | 60.A7 | UAI9217-5:-7 | 2 BAY BACK LEFT WALL | 60.A5
AF0072:56 | W0722 | 007256 | SH | 20 | 60.A7 | FW0892:1 | 2 BAY BACK LEFT WALL | 60.A6
AF0072:12 | W0723 | 007212 | RED | 20 | 74.A7 | UAI9217-7:+8 | 2 BAY BACK LEFT WALL | 74.A5
AF0072:28 | W0723 | 007228 | BLK | 20 | 74.A7 | UAI9217-7:-7 | 2 BAY BACK LEFT WALL | 74.A5
AF0072:60 | W0723 | 007260 | SH | 20 | 74.A7 | FW0887:1 | 2 BAY BACK LEFT WALL | 74.A6
AF0075:00 | W0750 | 007500 | RED | 20 | 58.A7 | UAI9290-7:+8 | 2 BAY BACK LEFT WALL | 58.A5
AF0075:16 | W0750 | 007516 | BLK | 20 | 58.A7 | UAI9290-7:-7 | 2 BAY BACK LEFT WALL | 58.A5
AF0075:48 | W0750 | 007548 | SH | 20 | 58.A7 | FW1217:1 | 2 BAY BACK LEFT WALL | 58.B6
AF0075:04 | W0751 | 007504 | RED | 20 | 56.D7 | UAI9290-5:+8 | 2 BAY BACK LEFT WALL | 56.D5
AF0075:20 | W0751 | 007520 | BLK | 20 | 56.D7 | UAI9290-5:-7 | 2 BAY BACK LEFT WALL | 56.D5
AF0075:52 | W0751 | 007552 | SH | 20 | 56.D7 | FW0888:3 | 2 BAY BACK LEFT WALL | 56.D6
AF0075:08 | W0752 | 007508 | RED | 20 | 56.B7 | UAI9210-1:+8 | 2 BAY BACK LEFT WALL | 56.B5
AF0075:24 | W0752 | 007524 | BLK | 20 | 56.B7 | UAI9210-1:-7 | 2 BAY BACK LEFT WALL | 56.B5
AF0075:56 | W0752 | 007556 | SH | 20 | 56.B7 | FW0888:1 | 2 BAY BACK LEFT WALL | 56.B6
AF0075:12 | W0753 | 007512 | RED | 20 | 50.B7 | UAI9290-3:+8 | 2 BAY BACK LEFT WALL | 50.B5
AF0075:28 | W0753 | 007528 | BLK | 20 | 50.B7 | UAI9290-3:-7 | 2 BAY BACK LEFT WALL | 50.B5
AF0075:60 | W0753 | 007560 | SH | 20 | 50.B7 | FW0891:1 | 2 BAY BACK LEFT WALL | 50.B6
AF0450:06 | W4501 | UAI1520O/P | RED | 20 | 52.A7 | UAI1520:O/P | 2 BAY BACK LEFT WALL | 52.A5
AF0450:08 | W4501 | UAI15200V | BLK | 20 | 52.A7 | UAI1520:0V | 2 BAY BACK LEFT WALL | 52.A5
AF0450:23 | W4501 | UAI1520S | SH | 20 | 52.A7 | FW-UAI1520:1 | 2 BAY BACK LEFT WALL | 52.A6
AF0051:04 | SC | SV2645-1 | WHT | 16 | 77.B7 | XT-9327:5 | 2 BAY BACK RIGHT PANEL | 77.B4
AF0051:06 | SC | SV2646-1 | WHT | 16 | 77.C7 | XT-9327:7 | 2 BAY BACK RIGHT PANEL | 77.C4
AF0051:08 | SC | SV2647-1 | WHT | 16 | 77.C7 | XT-9327:9 | 2 BAY BACK RIGHT PANEL | 77.C4
AF0051:20 | SC | SV2645-2 | WHT | 16 | 77.B7 | XT-9327:6 | 2 BAY BACK RIGHT PANEL | 77.B4
AF0051:22 | SC | SV2646-2 | WHT | 16 | 77.C7 | XT-9327:8 | 2 BAY BACK RIGHT PANEL | 77.C4
AF0051:24 | SC | SV2647-2 | WHT | 16 | 77.C7 | XT-9327:10 | 2 BAY BACK RIGHT PANEL | 77.C4
AF0052:02 | SC | SV2260-1 | WHT | 16 | 80.C7 | XT-9324:3 | 2 BAY BACK RIGHT PANEL | 80.C4
AF0052:04 | SC | 005204 | WHT | 20 | 71.B7 | KA0225:11 | 2 BAY BACK RIGHT PANEL | 71.B6
AF0052:08 | SC | SV2250-1 | WHT | 16 | 72.C7 | XT-9327:1 | 2 BAY BACK RIGHT PANEL | 72.C4
AF0052:10 | SC | SV2251-1 | WHT | 16 | 72.C7 | XT-9327:3 | 2 BAY BACK RIGHT PANEL | 72.D4
AF0052:18 | SC | SV2260-2 | WHT | 16 | 80.C7 | XT-9324:4 | 2 BAY BACK RIGHT PANEL | 80.C4
AF0052:20 | SC | SV22222 | WHT | 16 | 71.B7 | XT-9324:2 | 2 BAY BACK RIGHT PANEL | 71.B4
AF0052:24 | SC | SV2250-2 | WHT | 16 | 72.C7 | XT-9327:2 | 2 BAY BACK RIGHT PANEL | 72.C4
AF0052:26 | SC | SV2251-2 | WHT | 16 | 72.C7 | XT-9327:4 | 2 BAY BACK RIGHT PANEL | 72.D4
AF0053:02 | SC | SV6430-1 | WHT | 16 | 75.B7 | XT-9330:1 | 2 BAY BACK RIGHT PANEL | 75.B4
AF0053:06 | SC | SV2610-1 | WHT | 16 | 62.B7 | XT-9324:7 | 2 BAY BACK RIGHT PANEL | 62.B4
AF0053:08 | SC | SV2614-1 | WHT | 16 | 78.D7 | XT-9324:9 | 2 BAY BACK RIGHT PANEL | 78.D4
AF0053:18 | SC | SV6430-2 | WHT | 16 | 75.B7 | XT-9330:2 | 2 BAY BACK RIGHT PANEL | 75.C4
AF0053:22 | SC | SV2610-2 | WHT | 16 | 62.B7 | XT-9324:8 | 2 BAY BACK RIGHT PANEL | 62.B4
AF0053:24 | SC | SV2614-2 | WHT | 16 | 78.D7 | XT-9324:10 | 2 BAY BACK RIGHT PANEL | 78.D4
AF0061:04 | SC | FCE21309 | WHT | 20 | 55.C7 | XT-9329:10 | 2 BAY BACK RIGHT PANEL | 55.B5
AF0061:06 | SC | 006106 | WHT | 20 | 23.D6 | KA0701:A1 | 2 BAY BACK RIGHT PANEL | 23.D5
AF0061:20 | SC | FCE213010 | WHT | 20 | 55.C7 | XT-9329:11 | 2 BAY BACK RIGHT PANEL | 55.B5
AF0061:22 | SC | 006122 | WHT | 20 | 23.D6 | KA0701:A2 | 2 BAY BACK RIGHT PANEL | 23.D5
AF0063:02 | SC | FCE213014 | WHT | 20 | 55.D7 | XT-9329:17 | 2 BAY BACK RIGHT PANEL | 55.C5
AF0063:03 | SC | FCE213012 | WHT | 20 | 55.C7 | XT-9329:14 | 2 BAY BACK RIGHT PANEL | 55.C5
AF0063:34 | SC | FCE213013 | WHT | 20 | 55.D7 | XT-9329:16 | 2 BAY BACK RIGHT PANEL | 55.C5
AF0063:35 | SC | FCE213011 | WHT | 20 | 55.C7 | XT-9329:13 | 2 BAY BACK RIGHT PANEL | 55.C5
AF0067:02 | SC | 006200 | WHT | 16 | 59.B7 | KA0222:14 | 2 BAY BACK RIGHT PANEL | 59.B6
AF0067:04 | SC | SV2121-1 | WHT | 16 | 59.C7 | XT-9330:5 | 2 BAY BACK RIGHT PANEL | 59.C4
AF0067:06 | SC | 006706 | WHT | 20 | 70.B7 | KA0224:11 | 2 BAY BACK RIGHT PANEL | 70.B6
AF0067:08 | SC | SV1720-1 | WHT | 20 | 53.D7 | XT-9324:5 | 2 BAY BACK RIGHT PANEL | 53.D5
AF0067:18 | SC | SV2124-2 | WHT | 16 | 59.B7 | XT-9330:8 | 2 BAY BACK RIGHT PANEL | 59.C4
AF0067:20 | SC | SV2121-2 | WHT | 16 | 59.C7 | XT-9330:6 | 2 BAY BACK RIGHT PANEL | 59.C4
AF0067:24 | SC | SV1720-2 | WHT | 20 | 53.D7 | XT-9324:6 | 2 BAY BACK RIGHT PANEL | 53.D5
AF0076:02 | SC | 007602 | WHT | 20 | 59.A7 | KA0221:A1 | 2 BAY BACK RIGHT PANEL | 59.A6
AF0076:03 | SC | 007603 | WHT | 20 | 64.C7 | KA0220:A1 | 2 BAY BACK RIGHT PANEL | 64.C5
AF0076:04 | SC | 007604 | WHT | 20 | 59.B7 | KA0222:A1 | 2 BAY BACK RIGHT PANEL | 59.B6
AF0076:05 | SC | 007605 | WHT | 20 | 70.B7 | KA0224:A1 | 2 BAY BACK RIGHT PANEL | 70.B6
AF0076:06 | SC | 007606 | WHT | 20 | 71.B7 | KA0225:A1 | 2 BAY BACK RIGHT PANEL | 71.B6
AF0076:07 | SC | 007607 | WHT | 20 | 35.B7 | KA1020:A1 | 2 BAY BACK RIGHT PANEL | 35.B5
AF0076:11 | SC | UA1200J14 | WHT | 20 | 19.C7 | XT-9326:1 | 2 BAY BACK RIGHT PANEL | 19.C4
AF0076:14 | SC | 007614 | WHT | 20 | 121.B7 | KA076E:A1 | 2 BAY BACK RIGHT PANEL | 121.B5
AF0076:16 | SC | FCE21308 | WHT | 20 | 55.B7 | XT-9329:8 | 2 BAY BACK RIGHT PANEL | 55.B5
AF0076:18 | SC | 007618 | WHT | 20 | 59.A7 | KA0221:A2 | 2 BAY BACK RIGHT PANEL | 59.A6
AF0076:19 | SC | 007619 | WHT | 20 | 64.C7 | KA0220:A2 | 2 BAY BACK RIGHT PANEL | 64.C5
AF0076:20 | SC | 007620 | WHT | 20 | 59.B7 | KA0222:A2 | 2 BAY BACK RIGHT PANEL | 59.B6
AF0076:21 | SC | 007621 | WHT | 20 | 70.B7 | KA0224:A2 | 2 BAY BACK RIGHT PANEL | 70.B6
AF0076:22 | SC | 007622 | WHT | 20 | 71.B7 | KA0225:A2 | 2 BAY BACK RIGHT PANEL | 71.B6
AF0076:23 | SC | 007623 | WHT | 20 | 35.B7 | KA1020:A2 | 2 BAY BACK RIGHT PANEL | 35.B5
AF0076:30 | SC | 007630 | WHT | 20 | 121.B7 | KA076E:A2 | 2 BAY BACK RIGHT PANEL | 121.B5
IEG8240:00 | SC | IEG8240-G | GRN | 8 | 4.D2 | IEG8230:0 | 2 BAY BACK RIGHT PANEL | 4.D2
XT-9338:1 | SC | FCE2225-5 | WHT | 16 | 64.C4 | KA0220:11 | 2 BAY BACK RIGHT PANEL | 64.C5
XT-9350:11 | SC | YK7175-1 | WHT | 20 | 121.B4 | KA076E:11 | 2 BAY BACK RIGHT PANEL | 121.B5
XT-9350:12 | SC | YK7175-2 | WHT | 20 | 121.B4 | KA076E:14 | 2 BAY BACK RIGHT PANEL | 121.B5
XT-9370:1 | SC | SV6432-1 | WHT | 16 | 76.C4 | AF0092:13 | 2 BAY BACK RIGHT PANEL | 76.C7
XT-9370:2 | SC | SV6432-2 | WHT | 16 | 76.C4 | AF0092:29 | 2 BAY BACK RIGHT PANEL | 76.C7
XT-9370:3 | SC | SV6433-1 | WHT | 16 | 76.D4 | AF0092:14 | 2 BAY BACK RIGHT PANEL | 76.D7
XT-9370:4 | SC | SV6433-2 | WHT | 16 | 76.D4 | AF0092:30 | 2 BAY BACK RIGHT PANEL | 76.D7
XT-9370:5 | SC | SV6434-1 | WHT | 16 | 76.D4 | AF0092:15 | 2 BAY BACK RIGHT PANEL | 76.D7
XT-9370:6 | SC | SV6434-2 | WHT | 16 | 76.D4 | AF0092:31 | 2 BAY BACK RIGHT PANEL | 76.D7
XT-9370:7 | SC | SV6431-1 | WHT | 16 | 75.C4 | AF0092:01 | 2 BAY BACK RIGHT PANEL | 75.C7
XT-9370:8 | SC | SV6431-2 | WHT | 16 | 75.C4 | AF0092:17 | 2 BAY BACK RIGHT PANEL | 75.C7
XT-9381:13 | SC | HA1300-2 | WHT | 16 | 106.A4 | AF0094:00 | 2 BAY BACK RIGHT PANEL | 106.A7
XT-9381:14 | SC | HA1300-1 | WHT | 16 | 106.A4 | AF0094:16 | 2 BAY BACK RIGHT PANEL | 106.A7
XT-9381:16 | SC | SB6200-23 | WHT | 20 | 35.A4 | AF0087:37 | 2 BAY BACK RIGHT PANEL | 35.A7
XT-9381:17 | SC | SB6200-24 | WHT | 20 | 35.A4 | AF0087:05 | 2 BAY BACK RIGHT PANEL | 35.A7
XT-9381:19 | SC | HL6200-1 | WHT | 20 | 35.B4 | AF0093:15 | 2 BAY BACK RIGHT PANEL | 35.A7
XT-9381:20 | SC | HL6200-2 | WHT | 20 | 35.B4 | AF0093:31 | 2 BAY BACK RIGHT PANEL | 35.A7
AF0057:00 | W0570 | SM7632-1 | RED | 20 | 42.A7 | XT-9312:4 | 2 BAY BACK RIGHT PANEL | 42.A4
AF0057:16 | W0570 | SM7632-2 | BLK | 20 | 42.A7 | XT-9312:5 | 2 BAY BACK RIGHT PANEL | 42.A4
AF0057:48 | W0570 | SM7632-S | SH | 20 | 42.A7 | XT-9312:6 | 2 BAY BACK RIGHT PANEL | 42.A4
AF0057:02 | W0571 | SM7633-1 | RED | 20 | 42.A7 | XT-9312:1 | 2 BAY BACK RIGHT PANEL | 42.A4
AF0057:18 | W0571 | SM7633-2 | BLK | 20 | 42.A7 | XT-9312:2 | 2 BAY BACK RIGHT PANEL | 42.A4
AF0057:50 | W0571 | SM7633-S | SH | 20 | 42.A7 | XT-9312:3 | 2 BAY BACK RIGHT PANEL | 42.B4
AF0057:04 | W0572 | SM7634-1 | RED | 20 | 42.B7 | XT-9312:21 | 2 BAY BACK RIGHT PANEL | 42.B4
AF0057:20 | W0572 | SM7634-2 | BLK | 20 | 42.B7 | XT-9312:22 | 2 BAY BACK RIGHT PANEL | 42.B4
AF0057:52 | W0572 | SM7634-S | SH | 20 | 42.B7 | XT-9312:23 | 2 BAY BACK RIGHT PANEL | 42.B4
AF0057:06 | W0573 | SM7635-1 | RED | 20 | 42.B7 | XT-9312:28 | 2 BAY BACK RIGHT PANEL | 42.B4
AF0057:22 | W0573 | SM7635-2 | BLK | 20 | 42.B7 | XT-9312:29 | 2 BAY BACK RIGHT PANEL | 42.C4
AF0057:54 | W0573 | SM7635-S | SH | 20 | 42.B7 | XT-9312:30 | 2 BAY BACK RIGHT PANEL | 42.C4
AF0071:04 | W0710 | SE1260-1 | RED | 20 | 81.A7 | XT-9325A:1 | 2 BAY BACK RIGHT PANEL | 81.A5
AF0071:20 | W0710 | SE1260-2 | BLK | 20 | 81.A7 | XT-9325A:2 | 2 BAY BACK RIGHT PANEL | 81.A5
AF0071:52 | W0710 | SE1260-S1 | SH | 20 | 81.A7 | XT-9325A:3 | 2 BAY BACK RIGHT PANEL | 81.A5
XT-9336:4 | W0857 | FCE1440-3 | RED | 20 | 46.A5 | AF0085:14 | 2 BAY BACK RIGHT PANEL | 46.A7
XT-9336:5 | W0857 | FCE1440-4 | BLK | 20 | 46.A5 | AF0085:30 | 2 BAY BACK RIGHT PANEL | 46.A7
XT-9336:6 | W0857 | FCE1440-S2 | SH | 20 | 46.A5 | AF0085:62 | 2 BAY BACK RIGHT PANEL | 46.A7
XT-9336:7 | W0860 | FCE1440-5 | RED | 20 | 46.B5 | AF0086:00 | 2 BAY BACK RIGHT PANEL | 46.B7
XT-9336:8 | W0860 | FCE1440-6 | BLK | 20 | 46.B5 | AF0086:16 | 2 BAY BACK RIGHT PANEL | 46.B7
XT-9336:9 | W0860 | FCE1440-S3 | SH | 20 | 46.B5 | AF0086:48 | 2 BAY BACK RIGHT PANEL | 46.B7
XT-9380:4 | W0866 | FT2108-1 | RED | 20 | 61.C4 | AF0086:12 | 2 BAY BACK RIGHT PANEL | 61.C7
XT-9380:5 | W0866 | FT2108-2 | BLK | 20 | 61.C4 | AF0086:28 | 2 BAY BACK RIGHT PANEL | 61.C7
XT-9380:6 | W0866 | FT2108-S1 | SH | 20 | 61.C4 | AF0086:60 | 2 BAY BACK RIGHT PANEL | 61.C7
AU0070:L1 | WC0008 | AU0080L2 | ENET | CABLE | 3.A5 | AU0080:L2 | 2 BAY BACK RIGHT PANEL | 3.A4
XT-9335:4 | WC4191 | FCE1420-5 | RED | 20 | 45.B5 | AF0085:00 | 2 BAY BACK RIGHT PANEL | 45.B7
XT-9335:5 | WC4191 | FCE1420-6 | BLK | 20 | 45.B5 | AF0085:16 | 2 BAY BACK RIGHT PANEL | 45.B7
XT-9335:6 | WC4191 | FCE1420-S2 | SH | 20 | 45.B5 | AF0085:48 | 2 BAY BACK RIGHT PANEL | 45.B7
AF0066:04 | WC4681 | FCE21301 | RED | 20 | 55.A7 | XT-9329:1 | 2 BAY BACK RIGHT PANEL | 55.A5
AF0066:20 | WC4681 | FCE21302 | BLK | 20 | 55.A7 | XT-9329:2 | 2 BAY BACK RIGHT PANEL | 55.A5
AF0066:52 | WC4681 | FCE2130S1 | SH | 20 | 55.A7 | XT-9329:3 | 2 BAY BACK RIGHT PANEL | 55.A5
AF0074:00 | WC4682 | FCE21305 | RED | 20 | 55.B7 | XT-9329:4 | 2 BAY BACK RIGHT PANEL | 55.A5
AF0074:16 | WC4682 | FCE21306 | BLK | 20 | 55.B7 | XT-9329:5 | 2 BAY BACK RIGHT PANEL | 55.B5
AF0074:48 | WC4682 | FCE2130S2 | SH | 20 | 55.B7 | XT-9329:6 | 2 BAY BACK RIGHT PANEL | 55.B5
AF0053:12 | SC | 005312 | WHT | 20 | 35.C7 | PC0471:INP_A | 2 BAY LEFT WALL | 35.C5
AF0053:14 | SC | 005314 | WHT | 20 | 35.D7 | PC0471:INP_B | 2 BAY LEFT WALL | 35.C5
AF0053:30 | SC | 005330 | WHT | 20 | 35.D7 | PC0471:-PWR | 2 BAY LEFT WALL | 35.C5
AF0053:44 | SC | 005344 | WHT | 20 | 35.C7 | PC0471:+PWR | 2 BAY LEFT WALL | 35.C5
AF0061:02 | SC | 006102 | WHT | 20 | 45.B7 | KA0233:14 | 2 BAY LEFT WALL | 45.B6
AF0061:14 | SC | 006114 | WHT | 20 | 46.B7 | KA0234:14 | 2 BAY LEFT WALL | 46.B6
AF0062:02 | SC | 006202 | WHT | 20 | 121.A7 | KA0621:A1 | 2 BAY LEFT WALL | 121.A5
AF0062:04 | SC | 006204 | WHT | 20 | 121.B7 | KA0622:A1 | 2 BAY LEFT WALL | 121.B5
AF0062:18 | SC | 006218 | WHT | 20 | 121.A7 | KA0621:A2 | 2 BAY LEFT WALL | 121.A5
AF0062:20 | SC | 006220 | WHT | 20 | 121.B7 | KA0622:A2 | 2 BAY LEFT WALL | 121.B5
AF0076:00 | SC | 007600 | WHT | 20 | 55.B7 | KA0237:14 | 2 BAY LEFT WALL | 55.B5
AF0076:01 | SC | 007601 | WHT | 20 | 57.B7 | KA0237:24 | 2 BAY LEFT WALL | 57.B5
AF0076:10 | SC | KT014615 | WHT | 20 | 18.C7 | KT0146:15 | 2 BAY LEFT WALL | 18.C6
AF0076:12 | SC | 007612 | WHT | 20 | 19.C7 | XT0237:1 B2 | 2 BAY LEFT WALL | 19.C5
AF0076:13 | SC | KT0146B1 | WHT | 20 | 17.B2 | KT0146:B1 | 2 BAY LEFT WALL | 17.B2
AF0076:26 | SC | KA0231A2 | WHT | 20 | 18.C7 | KA0231:A2 | 2 BAY LEFT WALL | 18.C6
AF0076:29 | SC | KT0146A2 | WHT | 20 | 17.B2 | KT0146:A2 | 2 BAY LEFT WALL | 17.B2
FU0050:LI | SC | FU0210 | WHT | 14 | 10.B1 | XT0233:2 | 2 BAY LEFT WALL | 16.C5
FU0060:LI | SC | FU0210 | WHT | 14 | 9.C1 | XT0233:1 | 2 BAY LEFT WALL | 16.C5
FU0070:LI | SC | FU0210 | WHT | 14 | 9.B1 | XT0233:2 | 2 BAY LEFT WALL | 16.C5
XT0050:1 | SC | 0V | WHT | 14 | 10.B1 | XT0235:1 | 2 BAY LEFT WALL | 16.D5
XT0050:4 | SC | FU0054 | WHT | 16 | 64.C7 | KA0250:14 | 2 BAY LEFT WALL | 64.C6
XT0110:1 | SC | FU0136 | WHT | 14 | 23.A6 | XT0138:4 | 2 BAY LEFT WALL | 16.A4
XT0110:2 | SC | 0V | WHT | 14 | 23.A6 | XT0134:4 | 2 BAY LEFT WALL | 16.B4
XT0450:1 | SC | FU0136 | WHT | 14 | 22.A5 | XT0138:3 | 2 BAY LEFT WALL | 16.A4
XT0450:2 | SC | 0V | WHT | 16 | 22.A5 | XT0134:3 | 2 BAY LEFT WALL | 16.B4
XT-9334:7 | SC | FCE2140-7 | WHT | 20 | 57.B5 | KA0237:21 | 2 BAY LEFT WALL | 57.B5
XT-9335:7 | SC | FCE1420-7 | WHT | 20 | 45.B5 | KA0233:11 | 2 BAY LEFT WALL | 45.B6
XT-9336:10 | SC | FCE1440-7 | WHT | 20 | 46.B5 | KA0234:11 | 2 BAY LEFT WALL | 46.B6
XT-9350:1 | SC | XK7170-1 | WHT | 20 | 120.A4 | KA0822:A1 | 2 BAY LEFT WALL | 120.A5
XT-9350:10 | SC | YK7174-2 | WHT | 20 | 121.A4 | KA0621:14 | 2 BAY LEFT WALL | 121.A5
XT-9350:13 | SC | YK7176-1 | WHT | 20 | 121.B4 | KA0622:11 | 2 BAY LEFT WALL | 121.C5
XT-9350:14 | SC | YK7176-2 | WHT | 20 | 121.C4 | KA0622:14 | 2 BAY LEFT WALL | 121.C5
XT-9350:2 | SC | XK7170-2 | WHT | 20 | 120.A4 | KA0822:A2 | 2 BAY LEFT WALL | 120.A5
XT-9350:3 | SC | XK7171-1 | WHT | 20 | 120.A4 | KA0810:A1 | 2 BAY LEFT WALL | 120.A5
XT-9350:4 | SC | XK7171-2 | WHT | 20 | 120.B4 | KA0810:A2 | 2 BAY LEFT WALL | 120.A5
XT-9350:5 | SC | XK7172-1 | WHT | 20 | 120.B4 | KA0823:A1 | 2 BAY LEFT WALL | 120.B5
XT-9350:6 | SC | XK7172-2 | WHT | 20 | 120.B4 | KA0823:A2 | 2 BAY LEFT WALL | 120.B5
XT-9350:7 | SC | XK7173-1 | WHT | 20 | 120.C4 | KA0811:A1 | 2 BAY LEFT WALL | 120.C5
XT-9350:8 | SC | XK7173-2 | WHT | 20 | 120.C4 | KA0811:A2 | 2 BAY LEFT WALL | 120.C5
XT-9350:9 | SC | YK7174-1 | WHT | 20 | 121.A4 | KA0621:11 | 2 BAY LEFT WALL | 121.A5
XT-9355:1 | SC | UF1300-DI2 | WHT | 20 | 43.A5 | KA0248:24 | 2 BAY LEFT WALL | 91.D6
XT-9381:1 | SC | FU0210 | WHT | 16 | 61.C4 | XT0233:3 | 2 BAY LEFT WALL | 16.C5
XT-9381:10 | SC | SV2220-1 | WHT | 16 | 70.B4 | KA0240:11 | 2 BAY LEFT WALL | 70.B5
XT-9381:2 | SC | 0V | WHT | 16 | 61.C4 | XT0235:3 | 2 BAY LEFT WALL | 16.D5
XT-9381:4 | SC | FU0210 | WHT | 16 | 68.C4 | XT0233:2 | 2 BAY LEFT WALL | 16.C5
XT-9381:7 | SC | FU0210 | WHT | 16 | 67.C4 | XT0233:2 | 2 BAY LEFT WALL | 16.C5
AF0068:00 | W0680 | 006800 | RED | 20 | 48.B7 | UAI9201-1:+7 | 2 BAY LEFT WALL | 48.B5
AF0068:01 | W0680 | 006801 | BLK | 20 | 48.B7 | UAI9201-1:-8 | 2 BAY LEFT WALL | 48.B5
AF0068:48 | W0680 | 006848 | SH | 20 | 48.B7 | FLOATING | 2 BAY LEFT WALL | 48.B6
AF0068:02 | W0681 | 006802 | RED | 20 | 48.C7 | UAI9201-3:+7 | 2 BAY LEFT WALL | 48.C5
AF0068:03 | W0681 | 006803 | BLK | 20 | 48.C7 | UAI9201-3:-8 | 2 BAY LEFT WALL | 48.C5
AF0068:50 | W0681 | 006850 | SH | 20 | 48.C7 | FLOATING | 2 BAY LEFT WALL | 48.C6
AF0068:04 | W0682 | 006804 | RED | 20 | 48.D7 | UAI9201-5:+7 | 2 BAY LEFT WALL | 48.D5
AF0068:05 | W0682 | 006805 | BLK | 20 | 48.D7 | UAI9201-5:-8 | 2 BAY LEFT WALL | 48.D5
AF0068:52 | W0682 | 006852 | SH | 20 | 48.D7 | FLOATING | 2 BAY LEFT WALL | 48.D6
AF0068:06 | W0683 | 006806 | RED | 20 | 49.B7 | UAI9201-7:+7 | 2 BAY LEFT WALL | 49.B5
AF0068:07 | W0683 | 006807 | BLK | 20 | 49.B7 | UAI9201-7:-8 | 2 BAY LEFT WALL | 49.B5
AF0068:54 | W0683 | 006854 | SH | 20 | 49.B7 | FW0751:1 | 2 BAY LEFT WALL | 49.B6
AF0068:08 | W0684 | 006808 | RED | 20 | 49.B7 | UAI9201-9:+7 | 2 BAY LEFT WALL | 49.B5
AF0068:09 | W0684 | 006809 | BLK | 20 | 49.B7 | UAI9201-9:-8 | 2 BAY LEFT WALL | 49.B5
AF0068:56 | W0684 | 006856 | SH | 20 | 49.B7 | FW0753:1 | 2 BAY LEFT WALL | 49.C6
AF0068:10 | W0685 | 006810 | RED | 20 | 49.C7 | UAI9202-1:+7 | 2 BAY LEFT WALL | 49.C5
AF0068:11 | W0685 | 006811 | BLK | 20 | 49.C7 | UAI9202-1:-8 | 2 BAY LEFT WALL | 49.C5
AF0068:58 | W0685 | 006858 | SH | 20 | 49.C7 | FW0755:1 | 2 BAY LEFT WALL | 49.D6
AF0068:45 | W0686 | 006845 | RED | 20 | 48.A7 | UAI9206-1:-7 | 2 BAY LEFT WALL | 48.A5
AF0068:29 | W0686 | 006829 | WHT | 20 | 48.A7 | UAI9206-1:-5 | 2 BAY LEFT WALL | 48.A5
AF0068:28 | W0686 | 006828 | BLK | 20 | 48.A7 | UAI9206-1:+6 | 2 BAY LEFT WALL | 48.A5
AF0068:60 | W0686 | 006860 | SH | 20 | 48.A7 | FLOATING | 2 BAY LEFT WALL | 48.A6
AF0073:00 | W0730 | 007300 | RED | 20 | 48.B7 | UAI9201-2:+7 | 2 BAY LEFT WALL | 48.B5
AF0073:01 | W0730 | 007301 | BLK | 20 | 48.B7 | UAI9201-2:-8 | 2 BAY LEFT WALL | 48.B5
AF0073:48 | W0730 | 007348 | SH | 20 | 48.B7 | FLOATING | 2 BAY LEFT WALL | 48.B6
AF0073:02 | W0731 | 007302 | RED | 20 | 48.C7 | UAI9201-4:+7 | 2 BAY LEFT WALL | 48.C5
AF0073:03 | W0731 | 007303 | BLK | 20 | 48.C7 | UAI9201-4:-8 | 2 BAY LEFT WALL | 48.C5
AF0073:50 | W0731 | 007350 | SH | 20 | 48.C7 | FLOATING | 2 BAY LEFT WALL | 48.C6
AF0073:04 | W0732 | 007304 | RED | 20 | 48.D7 | UAI9201-6:+7 | 2 BAY LEFT WALL | 48.D5
AF0073:05 | W0732 | 007305 | BLK | 20 | 48.D7 | UAI9201-6:-8 | 2 BAY LEFT WALL | 48.D5
AF0073:52 | W0732 | 007352 | SH | 20 | 48.D7 | FLOATING | 2 BAY LEFT WALL | 48.D6
AF0073:06 | W0733 | 007306 | RED | 20 | 49.B7 | UAI9201-8:+7 | 2 BAY LEFT WALL | 49.B5
AF0073:07 | W0733 | 007307 | BLK | 20 | 49.B7 | UAI9201-8:-8 | 2 BAY LEFT WALL | 49.B5
AF0073:54 | W0733 | 007354 | SH | 20 | 49.B7 | FW0752:1 | 2 BAY LEFT WALL | 49.B6
AF0073:08 | W0734 | 007308 | RED | 20 | 49.C7 | UAI9201-10:+7 | 2 BAY LEFT WALL | 49.C5
AF0073:09 | W0734 | 007309 | BLK | 20 | 49.C7 | UAI9201-10:-8 | 2 BAY LEFT WALL | 49.C5
AF0073:56 | W0734 | 007356 | SH | 20 | 49.C7 | FW0754:1 | 2 BAY LEFT WALL | 49.C6
AF0073:10 | W0735 | 007310 | RED | 20 | 49.D7 | UAI9202-2:+7 | 2 BAY LEFT WALL | 49.D5
AF0073:11 | W0735 | 007311 | BLK | 20 | 49.D7 | UAI9202-2:-8 | 2 BAY LEFT WALL | 49.D5
AF0073:58 | W0735 | 007358 | SH | 20 | 49.D7 | FW0756:1 | 2 BAY LEFT WALL | 49.D6
AF0073:45 | W0736 | 007345 | RED | 20 | 54.D7 | UAI9205-1:-7 | 2 BAY LEFT WALL | 54.D5
AF0073:29 | W0736 | 007329 | WHT | 20 | 54.D7 | UAI9205-1:-5 | 2 BAY LEFT WALL | 54.D5
AF0073:28 | W0736 | 007328 | BLK | 20 | 54.D7 | UAI9205-1:+6 | 2 BAY LEFT WALL | 54.D5
AF0073:60 | W0736 | 007360 | SH | 20 | 54.D7 | FW0889:1 | 2 BAY LEFT WALL | 54.D6
AF0074:12 | W0746 | 007412 | RED | 20 | 78.A7 | UAI9204-1:+8 | 2 BAY LEFT WALL | 78.A5
AF0074:28 | W0746 | 007428 | BLK | 20 | 78.A7 | UAI9204-1:-7 | 2 BAY LEFT WALL | 78.A5
AF0074:60 | W0746 | 007460 | SH | 20 | 78.A7 | FW1207:1 | 2 BAY LEFT WALL | 78.A6
AF0074:14 | W0747 | 007414 | RED | 20 | 119.A7 | UAI9203-1:+8 | 2 BAY LEFT WALL | 119.A5
AF0074:30 | W0747 | 007430 | BLK | 20 | 119.A7 | UAI9203-1:-7 | 2 BAY LEFT WALL | 119.A5
AF0074:62 | W0747 | 007462 | SH | 20 | 119.A7 | FW6:1 | 2 BAY LEFT WALL | 119.A6
FU0111:LD | SC | FU0111 | WHT | 14 | 23.A5 | UV0610:+DC | ORBIT 60^DOOR PANEL | 23.B1
FU0112:LD | SC | FU0112 | WHT | 14 | 23.A5 | UV0611:+DC | ORBIT 60^DOOR PANEL | 23.C1
XT0110:2 | SC | 0V | WHT | 14 | 23.A6 | UV0610:COM | ORBIT 60^DOOR PANEL | 23.B1
XT0110:3 | SC | 0V | WHT | 14 | 23.A6 | UV0611:COM | ORBIT 60^DOOR PANEL | 23.C1
SolarTools ver. 24.0.84.26264 (Jun 3, 2025)
Report date: 7/10/2025 2:56 PM

## ASSEMBLY CONSOLE
ASSEMBLY CONSOLE
Project # | G9440
Project Name | NOC AL SHAHEEN T130
Revision | A.5
Controls DE | G. Colby
Phone:
Controls ME | R. Duran
Phone:
From | [5 empty] | To
Device ID | Cable (W) Conductor (SC) Jumper Clip (JC) | Wire No. | Wire ID | Gauge/Size | Page/Zone | Device ID | Location | Page/Zone
EL0273:B1 | SC | ZS0273 | WHT | 14 | 11.B4 | ZS0273:2 | ASSEMBLY CONSOLE | 11.B4
EL0274:B1 | SC | ZS0274 | WHT | 14 | 11.C4 | ZS0274:2 | ASSEMBLY CONSOLE | 11.C4
ZS0274:1 | SC | FU0274 | WHT | 14 | 11.C4 | FU0274:LD | 2 BAY LEFT WALL | 11.C3
HA0273:(+) | WC5540 | HA0273P | BLK | 16 | 13.A1 | AF0202:23 | ASSEMBLY^CONTROL PANEL | 13.A3
HA0273:(-) | WC5540 | HA0273N | WHT | 16 | 13.A1 | AF0202:55 | ASSEMBLY^CONTROL PANEL | 13.A3
EL0273:W1 | SC | 0V1 | WHT | 14 | 11.B4 | XT0562:1 | PWR,DISTRIBUTION RAIL^LEFT DOOR | 11.B2
EL0274:W1 | SC | 0V1 | WHT | 14 | 11.C4 | XT0562:3 | PWR,DISTRIBUTION RAIL^LEFT DOOR | 11.B2
ZS0273:1 | SC | FU0273 | WHT | 14 | 11.B4 | FU0273:LD | PWR,DISTRIBUTION RAIL^LEFT DOOR | 11.B3
SolarTools ver. 24.0.84.26264 (Jun 3, 2025)
Report date: 7/10/2025 2:56 PM

## ASSEMBLY^CONTROL PANEL
ASSEMBLY^CONTROL PANEL
Project # | G9440
Project Name | NOC AL SHAHEEN T130
Revision | A.5
Controls DE | G. Colby
Phone:
Controls ME | R. Duran
Phone:
From | [5 empty] | To
Device ID | Cable (W) Conductor (SC) Jumper Clip (JC) | Wire No. | Wire ID | Gauge/Size | Page/Zone | Device ID | Location | Page/Zone
AF0201:00 | SC | TCP13NO | WHT | 20 | 14.A3 | SH0400:NO | ASSEMBLY^CONTROL PANEL | 14.A1
AF0201:01 | SC | TCP14NO | WHT | 20 | 14.A3 | SH0401:NO | ASSEMBLY^CONTROL PANEL | 14.A1
AF0201:02 | SC | TCP15NO | WHT | 20 | 14.B3 | SH0409:NO | ASSEMBLY^CONTROL PANEL | 14.B1
AF0201:03 | SC | TCP16NO | WHT | 20 | 14.B3 | SH0410:NO | ASSEMBLY^CONTROL PANEL | 14.B1
AF0201:04 | SC | TCP17A2 | WHT | 20 | 14.C3 | SA0400:14 | ASSEMBLY^CONTROL PANEL | 14.C1
AF0201:05 | SC | TCP17B2 | WHT | 20 | 14.C3 | SA0400:22 | ASSEMBLY^CONTROL PANEL | 14.C1
AF0201:08 | SC | TCP23NC | WHT | 20 | 14.D3 | SB0401:NC | ASSEMBLY^CONTROL PANEL | 14.D1
AF0201:09 | SC | TCP24NO | WHT | 20 | 14.D3 | SB0402:NO | ASSEMBLY^CONTROL PANEL | 14.D1
AF0201:10 | SC | TCP25NO | WHT | 20 | 14.A7 | SB0403:NO | ASSEMBLY^CONTROL PANEL | 14.A5
AF0201:11 | SC | TCP26NO | WHT | 20 | 14.A7 | SB0404:NO | ASSEMBLY^CONTROL PANEL | 14.A5
AF0201:12 | SC | TCP29NO | WHT | 20 | 13.D3 | SB0405:NO | ASSEMBLY^CONTROL PANEL | 13.D1
AF0201:13 | SC | TCP28NC | WHT | 20 | 13.C3 | SB0406:NC | ASSEMBLY^CONTROL PANEL | 13.C1
AF0201:14 | SC | TCP31NO | WHT | 20 | 13.A6 | SB0407:NO | ASSEMBLY^CONTROL PANEL | 13.A5
AF0201:15 | SC | TCP32NO | WHT | 20 | 13.A6 | SB0408:NO | ASSEMBLY^CONTROL PANEL | 13.A5
AF0201:16 | SC | TCP30NO | WHT | 20 | 13.D3 | SH0408:NO | ASSEMBLY^CONTROL PANEL | 13.D1
AF0201:17 | SC | TCP19NO | WHT | 20 | 13.A3 | SH0404:NO | ASSEMBLY^CONTROL PANEL | 13.A1
AF0201:18 | SC | TCP20NO | WHT | 20 | 13.B3 | SH0405:NO | ASSEMBLY^CONTROL PANEL | 13.B1
AF0201:19 | SC | TCP21NO | WHT | 20 | 13.B3 | SH0411:NO | ASSEMBLY^CONTROL PANEL | 13.B1
AF0201:20 | SC | TCP22NO | WHT | 20 | 13.C3 | SH0412:NO | ASSEMBLY^CONTROL PANEL | 13.C1
AF0201:32 | SC | TCP13C | WHT | 20 | 14.A3 | SH0400:C | ASSEMBLY^CONTROL PANEL | 14.A1
AF0201:33 | SC | TCP14C | WHT | 20 | 14.A3 | SH0401:C | ASSEMBLY^CONTROL PANEL | 14.A1
AF0201:34 | SC | TCP15C | WHT | 20 | 14.B3 | SH0409:C | ASSEMBLY^CONTROL PANEL | 14.B1
AF0201:35 | SC | TCP16C | WHT | 20 | 14.B3 | SH0410:C | ASSEMBLY^CONTROL PANEL | 14.B1
AF0201:36 | SC | TCP17A1 | WHT | 20 | 14.C3 | SA0400:13 | ASSEMBLY^CONTROL PANEL | 14.C1
AF0201:37 | SC | TCP17B1 | WHT | 20 | 14.C3 | SA0400:21 | ASSEMBLY^CONTROL PANEL | 14.C1
AF0201:40 | SC | TCP23C | WHT | 20 | 14.D3 | SB0401:C | ASSEMBLY^CONTROL PANEL | 14.D1
AF0201:41 | SC | TCP24C | WHT | 20 | 14.D3 | SB0402:C | ASSEMBLY^CONTROL PANEL | 14.D1
AF0201:42 | SC | TCP25C | WHT | 20 | 14.A7 | SB0403:C | ASSEMBLY^CONTROL PANEL | 14.A5
AF0201:43 | SC | TCP26C | WHT | 20 | 14.A7 | SB0404:C | ASSEMBLY^CONTROL PANEL | 14.A5
AF0201:44 | SC | TCP29C | WHT | 20 | 13.D3 | SB0405:C | ASSEMBLY^CONTROL PANEL | 13.D1
AF0201:45 | SC | TCP28C | WHT | 20 | 13.C3 | SB0406:C | ASSEMBLY^CONTROL PANEL | 13.C1
AF0201:46 | SC | TCP31C | WHT | 20 | 13.A6 | SB0407:C | ASSEMBLY^CONTROL PANEL | 13.A5
AF0201:47 | SC | TCP32C | WHT | 20 | 13.A6 | SB0408:C | ASSEMBLY^CONTROL PANEL | 13.A5
AF0201:48 | SC | TCP30C | WHT | 20 | 13.D3 | SH0408:C | ASSEMBLY^CONTROL PANEL | 13.D1
AF0201:49 | SC | TCP19C | WHT | 20 | 13.A3 | SH0404:C | ASSEMBLY^CONTROL PANEL | 13.A1
AF0201:50 | SC | TCP20C | WHT | 20 | 13.B3 | SH0405:C | ASSEMBLY^CONTROL PANEL | 13.B1
AF0201:51 | SC | TCP21C | WHT | 20 | 13.B3 | SH0411:C | ASSEMBLY^CONTROL PANEL | 13.B1
AF0201:52 | SC | TCP22C | WHT | 20 | 13.C3 | SH0412:C | ASSEMBLY^CONTROL PANEL | 13.C1
AF0201:COM | SC | AU0200N | WHT | 16 | 11.A4 | AU0200:COM | ASSEMBLY^CONTROL PANEL | 11.A3
AF0201:J | SC | * |  |  | 11.A4 | AF0202:P | ASSEMBLY^CONTROL PANEL | 11.A5
AF0201:P | SC | * |  |  | 11.A4 | AU0200:J | ASSEMBLY^CONTROL PANEL | 11.A3
AF0201:SHLD | SC | AF0201V+ | WHT | 20 | 11.B7 | AF0201:V+ | ASSEMBLY^CONTROL PANEL | 11.B7
AF0201:V+ | SC | AU0200P | WHT | 16 | 11.A4 | AU0200:V+ | ASSEMBLY^CONTROL PANEL | 11.A3
AF0202:00 | SC | TCP01AP | WHT | 20 | 12.A3 | HL0400:A+ | ASSEMBLY^CONTROL PANEL | 12.A1
AF0202:01 | SC | TCP02AP | WHT | 20 | 12.A3 | HL0401:A+ | ASSEMBLY^CONTROL PANEL | 12.A1
AF0202:02 | SC | TCP03AP | WHT | 20 | 12.B3 | HL0402:A+ | ASSEMBLY^CONTROL PANEL | 12.B1
AF0202:03 | SC | TCP04AP | WHT | 20 | 12.B3 | HL0403:A+ | ASSEMBLY^CONTROL PANEL | 12.B1
AF0202:04 | SC | TCP05AP | WHT | 20 | 12.C3 | HL0404:A+ | ASSEMBLY^CONTROL PANEL | 12.C1
AF0202:05 | SC | TCP06AP | WHT | 20 | 12.C3 | HL0405:A+ | ASSEMBLY^CONTROL PANEL | 12.C1
AF0202:06 | SC | TCP06BP | WHT | 20 | 12.D3 | HL0405:B+ | ASSEMBLY^CONTROL PANEL | 12.D1
AF0202:08 | SC | TCP07AP | WHT | 20 | 12.D3 | HL0406:A+ | ASSEMBLY^CONTROL PANEL | 12.D1
AF0202:09 | SC | TCP08AP | WHT | 20 | 12.A7 | HL0407:A+ | ASSEMBLY^CONTROL PANEL | 12.A5
AF0202:10 | SC | TCP09AP | WHT | 20 | 12.A7 | HL0408:A+ | ASSEMBLY^CONTROL PANEL | 12.A5
AF0202:11 | SC | TCP10AP | WHT | 20 | 12.B7 | HL0409:A+ | ASSEMBLY^CONTROL PANEL | 12.B5
AF0202:12 | SC | TCP11AP | WHT | 20 | 12.B7 | HL0411:A+ | ASSEMBLY^CONTROL PANEL | 12.B5
AF0202:13 | SC | TCP15AP | WHT | 20 | 12.C7 | SH0409:A+ | ASSEMBLY^CONTROL PANEL | 12.C5
AF0202:14 | SC | TCP15BP | WHT | 20 | 12.C7 | SH0409:B+ | ASSEMBLY^CONTROL PANEL | 12.C5
AF0202:15 | SC | TCP16AP | WHT | 20 | 12.D7 | SH0410:A+ | ASSEMBLY^CONTROL PANEL | 12.D5
AF0202:16 | SC | TCP16BP | WHT | 20 | 12.D7 | SH0410:B+ | ASSEMBLY^CONTROL PANEL | 12.D5
AF0202:17 | SC | TCP19AP | WHT | 20 | 13.B6 | SH0404:A+ | ASSEMBLY^CONTROL PANEL | 13.B5
AF0202:18 | SC | TCP20AP | WHT | 20 | 13.B6 | SH0405:A+ | ASSEMBLY^CONTROL PANEL | 13.B5
AF0202:19 | SC | TCP21AP | WHT | 20 | 13.C6 | SH0411:A+ | ASSEMBLY^CONTROL PANEL | 13.C5
AF0202:20 | SC | TCP22AP | WHT | 20 | 13.C6 | SH0412:A+ | ASSEMBLY^CONTROL PANEL | 13.C5
AF0202:21 | SC | TCP30AP | WHT | 20 | 13.D6 | SH0408:A+ | ASSEMBLY^CONTROL PANEL | 13.D5
AF0202:22 | SC | TCP30BP | WHT | 20 | 13.D6 | SH0408:B+ | ASSEMBLY^CONTROL PANEL | 13.D5
AF0202:32 | SC | TCP01A | WHT | 20 | 12.A3 | HL0400:A | ASSEMBLY^CONTROL PANEL | 12.A1
AF0202:33 | SC | TCP02A | WHT | 20 | 12.A3 | HL0401:A | ASSEMBLY^CONTROL PANEL | 12.A1
AF0202:34 | SC | TCP03A | WHT | 20 | 12.B3 | HL0402:A | ASSEMBLY^CONTROL PANEL | 12.B1
AF0202:35 | SC | TCP04A | WHT | 20 | 12.B3 | HL0403:A | ASSEMBLY^CONTROL PANEL | 12.B1
AF0202:36 | SC | TCP05A | WHT | 20 | 12.C3 | HL0404:A | ASSEMBLY^CONTROL PANEL | 12.C1
AF0202:37 | SC | TCP06A | WHT | 20 | 12.C3 | HL0405:A | ASSEMBLY^CONTROL PANEL | 12.C1
AF0202:38 | SC | TCP06B | WHT | 20 | 12.D3 | HL0405:B | ASSEMBLY^CONTROL PANEL | 12.D1
AF0202:40 | SC | TCP07A | WHT | 20 | 12.D3 | HL0406:A | ASSEMBLY^CONTROL PANEL | 12.D1
AF0202:41 | SC | TCP08A | WHT | 20 | 12.A7 | HL0407:A | ASSEMBLY^CONTROL PANEL | 12.A5
AF0202:42 | SC | TCP09A | WHT | 20 | 12.A7 | HL0408:A | ASSEMBLY^CONTROL PANEL | 12.A5
AF0202:43 | SC | TCP10A | WHT | 20 | 12.B7 | HL0409:A | ASSEMBLY^CONTROL PANEL | 12.B5
AF0202:44 | SC | TCP11A | WHT | 20 | 12.B7 | HL0411:A | ASSEMBLY^CONTROL PANEL | 12.B5
AF0202:45 | SC | TCP15A | WHT | 20 | 12.C7 | SH0409:A | ASSEMBLY^CONTROL PANEL | 12.C5
AF0202:46 | SC | TCP15B | WHT | 20 | 12.C7 | SH0409:B | ASSEMBLY^CONTROL PANEL | 12.C5
AF0202:47 | SC | TCP16A | WHT | 20 | 12.D7 | SH0410:A | ASSEMBLY^CONTROL PANEL | 12.D5
AF0202:48 | SC | TCP16B | WHT | 20 | 12.D7 | SH0410:B | ASSEMBLY^CONTROL PANEL | 12.D5
AF0202:49 | SC | TCP19A | WHT | 20 | 13.B6 | SH0404:A | ASSEMBLY^CONTROL PANEL | 13.B5
AF0202:50 | SC | TCP20A | WHT | 20 | 13.B6 | SH0405:A | ASSEMBLY^CONTROL PANEL | 13.B5
AF0202:51 | SC | TCP21A | WHT | 20 | 13.C6 | SH0411:A | ASSEMBLY^CONTROL PANEL | 13.C5
AF0202:52 | SC | TCP22A | WHT | 20 | 13.C6 | SH0412:A | ASSEMBLY^CONTROL PANEL | 13.C5
AF0202:53 | SC | TCP30A | WHT | 20 | 13.D6 | SH0408:A | ASSEMBLY^CONTROL PANEL | 13.D5
AF0202:54 | SC | TCP30B | WHT | 20 | 13.D6 | SH0408:B | ASSEMBLY^CONTROL PANEL | 13.D5
AF0202:COM-L | SC | AF0202COM-L | WHT | 20 | 11.B7 | AF0202:SHLD | ASSEMBLY^CONTROL PANEL | 11.B7
HL0400:A | SC | TCP01A | WHT | 20 | 12.A1 | HL0400:B | ASSEMBLY^CONTROL PANEL | 12.A1
HL0400:A+ | SC | TCP01AP | WHT | 20 | 12.A1 | HL0400:B+ | ASSEMBLY^CONTROL PANEL | 12.A1
HL0401:A | SC | TCP02A | WHT | 20 | 12.A1 | HL0401:B | ASSEMBLY^CONTROL PANEL | 12.A1
HL0401:A+ | SC | TCP02AP | WHT | 20 | 12.A1 | HL0401:B+ | ASSEMBLY^CONTROL PANEL | 12.A1
HL0402:A | SC | TCP03A | WHT | 20 | 12.B1 | HL0402:B | ASSEMBLY^CONTROL PANEL | 12.B1
HL0402:A+ | SC | TCP03AP | WHT | 20 | 12.B1 | HL0402:B+ | ASSEMBLY^CONTROL PANEL | 12.B1
HL0403:A | SC | TCP04A | WHT | 20 | 12.B1 | HL0403:B | ASSEMBLY^CONTROL PANEL | 12.B1
HL0403:A+ | SC | TCP04AP | WHT | 20 | 12.B1 | HL0403:B+ | ASSEMBLY^CONTROL PANEL | 12.B1
HL0404:A | SC | TCP05A | WHT | 20 | 12.C1 | HL0404:B | ASSEMBLY^CONTROL PANEL | 12.C1
HL0404:A+ | SC | TCP05AP | WHT | 20 | 12.C1 | HL0404:B+ | ASSEMBLY^CONTROL PANEL | 12.C1
HL0406:A | SC | TCP07A | WHT | 20 | 12.D1 | HL0406:B | ASSEMBLY^CONTROL PANEL | 12.D1
HL0406:A+ | SC | TCP07AP | WHT | 20 | 12.D1 | HL0406:B+ | ASSEMBLY^CONTROL PANEL | 12.D1
HL0407:A | SC | TCP08A | WHT | 20 | 12.A5 | HL0407:B | ASSEMBLY^CONTROL PANEL | 12.A5
HL0407:A+ | SC | TCP08AP | WHT | 20 | 12.A5 | HL0407:B+ | ASSEMBLY^CONTROL PANEL | 12.A5
HL0408:A | SC | TCP09A | WHT | 20 | 12.A5 | HL0408:B | ASSEMBLY^CONTROL PANEL | 12.A5
HL0408:A+ | SC | TCP09AP | WHT | 20 | 12.A5 | HL0408:B+ | ASSEMBLY^CONTROL PANEL | 12.A5
HL0409:A | SC | TCP10A | WHT | 20 | 12.B5 | HL0409:B | ASSEMBLY^CONTROL PANEL | 12.B5
HL0409:A+ | SC | TCP10AP | WHT | 20 | 12.B5 | HL0409:B+ | ASSEMBLY^CONTROL PANEL | 12.B5
HL0410:A | SC | 0V | WHT | 20 | 14.B5 | HL0410:B | ASSEMBLY^CONTROL PANEL | 14.B5
HL0410:A+ | SC | TCP12AP | WHT | 20 | 14.B5 | XT0564:1 B1 | ASSEMBLY^CONTROL PANEL | 14.B5
HL0410:A+ | SC | TCP12AP | WHT | 20 | 14.B5 | HL0410:B+ | ASSEMBLY^CONTROL PANEL | 14.B5
HL0411:A | SC | TCP11A | WHT | 20 | 12.B5 | HL0411:B | ASSEMBLY^CONTROL PANEL | 12.B5
HL0411:A+ | SC | TCP11AP | WHT | 20 | 12.B5 | HL0411:B+ | ASSEMBLY^CONTROL PANEL | 12.B5
SB0404:NO | SC | TCP26NO | WHT | 20 | 14.A5 | XT0564:1 T1 | ASSEMBLY^CONTROL PANEL | 14.B5
SH0400:A | SC | 0V1 | WHT | 20 | 14.B5 | SH0401:A | ASSEMBLY^CONTROL PANEL | 14.C5
SH0400:A | SC | 0V1 | WHT | 20 | 14.B5 | SH0400:B | ASSEMBLY^CONTROL PANEL | 14.B5
SH0400:A+ | SC | TCP13AP | WHT | 20 | 14.B5 | XT0564:2 B1 | ASSEMBLY^CONTROL PANEL | 14.B5
SH0400:B+ | SC | TCP13BP | WHT | 20 | 14.B5 | XT0564:3 B1 | ASSEMBLY^CONTROL PANEL | 14.B5
SH0401:A | SC | 0V1 | WHT | 20 | 14.C5 | SH0401:B | ASSEMBLY^CONTROL PANEL | 14.C5
SH0401:A+ | SC | TCP14AP | WHT | 20 | 14.C5 | XT0564:5 B1 | ASSEMBLY^CONTROL PANEL | 14.C5
SH0401:B+ | SC | TCP14BP | WHT | 20 | 14.C5 | XT0564:4 B1 | ASSEMBLY^CONTROL PANEL | 14.C5
SH0404:A | SC | TCP19A | WHT | 20 | 13.B5 | SH0404:B | ASSEMBLY^CONTROL PANEL | 13.B5
SH0404:A+ | SC | TCP19AP | WHT | 20 | 13.B5 | SH0404:B+ | ASSEMBLY^CONTROL PANEL | 13.B5
SH0405:A | SC | TCP20A | WHT | 20 | 13.B5 | SH0405:B | ASSEMBLY^CONTROL PANEL | 13.B5
SH0405:A+ | SC | TCP20AP | WHT | 20 | 13.B5 | SH0405:B+ | ASSEMBLY^CONTROL PANEL | 13.B5
SH0411:A | SC | TCP21A | WHT | 20 | 13.C5 | SH0411:B | ASSEMBLY^CONTROL PANEL | 13.C5
SH0411:A+ | SC | TCP21AP | WHT | 20 | 13.C5 | SH0411:B+ | ASSEMBLY^CONTROL PANEL | 13.C5
SH0412:A | SC | TCP22A | WHT | 20 | 13.C5 | SH0412:B | ASSEMBLY^CONTROL PANEL | 13.C5
SH0412:A+ | SC | TCP22AP | WHT | 20 | 13.C5 | SH0412:B+ | ASSEMBLY^CONTROL PANEL | 13.C5
XT0564:1 T2 | SC | TCP26NO | WHT | 20 | 14.B5 | XT0564:2 T2 | ASSEMBLY^CONTROL PANEL | 14.B5
XT0564:2 T1 | SC | TCP26NO | WHT | 20 | 14.B5 | XT0564:3 T1 | ASSEMBLY^CONTROL PANEL | 14.B5
XT0564:3 T2 | SC | TCP26NO | WHT | 20 | 14.B5 | XT0564:4 T2 | ASSEMBLY^CONTROL PANEL | 14.C5
XT0564:4 T1 | SC | TCP26NO | WHT | 20 | 14.C5 | XT0564:5 T1 | ASSEMBLY^CONTROL PANEL | 14.C5
AU0200:L1 | WC0122 | AT0220P2 | ENET | CABLE | 3.C2 | AT0220:P2 | 1 BAY LEFT WALL | 3.B4
SB0400:21 | SC | TCP18B1 | WHT | 20 | 14.D5 | AF0081:37 | 2 BAY BACK RIGHT PANEL | 14.D6
SB0400:22 | SC | TCP18B2 | WHT | 20 | 14.D5 | AF0081:05 | 2 BAY BACK RIGHT PANEL | 14.D6
GR0200: | SC | IEG8210-1 | GRN | 14 | 11.A3 | IEG8210:1 | 2 BAY LEFT WALL | 11.A2
AF0202:23 | WC5540 | HA0273P | BLK | 16 | 13.A3 | HA0273:(+) | ASSEMBLY CONSOLE | 13.A1
AF0202:55 | WC5540 | HA0273N | WHT | 16 | 13.A3 | HA0273:(-) | ASSEMBLY CONSOLE | 13.A1
AF0202:COM | SC | 0V1 | WHT | 14 | 11.A5 | XT0562:1 | PWR,DISTRIBUTION RAIL^LEFT DOOR | 11.B2
AF0202:V+ | SC | FU0201 | WHT | 14 | 11.A5 | FU0201:LD | PWR,DISTRIBUTION RAIL^LEFT DOOR | 11.B3
AU0200:COM | SC | 0V1 | WHT | 14 | 11.A3 | XT0562:1 | PWR,DISTRIBUTION RAIL^LEFT DOOR | 11.B2
AU0200:V+ | SC | FU0200 | WHT | 14 | 11.A3 | FU0200:LD | PWR,DISTRIBUTION RAIL^LEFT DOOR | 11.A3
HL0410:A | SC | 0V | WHT | 20 | 14.B5 | XT0563:4 | PWR,DISTRIBUTION RAIL^LEFT DOOR | 14.B6
SA0401:1 | SC | KA0241A1 | WHT | 20 | 14.C5 | XT0563:5 | PWR,DISTRIBUTION RAIL^LEFT DOOR | 14.C6
SA0401:2 | SC | FU0139 | WHT | 20 | 14.C5 | XT0563:6 | PWR,DISTRIBUTION RAIL^LEFT DOOR | 14.C6
SB0400:11 | SC | ESTOPB | WHT | 20 | 14.D5 | XT0563:1 | PWR,DISTRIBUTION RAIL^LEFT DOOR | 14.D6
SB0400:12 | SC | ESTOPA | WHT | 20 | 14.D5 | XT0563:2 | PWR,DISTRIBUTION RAIL^LEFT DOOR | 14.D6
SH0400:B | SC | 0V1 | WHT | 20 | 14.B5 | XT0562:3 | PWR,DISTRIBUTION RAIL^LEFT DOOR | 11.B2
XT0564:1 B2 | SC | KA023612 | WHT | 20 | 14.B5 | XT0563:3 | PWR,DISTRIBUTION RAIL^LEFT DOOR | 14.B6
SolarTools ver. 24.0.84.26264 (Jun 3, 2025)
Report date: 7/10/2025 2:56 PM

## CONSOLE DOOR^PANEL
CONSOLE DOOR^PANEL
Project # | G9440
Project Name | NOC AL SHAHEEN T130
Revision | A.5
Controls DE | G. Colby
Phone:
Controls ME | R. Duran
Phone:
From | [5 empty] | To
Device ID | Cable (W) Conductor (SC) Jumper Clip (JC) | Wire No. | Wire ID | Gauge/Size | Page/Zone | Device ID | Location | Page/Zone
AT0190:GND | SC | AT0190G | GRN/YEL | 14 | 11.C4 | FRAME | CONSOLE DOOR^PANEL | 11.D3
AT0190:USB1 | SC | AT0190K | CABLE | USB | 11.C4 | AT0190K:KI | CONSOLE DOOR^PANEL | 11.D5
GF4000:A13 | SC | GF4000-A13 | GRN/YEL | 14 | 105.B5 | FG-GF4000:1 | CONSOLE DOOR^PANEL | 105.B5
TM0102:GND | SC | TM0102G | GRN/YEL | 14 | 21.B5 | FRAME | CONSOLE DOOR^PANEL | 21.C5
GF4000:A1 | W4000 | RE4000-1 | WHT | 16 | 105.A5 | XT-9105:1 | 1 BAY BACK WALL | 105.A4
GF4000:A3 | W4000 | RE4000-2 | BLK | 16 | 105.A5 | XT-9105:2 | 1 BAY BACK WALL | 105.A4
GF4000:A4 | SC | 012246 | WHT | 20 | 105.A6 | AF0122:46 | 1 BAY RIGHT WALL | 105.A7
GF4000:A5 | SC | 012214 | WHT | 20 | 105.A6 | AF0122:14 | 1 BAY RIGHT WALL | 105.A7
GF4000:A6 | SC | 012247 | WHT | 20 | 105.B6 | AF0122:47 | 1 BAY RIGHT WALL | 105.B7
GF4000:A7 | SC | 012215 | WHT | 20 | 105.B6 | AF0122:15 | 1 BAY RIGHT WALL | 105.B7
AT0190:NEG | SC | 0V1 | WHT | 14 | 11.C4 | XT0562:2 | PWR,DISTRIBUTION RAIL^LEFT DOOR | 11.B2
AT0190:POS | SC | FU0190 | WHT | 14 | 11.C4 | FU0190:LD | PWR,DISTRIBUTION RAIL^LEFT DOOR | 11.D3
AT0190:ETAP:L1 | WC0019 | AT0190E | ENET | CABLE | 11.C4 | AT0680:LAN2 | PWR,DISTRIBUTION RAIL^LEFT DOOR | 5.A4
TM0102:1 | SC | VGENA | RED | 16 | 21.B5 | SA0710:16 | SWITCH PANEL | 21.D5
TM0102:2 | SC | VGENB | RED | 16 | 21.B5 | SA0710:26 | SWITCH PANEL | 21.C5
TM0102:3 | SC | VGENC | RED | 16 | 21.B5 | SA0710:17 | SWITCH PANEL | 21.D5
TM0102:4 | SC | TM01024 | RED | 16 | 21.B5 | SA0770:13 | SWITCH PANEL | 21.B5
TM0102:5 | SC | TM01025 | RED | 16 | 21.B5 | SA0770:17 | SWITCH PANEL | 21.B5
TM0102:6 | SC | TM01026 | RED | 16 | 21.B5 | SA0770:27 | SWITCH PANEL | 21.B5
TM0102:7 | SC | TM01027 | RED | 16 | 21.B5 | SA0770:23 | SWITCH PANEL | 21.B5
SolarTools ver. 24.0.84.26264 (Jun 3, 2025)
Report date: 7/10/2025 2:56 PM

## METER PANEL
METER PANEL
Project # | G9440
Project Name | NOC AL SHAHEEN T130
Revision | A.5
Controls DE | G. Colby
Phone:
Controls ME | R. Duran
Phone:
From | [5 empty] | To
Device ID | Cable (W) Conductor (SC) Jumper Clip (JC) | Wire No. | Wire ID | Gauge/Size | Page/Zone | Device ID | Location | Page/Zone
PA0703:1 | SC | PA07714 | BLU | 16 | 21.A4 | PA0771:4 | METER PANEL | 21.C3
PA0771:8 | SC | VGENC | RED | 16 | 21.C3 | XT-9110:6 | 1 BAY BACK WALL | 100.D4
PF0701:7 | SC | PF07017 | RED | 16 | 21.B6 | KA121A:14 | 1 BAY BACK WALL | 21.B6
PA0701:7 | W8064 | PA07017 | RED | 20 | 20.A1 | RS0106:1 | 1 BAY BACK WALL | 20.A4
PA0701:8 | W8064 | PA07018 | BLK | 20 | 20.A1 | RS0106:3 | 1 BAY BACK WALL | 20.A4
FLOATING | W8064 | EXCS | SH | 20 | 20.A1 | XT0106:1 | 1 BAY BACK WALL | 20.A4
PA0703:5 | SC | PA07035 | BLU | 16 | 21.A4 | XT0342:1 | 1 BAY LEFT WALL | 21.A2
PA0771:6 | SC | PA07716 | BLU | 16 | 21.C3 | XT0342:4 | 1 BAY LEFT WALL | 21.C2
PA0771:7 | SC | VGENB | RED | 16 | 21.C3 | XT0341:4 | 1 BAY LEFT WALL | 21.D2
PV0701:7 | W8065 | EXC0 | RED | 20 | 20.A1 | XT0340:5 | 1 BAY LEFT WALL | 20.A5
PV0701:8 | W8065 | EXC2 | BLK | 20 | 20.A1 | XT0340:6 | 1 BAY LEFT WALL | 20.B5
FLOATING | W8065 | EXCS | SH | 20 | 20.B1 | XT0340:7 | 1 BAY LEFT WALL | 20.B5
PA0700:7 | SC | PA07007 | BLU | 16 | 21.B2 | SA0740:11 | SWITCH PANEL | 21.B2
PA0700:8 | SC | MCTN | BLU | 16 | 21.B2 | SA0740:21 | SWITCH PANEL | 21.B2
PA0703:2 | SC | PA07032 | RED | 16 | 21.A4 | SA0770:26 | SWITCH PANEL | 21.B5
PA0703:3 | SC | PA07033 | BLU | 16 | 21.A4 | SA0740:12 | SWITCH PANEL | 21.C2
PA0703:4 | SC | PA07034 | RED | 16 | 21.A4 | SA0770:22 | SWITCH PANEL | 21.B5
PA0703:6 | SC | PA07036 | RED | 16 | 21.A4 | SA0770:12 | SWITCH PANEL | 21.B5
PA0703:7 | SC | PA07037 | BLU | 16 | 21.A4 | SA0740:24 | SWITCH PANEL | 21.B2
PA0703:8 | SC | PA07038 | RED | 16 | 21.A4 | SA0770:16 | SWITCH PANEL | 21.B5
PF0701:8 | SC | VGENB | RED | 16 | 21.B6 | SA0770:28 | SWITCH PANEL | 21.B6
PV0700:7 | SC | PV07007 | RED | 16 | 21.C5 | SA0710:11 | SWITCH PANEL | 21.D5
PV0700:8 | SC | PV07008 | RED | 16 | 21.C5 | SA0710:21 | SWITCH PANEL | 21.C5
SolarTools ver. 24.0.84.26264 (Jun 3, 2025)
Report date: 7/10/2025 2:56 PM

## ORBIT 60^DOOR PANEL
ORBIT 60^DOOR PANEL
CONTROL CONSOLE^(ORBIT 60 RACK DOOR PANEL)
Project # | G9440
Project Name | NOC AL SHAHEEN T130
Revision | A.5
Controls DE | G. Colby
Phone:
Controls ME | R. Duran
Phone:
From | [5 empty] | To
Device ID | Cable (W) Conductor (SC) Jumper Clip (JC) | Wire No. | Wire ID | Gauge/Size | Page/Zone | Device ID | Location | Page/Zone
UV0610:P.E. | SC | PEG01301 | GRN/YEL | 14 | 23.B1 | PEG0130:1 | 1 BAY RIGHT WALL | 23.C1
UV0611:P.E. | SC | PEG01302 | GRN/YEL | 14 | 23.C1 | PEG0130:2 | 1 BAY RIGHT WALL | 23.C2
AP0616:SIG3 | W6163 | 0616SIG3 | RED | 20 | 89.A6 | UAI9223-1:7 | 2 BAY BACK LEFT WALL | 89.A5
AP0616:COM3 | W6163 | 0616COM3 | BLK | 20 | 89.A6 | UAI9223-1:8 | 2 BAY BACK LEFT WALL | 89.A5
AP0616:SHLD3 | W6163 | 0616SHLD3 | SH | 20 | 89.A6 | FLOATING | 2 BAY BACK LEFT WALL | 89.A6
AP0622:A4(+) | W6224 | 0622A4 | RED | 20 | 89.D6 | UAI9223A-1:8+ | 2 BAY BACK LEFT WALL | 89.D5
AP0622:B4(-) | W6224 | 0622B4 | BLK | 20 | 89.D6 | UAI9223A-1:7- | 2 BAY BACK LEFT WALL | 89.D5
AP0622:SHLD4 | W6224 | 06224SHLD4 | SH | 20 | 89.D6 | FW2?:1 | 2 BAY BACK LEFT WALL | 89.D6
AP0624:SIG1 | W6241 | 0624SIG1 | RED | 20 | 89.B6 | UAI9223-2:7 | 2 BAY BACK LEFT WALL | 89.B5
AP0624:COM1 | W6241 | 0624COM1 | BLK | 20 | 89.B6 | UAI9223-2:8 | 2 BAY BACK LEFT WALL | 89.B5
AP0624:SHLD1 | W6241 | 0624SHLD1 | SH | 20 | 89.B6 | FLOATING | 2 BAY BACK LEFT WALL | 89.B6
AP0624:SIG2 | W6242 | 0624SIG2 | RED | 20 | 89.B6 | UAI9223-3:7 | 2 BAY BACK LEFT WALL | 89.B5
AP0624:COM2 | W6242 | 0624COM2 | BLK | 20 | 89.B6 | UAI9223-3:8 | 2 BAY BACK LEFT WALL | 89.B5
AP0624:SHLD2 | W6242 | 0624SHLD2 | SH | 20 | 89.B6 | FLOATING | 2 BAY BACK LEFT WALL | 89.B6
AP0624:SIG3 | W6243 | 0624SIG3 | RED | 20 | 89.C6 | UAI9223-4:7 | 2 BAY BACK LEFT WALL | 89.C5
AP0624:COM3 | W6243 | 0624COM3 | BLK | 20 | 89.C6 | UAI9223-4:8 | 2 BAY BACK LEFT WALL | 89.C5
AP0624:SHLD3 | W6243 | 0624SHLD3 | SH | 20 | 89.C6 | FLOATING | 2 BAY BACK LEFT WALL | 89.C6
AP0624:SIG4 | W6244 | 0624SIG4 | RED | 20 | 89.C6 | UAI9223-5:7 | 2 BAY BACK LEFT WALL | 89.C5
AP0624:COM4 | W6244 | 0624COM4 | BLK | 20 | 89.C6 | UAI9223-5:8 | 2 BAY BACK LEFT WALL | 89.C5
AP0624:SHLD4 | W6244 | 0624SHLD4 | SH | 20 | 89.C6 | FLOATING | 2 BAY BACK LEFT WALL | 89.C6
AP0612:ARM | SC | 0612ARM | WHT | 20 | 23.D2 | AF0082:38 | 2 BAY BACK RIGHT PANEL | 23.D2
AP0612:COM | SC | 0612COM | WHT | 20 | 23.D6 | KA0701:14 | 2 BAY BACK RIGHT PANEL | 23.D6
AP0612:NO | SC | 0612NO | WHT | 20 | 23.D2 | AF0082:06 | 2 BAY BACK RIGHT PANEL | 23.D2
AP0612:TM | SC | 0612TM | WHT | 20 | 23.D6 | KA0701:11 | 2 BAY BACK RIGHT PANEL | 23.D6
AP0628:ARM1 | SC | 0628ARM1 | WHT | 20 | 23.D1 | AF0082:39 | 2 BAY BACK RIGHT PANEL | 23.D1
AP0628:ARM2 | SC | 0628ARM2 | WHT | 20 | 23.D3 | AF0082:40 | 2 BAY BACK RIGHT PANEL | 23.D3
AP0628:ARM3 | SC | 0628ARM3 | WHT | 20 | 23.D4 | AF0082:41 | 2 BAY BACK RIGHT PANEL | 23.D4
AP0628:NO1 | SC | 0628NO1 | WHT | 20 | 23.D1 | AF0082:07 | 2 BAY BACK RIGHT PANEL | 23.D1
AP0628:NO2 | SC | 0628NO2 | WHT | 20 | 23.D3 | AF0082:08 | 2 BAY BACK RIGHT PANEL | 23.D3
AP0628:NO3 | SC | 0628NO3 | WHT | 20 | 23.D4 | AF0082:09 | 2 BAY BACK RIGHT PANEL | 23.D4
AP0615:PORT A | WC0609 | AP0605ENET | ENET | CABLE | 23.C2 | AP0605:ENET | 2 BAY BACK RIGHT PANEL | 23.C4
AP0616:SIG1 | W6161 | 0616SIG1 | RED | 20 | 83.A6 | UAI9208-1:7 | 2 BAY LEFT WALL | 83.A5
AP0616:COM1 | W6161 | 0616COM1 | BLK | 20 | 83.A6 | UAI9208-1:8 | 2 BAY LEFT WALL | 83.A5
AP0616:SHLD1 | W6161 | 0616SHLD1 | SH | 20 | 83.A6 | FLOATING | 2 BAY LEFT WALL | 83.A6
AP0617:SIG1 | W6171 | 0617SIG1 | RED | 20 | 83.B6 | UAI9208-2:7 | 2 BAY LEFT WALL | 83.B5
AP0617:COM1 | W6171 | 0617COM1 | BLK | 20 | 83.B6 | UAI9208-2:8 | 2 BAY LEFT WALL | 83.B5
AP0617:SHLD1 | W6171 | 0617SHLD1 | SH | 20 | 83.B6 | FLOATING | 2 BAY LEFT WALL | 83.B6
AP0617:SIG2 | W6172 | 0617SIG2 | RED | 20 | 83.B6 | UAI9208-3:7 | 2 BAY LEFT WALL | 83.B5
AP0617:COM2 | W6172 | 0617COM2 | BLK | 20 | 83.B6 | UAI9208-3:8 | 2 BAY LEFT WALL | 83.B5
AP0617:SHLD2 | W6172 | 0617SHLD2 | SH | 20 | 83.B6 | FLOATING | 2 BAY LEFT WALL | 83.B6
AP0617:SIG3 | W6173 | 0617SIG3 | RED | 20 | 83.C6 | UAI9208-4:7 | 2 BAY LEFT WALL | 83.C5
AP0617:COM3 | W6173 | 0617COM3 | BLK | 20 | 83.C6 | UAI9208-4:8 | 2 BAY LEFT WALL | 83.C5
AP0617:SHLD3 | W6173 | 0617SHLD3 | SH | 20 | 83.C6 | FLOATING | 2 BAY LEFT WALL | 83.C6
AP0617:SIG4 | W6174 | 0617SIG4 | RED | 20 | 83.C6 | UAI9208-5:7 | 2 BAY LEFT WALL | 83.C5
AP0617:COM4 | W6174 | 0617COM4 | BLK | 20 | 83.C6 | UAI9208-5:8 | 2 BAY LEFT WALL | 83.C5
AP0617:SHLD4 | W6174 | 0617SHLD4 | SH | 20 | 83.C6 | FLOATING | 2 BAY LEFT WALL | 83.C6
AP0618:SIG1 | W6181 | 0618SIG1 | RED | 20 | 83.C6 | UAI9208-6:7 | 2 BAY LEFT WALL | 83.C5
AP0618:COM1 | W6181 | 0618COM1 | BLK | 20 | 83.C6 | UAI9208-6:8 | 2 BAY LEFT WALL | 83.C5
AP0618:SHLD1 | W6181 | 0618SHLD1 | SH | 20 | 83.C6 | FLOATING | 2 BAY LEFT WALL | 83.D6
AP0618:SIG2 | W6182 | 0618SIG2 | RED | 20 | 83.D6 | UAI9208-7:7 | 2 BAY LEFT WALL | 83.D5
AP0618:COM2 | W6182 | 0618COM2 | BLK | 20 | 83.D6 | UAI9208-7:8 | 2 BAY LEFT WALL | 83.D5
AP0618:SHLD2 | W6182 | 0618SHLD2 | SH | 20 | 83.D6 | FLOATING | 2 BAY LEFT WALL | 83.D6
AP0621:SIG1 | W6211 | 0621SIG1 | RED | 20 | 84.A6 | UAI9209-1:7 | 2 BAY LEFT WALL | 84.A5
AP0621:COM1 | W6211 | 0621COM1 | BLK | 20 | 84.A6 | UAI9209-1:8 | 2 BAY LEFT WALL | 84.A5
AP0621:SHLD1 | W6211 | 0621SHLD1 | SH | 20 | 84.A6 | FW1213:1 | 2 BAY LEFT WALL | 84.A6
AP0621:SIG3 | W6213 | 0621SIG3 | RED | 20 | 83.D6 | UAI9208-8:7 | 2 BAY LEFT WALL | 83.D5
AP0621:COM3 | W6213 | 0621COM3 | BLK | 20 | 83.D6 | UAI9208-8:8 | 2 BAY LEFT WALL | 83.D5
AP0621:SHLD3 | W6213 | 0621SHLD3 | SH | 20 | 83.D6 | FLOATING | 2 BAY LEFT WALL | 83.D6
UV0610:+DC | SC | FU0111 | WHT | 14 | 23.B1 | FU0111:LD | 2 BAY RIGHT WALL | 23.A5
UV0610:COM | SC | 0V | WHT | 14 | 23.B1 | XT0110:2 | 2 BAY RIGHT WALL | 23.A6
UV0611:+DC | SC | FU0112 | WHT | 14 | 23.C1 | FU0112:LD | 2 BAY RIGHT WALL | 23.A5
UV0611:COM | SC | 0V | WHT | 14 | 23.C1 | XT0110:3 | 2 BAY RIGHT WALL | 23.A6
SolarTools ver. 24.0.84.26264 (Jun 3, 2025)
Report date: 7/10/2025 2:56 PM

## PWR,DIST RAIL^LEFT DOOR
PWR,DISTRIBUTION RAIL^LEFT DOOR
Project # | G9440
Project Name | NOC AL SHAHEEN T130
Revision | A.5
Controls DE | G. Colby
Phone:
Controls ME | R. Duran
Phone:
From | [5 empty] | To
Device ID | Cable (W) Conductor (SC) Jumper Clip (JC) | Wire No. | Wire ID | Gauge/Size | Page/Zone | Device ID | Location | Page/Zone
XT0561:2 | JC | FU0200LI | CLIP | --- | 11.A2 | XT0561:1 | PWR,DISTRIBUTION RAIL^LEFT DOOR | 11.A2
XT0562:1 | JC | 0V1 | CLIP | --- | 11.B2 | XT0562:2 | PWR,DISTRIBUTION RAIL^LEFT DOOR | 11.B2
XT0562:2 | JC | 0V1 | CLIP | --- | 11.B2 | XT0562:3 | PWR,DISTRIBUTION RAIL^LEFT DOOR | 11.B2
XT0560:2 | SC | JW0 | CLIP | -- | 11.B2 | XT0562:1 | PWR,DISTRIBUTION RAIL^LEFT DOOR | 11.B2
AT0680:NEG | SC | 0V | WHT | 14 | 5.A4 | XT0680:2 | PWR,DISTRIBUTION RAIL^LEFT DOOR | 5.B3
AT0680:POS | SC | AT0680POS | WHT | 14 | 5.A4 | XT0680:1 | PWR,DISTRIBUTION RAIL^LEFT DOOR | 5.B3
FU0200:LI | SC | FU0200LI | WHT | 14 | 11.A3 | FU0201:LI | PWR,DISTRIBUTION RAIL^LEFT DOOR | 11.B3
FU0200:LI | SC | FU0200LI | WHT | 14 | 11.A3 | XT0561:1 | PWR,DISTRIBUTION RAIL^LEFT DOOR | 11.A2
FU0201:LI | SC | FU0200LI | WHT | 14 | 11.B3 | FU0273:LI | PWR,DISTRIBUTION RAIL^LEFT DOOR | 11.B3
FU0560:LD | SC | FU0200LI | WHT | 14 | 11.A2 | XT0561:1 | PWR,DISTRIBUTION RAIL^LEFT DOOR | 11.A2
FU0560:LI | SC | FU0136 | WHT | 12 | 11.A2 | XT0560:1 | PWR,DISTRIBUTION RAIL^LEFT DOOR | 11.A2
FU0680:LD | SC | AT0680POS | WHT | 14 | 5.B2 | XT0680:1 | PWR,DISTRIBUTION RAIL^LEFT DOOR | 5.B3
AT0680:LAN1 | WC0680 | AP0606L1 | ENET | CABLE | 5.A4 | AP0606:L1 | 2 BAY BACK RIGHT PANEL | 5.C4
FU0190:LI | SC | FU0200LI | WHT | 14 | 11.D3 | FU0274:LI | 2 BAY LEFT WALL | 11.C3
FU0273:LI | SC | FU0200LI | WHT | 14 | 11.B3 | FU0274:LI | 2 BAY LEFT WALL | 11.C3
FU0680:LI | SC | FU0210 | WHT | 14 | 5.B2 | XT0233:3 | 2 BAY LEFT WALL | 16.C5
XT0560:1 | SC | FU0136 | WHT | 12 | 11.A2 | XT0138:2 | 2 BAY LEFT WALL | 16.A4
XT0560:2 | SC | 0V | WHT | 16 | 11.B2 | XT0134:2 | 2 BAY LEFT WALL | 16.B4
XT0563:1 | SC | ESTOPB | WHT | 20 | 14.D6 | XT0240:2 | 2 BAY LEFT WALL | 18.A3
XT0563:2 | SC | ESTOPA | WHT | 20 | 14.D6 | XT0240:3 | 2 BAY LEFT WALL | 18.A3
XT0563:3 | SC | KA023612 | WHT | 20 | 14.B6 | XT0240:13 | 2 BAY LEFT WALL | 18.D4
XT0563:4 | SC | 0V | WHT | 20 | 14.B6 | XT0240:9 | 2 BAY LEFT WALL | 18.D3
XT0563:5 | SC | KA0241A1 | WHT | 20 | 14.C6 | XT0240:6 | 2 BAY LEFT WALL | 18.C3
XT0563:6 | SC | FU0139 | WHT | 20 | 14.C6 | XT0240:11 | 2 BAY LEFT WALL | 18.C4
XT0680:2 | SC | 0V | WHT | 14 | 5.B3 | XT0235:3 | 2 BAY LEFT WALL | 16.D5
FU0273:LD | SC | FU0273 | WHT | 14 | 11.B3 | ZS0273:1 | ASSEMBLY CONSOLE | 11.B4
XT0562:1 | SC | 0V1 | WHT | 14 | 11.B2 | EL0273:W1 | ASSEMBLY CONSOLE | 11.B4
XT0562:3 | SC | 0V1 | WHT | 14 | 11.B2 | EL0274:W1 | ASSEMBLY CONSOLE | 11.C4
FU0200:LD | SC | FU0200 | WHT | 14 | 11.A3 | AU0200:V+ | ASSEMBLY^CONTROL PANEL | 11.A3
FU0201:LD | SC | FU0201 | WHT | 14 | 11.B3 | AF0202:V+ | ASSEMBLY^CONTROL PANEL | 11.A5
XT0562:1 | SC | 0V1 | WHT | 14 | 11.B2 | AF0202:COM | ASSEMBLY^CONTROL PANEL | 11.A5
XT0562:1 | SC | 0V1 | WHT | 14 | 11.B2 | AU0200:COM | ASSEMBLY^CONTROL PANEL | 11.A3
XT0562:3 | SC | 0V1 | WHT | 20 | 11.B2 | SH0400:B | ASSEMBLY^CONTROL PANEL | 14.B5
XT0563:1 | SC | ESTOPB | WHT | 20 | 14.D6 | SB0400:11 | ASSEMBLY^CONTROL PANEL | 14.D5
XT0563:2 | SC | ESTOPA | WHT | 20 | 14.D6 | SB0400:12 | ASSEMBLY^CONTROL PANEL | 14.D5
XT0563:3 | SC | KA023612 | WHT | 20 | 14.B6 | XT0564:1 B2 | ASSEMBLY^CONTROL PANEL | 14.B5
XT0563:4 | SC | 0V | WHT | 20 | 14.B6 | HL0410:A | ASSEMBLY^CONTROL PANEL | 14.B5
XT0563:5 | SC | KA0241A1 | WHT | 20 | 14.C6 | SA0401:1 | ASSEMBLY^CONTROL PANEL | 14.C5
XT0563:6 | SC | FU0139 | WHT | 20 | 14.C6 | SA0401:2 | ASSEMBLY^CONTROL PANEL | 14.C5
FU0190:LD | SC | FU0190 | WHT | 14 | 11.D3 | AT0190:POS | CONSOLE DOOR^PANEL | 11.C4
XT0562:2 | SC | 0V1 | WHT | 14 | 11.B2 | AT0190:NEG | CONSOLE DOOR^PANEL | 11.C4
AT0680:LAN2 | WC0019 | AT0190E | ENET | CABLE | 5.A4 | AT0190:ETAP:L1 | CONSOLE DOOR^PANEL | 11.C4
SolarTools ver. 24.0.84.26264 (Jun 3, 2025)
Report date: 7/10/2025 2:56 PM

## SWITCH PANEL
SWITCH PANEL
Project # | G9440
Project Name | NOC AL SHAHEEN T130
Revision | A.5
Controls DE | G. Colby
Phone:
Controls ME | R. Duran
Phone:
From | [5 empty] | To
Device ID | Cable (W) Conductor (SC) Jumper Clip (JC) | Wire No. | Wire ID | Gauge/Size | Page/Zone | Device ID | Location | Page/Zone
HL0701:A | SC | 0V | WHT | 16 | 20.C2 | HL0702:A | SWITCH PANEL | 20.C2
HL0703: | SC | VBUSA | RED | 16 | 21.A5 | PF0700:2 | SWITCH PANEL | 21.A4
HL0703: | SC | PF07008 | RED | 16 | 21.A5 | SA0700:12 | SWITCH PANEL | 21.A5
HL0704: | SC | VBUSC | RED | 16 | 21.A5 | PF0700:1 | SWITCH PANEL | 21.A4
HL0704: | SC | PF07007 | RED | 16 | 21.A5 | SA0700:16 | SWITCH PANEL | 21.A5
SA0700:12 | SC | PF07008 | RED | 16 | 21.A5 | PF0700:8 | SWITCH PANEL | 21.A4
SA0700:13 | SC | VGENA | RED | 16 | 21.A5 | SA0770:18 | SWITCH PANEL | 21.B6
SA0700:16 | SC | PF07007 | RED | 16 | 21.A5 | PF0700:7 | SWITCH PANEL | 21.A4
SA0700:17 | SC | VGENC | RED | 16 | 21.A5 | SA0770:24 | SWITCH PANEL | 21.B6
SA0700:22 | SC | SA070022 | WHT | 16 | 20.C3 | SA0701:13 | SWITCH PANEL | 20.C2
SA0701:12 | SC | FU0333 | WHT | 16 | 20.C2 | SA0701:14 | SWITCH PANEL | 20.C2
SA0710:12 | SC | VBUSA | RED | 16 | 21.D5 | SA0710:24 | SWITCH PANEL | 21.D5
SA0710:13 | SC | VBUSC | RED | 16 | 21.D5 | SA0710:14 | SWITCH PANEL | 21.D5
SA0710:16 | SC | VGENA | RED | 16 | 21.D5 | SA0710:28 | SWITCH PANEL | 21.D5
SA0710:17 | SC | VGENC | RED | 16 | 21.D5 | SA0710:18 | SWITCH PANEL | 21.D5
SA0710:22 | SC | VBUSB | RED | 16 | 21.C5 | SA0710:23 | SWITCH PANEL | 21.D5
SA0710:26 | SC | VGENB | RED | 16 | 21.C5 | SA0710:27 | SWITCH PANEL | 21.D5
SA0710:28 | SC | VGENA | RED | 16 | 21.D5 | SA0770:18 | SWITCH PANEL | 21.B6
SA0740:12 | SC | PA07033 | BLU | 16 | 21.C2 | SA0740:22 | SWITCH PANEL | 21.B2
SA0740:13 | SC | SA074013 | BLU | 16 | 21.B2 | SA0740:23 | SWITCH PANEL | 21.B2
SA0740:14 | SC | PA07037 | BLU | 16 | 21.B2 | SA0740:24 | SWITCH PANEL | 21.B2
SA0770:11 | SC | PA07036 | RED | 16 | 21.B6 | SA0770:12 | SWITCH PANEL | 21.B5
SA0770:14 | SC | VGENB | RED | 16 | 21.B6 | SA0770:28 | SWITCH PANEL | 21.B6
SA0770:15 | SC | PA07038 | RED | 16 | 21.B6 | SA0770:16 | SWITCH PANEL | 21.B5
SA0770:21 | SC | PA07034 | RED | 16 | 21.B6 | SA0770:22 | SWITCH PANEL | 21.B5
SA0770:25 | SC | PA07032 | RED | 16 | 21.B6 | SA0770:26 | SWITCH PANEL | 21.B5
SA0770:24 | SC | VGENC | RED | 16 | 21.B6 | KA121A:11 | 1 BAY BACK WALL | 21.B6
HL0701:A+ | SC | KA9602NC | WHT | 16 | 20.C2 | XT0343:3 | 1 BAY LEFT WALL | 20.C5
HL0702:A+ | SC | KA0330A1 | WHT | 16 | 20.C2 | XT0343:4 | 1 BAY LEFT WALL | 20.C5
HL0703: | SC | VBUSA | RED | 16 | 21.A5 | XT0341:2 | 1 BAY LEFT WALL | 21.D2
HL0704: | SC | VBUSC | RED | 16 | 21.A5 | XT0341:3 | 1 BAY LEFT WALL | 21.D2
SA0700:13 | SC | VGENA | RED | 16 | 21.A5 | XT0341:7 | 1 BAY LEFT WALL | 21.D2
SA0700:17 | SC | VGENC | RED | 16 | 21.A5 | XT0341:6 | 1 BAY LEFT WALL | 21.D2
SA0700:23 | SC | KA018511 | WHT | 16 | 20.C3 | XT0343:1 | 1 BAY LEFT WALL | 20.C5
SA0701:15 | SC | KA0333A1 | WHT | 16 | 20.C2 | XT0343:2 | 1 BAY LEFT WALL | 20.C5
SA0710:12 | SC | VBUSA | RED | 16 | 21.D5 | XT0341:2 | 1 BAY LEFT WALL | 21.D2
SA0710:14 | SC | VBUSC | RED | 16 | 21.D5 | XT0341:3 | 1 BAY LEFT WALL | 21.D2
SA0710:18 | SC | VGENC | RED | 16 | 21.D5 | XT0341:6 | 1 BAY LEFT WALL | 21.D2
SA0710:23 | SC | VBUSB | RED | 16 | 21.D5 | XT0341:1 | 1 BAY LEFT WALL | 21.D2
SA0710:27 | SC | VGENB | RED | 16 | 21.D5 | XT0341:5 | 1 BAY LEFT WALL | 21.D2
SA0740:13 | SC | SA074013 | BLU | 16 | 21.B2 | XT0342:3 | 1 BAY LEFT WALL | 21.B3
SA0740:21 | SC | MCTN | BLU | 16 | 21.B2 | XT0342:2 | 1 BAY LEFT WALL | 21.B2
SA0770:14 | SC | VGENB | RED | 16 | 21.B6 | XT0341:4 | 1 BAY LEFT WALL | 21.D2
HL0702:A | SC | 0V | WHT | 16 | 20.C2 | XT0336:3 | 1 BAY RIGHT WALL | 24.C4
SA0701:14 | SC | FU0333 | WHT | 16 | 20.C2 | XT0335:1 | 1 BAY RIGHT WALL | 24.B4
SA0710:16 | SC | VGENA | RED | 16 | 21.D5 | TM0102:1 | CONSOLE DOOR^PANEL | 21.B5
SA0710:17 | SC | VGENC | RED | 16 | 21.D5 | TM0102:3 | CONSOLE DOOR^PANEL | 21.B5
SA0710:26 | SC | VGENB | RED | 16 | 21.C5 | TM0102:2 | CONSOLE DOOR^PANEL | 21.B5
SA0770:13 | SC | TM01024 | RED | 16 | 21.B5 | TM0102:4 | CONSOLE DOOR^PANEL | 21.B5
SA0770:17 | SC | TM01025 | RED | 16 | 21.B5 | TM0102:5 | CONSOLE DOOR^PANEL | 21.B5
SA0770:23 | SC | TM01027 | RED | 16 | 21.B5 | TM0102:7 | CONSOLE DOOR^PANEL | 21.B5
SA0770:27 | SC | TM01026 | RED | 16 | 21.B5 | TM0102:6 | CONSOLE DOOR^PANEL | 21.B5
SA0710:11 | SC | PV07007 | RED | 16 | 21.D5 | PV0700:7 | METER PANEL | 21.C5
SA0710:21 | SC | PV07008 | RED | 16 | 21.C5 | PV0700:8 | METER PANEL | 21.C5
SA0740:11 | SC | PA07007 | BLU | 16 | 21.B2 | PA0700:7 | METER PANEL | 21.B2
SA0740:12 | SC | PA07033 | BLU | 16 | 21.C2 | PA0703:3 | METER PANEL | 21.A4
SA0740:21 | SC | MCTN | BLU | 16 | 21.B2 | PA0700:8 | METER PANEL | 21.B2
SA0740:24 | SC | PA07037 | BLU | 16 | 21.B2 | PA0703:7 | METER PANEL | 21.A4
SA0770:12 | SC | PA07036 | RED | 16 | 21.B5 | PA0703:6 | METER PANEL | 21.A4
SA0770:16 | SC | PA07038 | RED | 16 | 21.B5 | PA0703:8 | METER PANEL | 21.A4
SA0770:22 | SC | PA07034 | RED | 16 | 21.B5 | PA0703:4 | METER PANEL | 21.A4
SA0770:26 | SC | PA07032 | RED | 16 | 21.B5 | PA0703:2 | METER PANEL | 21.A4
SA0770:28 | SC | VGENB | RED | 16 | 21.B6 | PF0701:8 | METER PANEL | 21.B6
SolarTools ver. 24.0.84.26264 (Jun 3, 2025)
Report date: 7/10/2025 2:56 PM

## Panel Errors
Panel Errors
Project # | G9440
Project Name | NOC AL SHAHEEN T130
Revision | A.5
Controls DE | G. Colby
Phone:
Controls ME | R. Duran
Phone:
From | [6 empty] | To
Device ID | Location | Cable (W) Conductor (SC) Jumper Clip (JC) | Wire ID | Wire No. | Gauge/Size | Page/Zone | Device ID | Location | Page/Zone
XT0930:3 | 1 BAY LEFT WALL | WC8010 | SH | AT0140LS(S) | 16 | 104.C5 | FW0220:3 | PANEL | 104.D6
Report date: 7/10/2025 2:56 PM |  |  |  | SolarTools ver. 24.0.84.26264 (Jun 3, 2025)

## Cable Part Numbers
Cable Part Numbers |  |  | SolarTools ver. 24.0.84.26264 (Jun 3, 2025)
Project # | G9440
Report date: 7/10/2025 2:58 PM
Project Name | NOC AL SHAHEEN T130
Revision | A.5
Controls DE | G. Colby
Phone:
Controls ME | R. Duran
Phone:
Device ID |  | Part Number |  | Description
W0851 |  | 1022941-12 |  | TPE, 1 PAIR TWISTED SHIELDED
WI0851 |  | 1022941-12 |  | TPE, 1 PAIR TWISTED SHIELDED
W0552 |  | 1022941-12 |  | TPE, 1 PAIR TWISTED SHIELDED
W0553 |  | 1022941-12 |  | TPE, 1 PAIR TWISTED SHIELDED
W0554 |  | 1022941-12 |  | TPE, 1 PAIR TWISTED SHIELDED
W0556 |  | 1022941-12 |  | TPE, 1 PAIR TWISTED SHIELDED
W0557 |  | 1022941-12 |  | TPE, 1 PAIR TWISTED SHIELDED
W0560 |  | 1022941-12 |  | TPE, 1 PAIR TWISTED SHIELDED
W0561 |  | 1022941-12 |  | TPE, 1 PAIR TWISTED SHIELDED
W0562 |  | 1022941-12 |  | TPE, 1 PAIR TWISTED SHIELDED
W0563 |  | 1022941-12 |  | TPE, 1 PAIR TWISTED SHIELDED
W0565 |  | 1022941-12 |  | TPE, 1 PAIR TWISTED SHIELDED
W0570 |  | 1022941-12 |  | TPE, 1 PAIR TWISTED SHIELDED
W0571 |  | 1022941-12 |  | TPE, 1 PAIR TWISTED SHIELDED
W0572 |  | 1022941-12 |  | TPE, 1 PAIR TWISTED SHIELDED
W0573 |  | 1022941-12 |  | TPE, 1 PAIR TWISTED SHIELDED
W0640 |  | 1022941-12 |  | TPE, 1 PAIR TWISTED SHIELDED
W0641 |  | 1022941-12 |  | TPE, 1 PAIR TWISTED SHIELDED
W0642 |  | 1022941-12 |  | TPE, 1 PAIR TWISTED SHIELDED
W0643 |  | 1022941-12 |  | TPE, 1 PAIR TWISTED SHIELDED
W0646 |  | 1022941-12 |  | TPE, 1 PAIR TWISTED SHIELDED
W0650 |  | 1022941-12 |  | TPE, 1 PAIR TWISTED SHIELDED
W0663 |  | 1022941-12 |  | TPE, 1 PAIR TWISTED SHIELDED
W0665 |  | 1022941-12 |  | TPE, 1 PAIR TWISTED SHIELDED
W0680 |  | 1022941-12 |  | TPE, 1 PAIR TWISTED SHIELDED
W0681 |  | 1022941-12 |  | TPE, 1 PAIR TWISTED SHIELDED
W0682 |  | 1022941-12 |  | TPE, 1 PAIR TWISTED SHIELDED
W0683 |  | 1022941-12 |  | TPE, 1 PAIR TWISTED SHIELDED
W0684 |  | 1022941-12 |  | TPE, 1 PAIR TWISTED SHIELDED
W0685 |  | 1022941-12 |  | TPE, 1 PAIR TWISTED SHIELDED
W0686 |  | 1022941-13 |  | TPE, 1 TRIAD TWISTED SHIELDED
W0710 |  | 1022941-12 |  | TPE, 1 PAIR TWISTED SHIELDED
W0720 |  | 1022941-12 |  | TPE, 1 PAIR TWISTED SHIELDED
W0722 |  | 1022941-12 |  | TPE, 1 PAIR TWISTED SHIELDED
W0723 |  | 1022941-12 |  | TPE, 1 PAIR TWISTED SHIELDED
W0730 |  | 1022941-12 |  | TPE, 1 PAIR TWISTED SHIELDED
W0731 |  | 1022941-12 |  | TPE, 1 PAIR TWISTED SHIELDED
W0732 |  | 1022941-12 |  | TPE, 1 PAIR TWISTED SHIELDED
W0733 |  | 1022941-12 |  | TPE, 1 PAIR TWISTED SHIELDED
W0734 |  | 1022941-12 |  | TPE, 1 PAIR TWISTED SHIELDED
W0735 |  | 1022941-12 |  | TPE, 1 PAIR TWISTED SHIELDED
W0736 |  | 1022941-13 |  | TPE, 1 TRIAD TWISTED SHIELDED
W0741 |  | 1022941-12 |  | TPE, 1 PAIR TWISTED SHIELDED
W0742 |  | 1022941-12 |  | TPE, 1 PAIR TWISTED SHIELDED
W0743 |  | 1022941-12 |  | TPE, 1 PAIR TWISTED SHIELDED
W0746 |  | 1022941-12 |  | TPE, 1 PAIR TWISTED SHIELDED
W0747 |  | 1022941-12 |  | TPE, 1 PAIR TWISTED SHIELDED
W0750 |  | 1022941-12 |  | TPE, 1 PAIR TWISTED SHIELDED
W0751 |  | 1022941-12 |  | TPE, 1 PAIR TWISTED SHIELDED
W0752 |  | 1022941-12 |  | TPE, 1 PAIR TWISTED SHIELDED
W0753 |  | 1022941-12 |  | TPE, 1 PAIR TWISTED SHIELDED
W0831 |  | 1022941-13 |  | TPE, 1 TRIAD TWISTED SHIELDED
W0832 |  | 1022941-13 |  | TPE, 1 TRIAD TWISTED SHIELDED
W0833 |  | 1022941-13 |  | TPE, 1 TRIAD TWISTED SHIELDED
W0834 |  | 1022941-13 |  | TPE, 1 TRIAD TWISTED SHIELDED
W0835 |  | 1022941-13 |  | TPE, 1 TRIAD TWISTED SHIELDED
W0836 |  | 1022941-13 |  | TPE, 1 TRIAD TWISTED SHIELDED
W0837 |  | 1022941-13 |  | TPE, 1 TRIAD TWISTED SHIELDED
W0840 |  | 1022941-13 |  | TPE, 1 TRIAD TWISTED SHIELDED
W0841 |  | 1022941-13 |  | TPE, 1 TRIAD TWISTED SHIELDED
W0842 |  | 1022941-13 |  | TPE, 1 TRIAD TWISTED SHIELDED
W0843 |  | 1022941-13 |  | TPE, 1 TRIAD TWISTED SHIELDED
W0844 |  | 1022941-13 |  | TPE, 1 TRIAD TWISTED SHIELDED
W0845 |  | 1022941-13 |  | TPE, 1 TRIAD TWISTED SHIELDED
W0846 |  | 1022941-13 |  | TPE, 1 TRIAD TWISTED SHIELDED
W0852 |  | 1022941-12 |  | TPE, 1 PAIR TWISTED SHIELDED
W0853 |  | 1022941-12 |  | TPE, 1 PAIR TWISTED SHIELDED
W0854 |  | 1022941-12 |  | TPE, 1 PAIR TWISTED SHIELDED
W0855 |  | 1022941-12 |  | TPE, 1 PAIR TWISTED SHIELDED
W0856 |  | 1022941-12 |  | TPE, 1 PAIR TWISTED SHIELDED
W0857 |  | 1022941-12 |  | TPE, 1 PAIR TWISTED SHIELDED
W0860 |  | 1022941-12 |  | TPE, 1 PAIR TWISTED SHIELDED
W0861 |  | 1022941-12 |  | TPE, 1 PAIR TWISTED SHIELDED
W0863 |  | 1022941-12 |  | TPE, 1 PAIR TWISTED SHIELDED
W0864 |  | 1022941-12 |  | TPE, 1 PAIR TWISTED SHIELDED
W0866 |  | 1022941-12 |  | TPE, 1 PAIR TWISTED SHIELDED
W4000 |  | 1022941-22 |  | TPE, 1 PAIR TWISTED SHIELDED
W4501 |  | 1022941-12 |  | TPE, 1 PAIR TWISTED SHIELDED
W6161 |  | 1022941-12 |  | TPE, 1 PAIR TWISTED SHIELDED
W6163 |  | 1022941-12 |  | TPE, 1 PAIR TWISTED SHIELDED
W6171 |  | 1022941-12 |  | TPE, 1 PAIR TWISTED SHIELDED
W6172 |  | 1022941-12 |  | TPE, 1 PAIR TWISTED SHIELDED
W6173 |  | 1022941-12 |  | TPE, 1 PAIR TWISTED SHIELDED
W6174 |  | 1022941-12 |  | TPE, 1 PAIR TWISTED SHIELDED
W6181 |  | 1022941-12 |  | TPE, 1 PAIR TWISTED SHIELDED
W6182 |  | 1022941-12 |  | TPE, 1 PAIR TWISTED SHIELDED
W6211 |  | 1022941-12 |  | TPE, 1 PAIR TWISTED SHIELDED
W6213 |  | 1022941-12 |  | TPE, 1 PAIR TWISTED SHIELDED
W6224 |  | 1022941-12 |  | TPE, 1 PAIR TWISTED SHIELDED
W6241 |  | 1022941-12 |  | TPE, 1 PAIR TWISTED SHIELDED
W6242 |  | 1022941-12 |  | TPE, 1 PAIR TWISTED SHIELDED
W6243 |  | 1022941-12 |  | TPE, 1 PAIR TWISTED SHIELDED
W6244 |  | 1022941-12 |  | TPE, 1 PAIR TWISTED SHIELDED
W8003 |  | 1022941-32 |  | TPE, 1 PAIR TWISTED SHIELDED
W8004 |  | 1022941-32 |  | TPE, 1 PAIR TWISTED SHIELDED
W8064 |  | 1022941-12 |  | TPE, 1 PAIR TWISTED SHIELDED
W8065 |  | 1022941-12 |  | TPE, 1 PAIR TWISTED SHIELDED
W8101 |  | 1022941-32 |  | TPE, 1 PAIR TWISTED SHIELDED
W8102 |  | 1022941-32 |  | TPE, 1 PAIR TWISTED SHIELDED
W8103 |  | 1022941-32 |  | TPE, 1 PAIR TWISTED SHIELDED
W8104 |  | 1022941-32 |  | TPE, 1 PAIR TWISTED SHIELDED
W8164 |  | 1022941-22 |  | TPE, 1 PAIR TWISTED SHIELDED
W8165 |  | 1022941-22 |  | TPE, 1 PAIR TWISTED SHIELDED
W8201 |  | 1022941-32 |  | TPE, 1 PAIR TWISTED SHIELDED
W8202 |  | 1022941-32 |  | TPE, 1 PAIR TWISTED SHIELDED
W8203 |  | 1022941-32 |  | TPE, 1 PAIR TWISTED SHIELDED
W8264 |  | 1022941-22 |  | TPE, 1 PAIR TWISTED SHIELDED
W8301 |  | 1022941-32 |  | TPE, 1 PAIR TWISTED SHIELDED
WC0001 |  | 1302073-36 |  | CABLE, ETHERNET - 36 INCHES
WC0003 |  | 1305733-1 |  | CABLE, COMMUNICATION CABLE - ETHERNET
WC0005 |  | 1302073-36 |  | CABLE, ETHERNET - 36 INCHES
WC0006 |  | 1302073-36 |  | CABLE, ETHERNET - 36 INCHES
WC0007 |  | 1302073-36 |  | CABLE, ETHERNET - 36 INCHES
WC0008 |  | 1302073-36 |  | CABLE, ETHERNET - 36 INCHES
WC0009 |  | 1302073-36 |  | CABLE, ETHERNET - 36 INCHES
WC0012 |  | 1302073-36 |  | CABLE, ETHERNET - 36 INCHES
WC0019 |  | 1302073-36 |  | CABLE, ETHERNET - 36 INCHES
WC0045 |  | 1302073-36 |  | CABLE, ETHERNET - 36 INCHES
WC0114 |  | 1302073-36 |  | CABLE, ETHERNET - 36 INCHES
WC0122 |  | 1302073-36 |  | CABLE, ETHERNET - 36 INCHES
WC0609 |  | 1040131-3 |  | CABLE, ETHERNET COMMUNICATION CABLE
WC0680 |  | 1302073-36 |  | CABLE
WC4190 |  | 1022941-12 |  | TPE, 1 PAIR TWISTED SHIELDED
WC4191 |  | 1022941-12 |  | TPE, 1 PAIR TWISTED SHIELDED
WC4681 |  | 1022941-12 |  | TPE, 1 PAIR TWISTED SHIELDED
WC4682 |  | 1022941-12 |  | TPE, 1 PAIR TWISTED SHIELDED
WC5540 |  | PART OF 1113568-200 |  | CABLE, 2 CONDUCTOR TRIMMED SHIELD PART OF HORN
WC8008 |  | 1022941-22 |  | TPE, 1 PAIR TWISTED SHIELDED
WC8009 |  | 1022941-22 |  | TPE, 1 PAIR TWISTED SHIELDED
WC8010 |  | 1022941-22 |  | TPE, 1 PAIR TWISTED SHIELDED
WC8061 |  | 1046415-40 |  | CABLE, CGCM REDUNDANT INTERFACE
WI0554 |  | 1022941-12 |  | TPE, 1 PAIR TWISTED SHIELDED
WI0556 |  | 1022941-12 |  | TPE, 1 PAIR TWISTED SHIELDED
WI0557 |  | 1022941-12 |  | TPE, 1 PAIR TWISTED SHIELDED
WI0560 |  | 1022941-12 |  | TPE, 1 PAIR TWISTED SHIELDED
WI0561 |  | 1022941-12 |  | TPE, 1 PAIR TWISTED SHIELDED
WI0562 |  | 1022941-12 |  | TPE, 1 PAIR TWISTED SHIELDED
WI0563 |  | 1022941-12 |  | TPE, 1 PAIR TWISTED SHIELDED
WI0565 |  | 1022941-12 |  | TPE, 1 PAIR TWISTED SHIELDED
WI0640 |  | 1022941-12 |  | TPE, 1 PAIR TWISTED SHIELDED
WI0641 |  | 1022941-12 |  | TPE, 1 PAIR TWISTED SHIELDED
WI0642 |  | 1022941-12 |  | TPE, 1 PAIR TWISTED SHIELDED
WI0650 |  | 1022941-12 |  | TPE, 1 PAIR TWISTED SHIELDED
WI0680 |  | 1022941-12 |  | TPE, 1 PAIR TWISTED SHIELDED
WI0681 |  | 1022941-12 |  | TPE, 1 PAIR TWISTED SHIELDED
WI0682 |  | 1022941-12 |  | TPE, 1 PAIR TWISTED SHIELDED
WI0683 |  | 1022941-12 |  | TPE, 1 PAIR TWISTED SHIELDED
WI0684 |  | 1022941-12 |  | TPE, 1 PAIR TWISTED SHIELDED
WI0685 |  | 1022941-12 |  | TPE, 1 PAIR TWISTED SHIELDED
WI0686 |  | 1022941-13 |  | TPE, 1 TRIAD TWISTED SHIELDED
WI0722 |  | 1022941-12 |  | TPE, 1 PAIR TWISTED SHIELDED
WI0723 |  | 1022941-12 |  | TPE, 1 PAIR TWISTED SHIELDED
WI0730 |  | 1022941-12 |  | TPE, 1 PAIR TWISTED SHIELDED
WI0731 |  | 1022941-12 |  | TPE, 1 PAIR TWISTED SHIELDED
WI0732 |  | 1022941-12 |  | TPE, 1 PAIR TWISTED SHIELDED
WI0733 |  | 1022941-12 |  | TPE, 1 PAIR TWISTED SHIELDED
WI0734 |  | 1022941-12 |  | TPE, 1 PAIR TWISTED SHIELDED
WI0735 |  | 1022941-12 |  | TPE, 1 PAIR TWISTED SHIELDED
WI0736 |  | 1022941-13 |  | TPE, 1 TRIAD TWISTED SHIELDED
WI0746 |  | 1022941-12 |  | TPE, 1 PAIR TWISTED SHIELDED
WI0747 |  | 1022941-12 |  | TPE, 1 PAIR TWISTED SHIELDED
WI0750 |  | 1022941-12 |  | TPE, 1 PAIR TWISTED SHIELDED
WI0751 |  | 1022941-12 |  | TPE, 1 PAIR TWISTED SHIELDED
WI0752 |  | 1022941-12 |  | TPE, 1 PAIR TWISTED SHIELDED
WI0753 |  | 1022941-12 |  | TPE, 1 PAIR TWISTED SHIELDED
WI0813A |  | 1022941-12 |  | TPE, 1 PAIR TWISTED SHIELDED
WI0814A |  | 1022941-12 |  | TPE, 1 PAIR TWISTED SHIELDED
WI0814B |  | 1022941-12 |  | TPE, 1 PAIR TWISTED SHIELDED
WI0816A |  | 1022941-12 |  | TPE, 1 PAIR TWISTED SHIELDED
WI0820 |  | 1022941-12 |  | TPE, 1 PAIR TWISTED SHIELDED
WI0821 |  | 1022941-12 |  | TPE, 1 PAIR TWISTED SHIELDED
WI0826A |  | 1022941-12 |  | TPE, 1 PAIR TWISTED SHIELDED
WI0826B |  | 1022941-12 |  | TPE, 1 PAIR TWISTED SHIELDED
WI0831 |  | 1022941-13 |  | TPE, 1 TRIAD TWISTED SHIELDED
WI0832 |  | 1022941-13 |  | TPE, 1 TRIAD TWISTED SHIELDED
WI0833 |  | 1022941-13 |  | TPE, 1 TRIAD TWISTED SHIELDED
WI0834 |  | 1022941-13 |  | TPE, 1 TRIAD TWISTED SHIELDED
WI0835 |  | 1022941-13 |  | TPE, 1 TRIAD TWISTED SHIELDED
WI0836 |  | 1022941-13 |  | TPE, 1 TRIAD TWISTED SHIELDED
WI0837 |  | 1022941-13 |  | TPE, 1 TRIAD TWISTED SHIELDED
WI0840 |  | 1022941-13 |  | TPE, 1 TRIAD TWISTED SHIELDED
WI0841 |  | 1022941-13 |  | TPE, 1 TRIAD TWISTED SHIELDED
WI0842 |  | 1022941-13 |  | TPE, 1 TRIAD TWISTED SHIELDED
WI0843 |  | 1022941-13 |  | TPE, 1 TRIAD TWISTED SHIELDED
WI0844 |  | 1022941-13 |  | TPE, 1 TRIAD TWISTED SHIELDED
WI0845 |  | 1022941-13 |  | TPE, 1 TRIAD TWISTED SHIELDED
WI0846 |  | 1022941-13 |  | TPE, 1 TRIAD TWISTED SHIELDED
WI0852 |  | 1022941-12 |  | TPE, 1 PAIR TWISTED SHIELDED
WI0853 |  | 1022941-12 |  | TPE, 1 PAIR TWISTED SHIELDED
WI0854 |  | 1022941-12 |  | TPE, 1 PAIR TWISTED SHIELDED
WI0855 |  | 1022941-12 |  | TPE, 1 PAIR TWISTED SHIELDED
WI0856 |  | 1022941-12 |  | TPE, 1 PAIR TWISTED SHIELDED
WI0861 |  | 1022941-12 |  | TPE, 1 PAIR TWISTED SHIELDED
WI0863 |  | 1022941-12 |  | TPE, 1 PAIR TWISTED SHIELDED
WI0864 |  | 1022941-12 |  | TPE, 1 PAIR TWISTED SHIELDED
WI0876A |  | 1022941-12 |  | TPE, 1 PAIR TWISTED SHIELDED
WI0910 |  | 1022941-12 |  | TPE, 1 PAIR TWISTED SHIELDED
WI0913 |  | 1022941-12 |  | TPE, 1 PAIR TWISTED SHIELDED
WI091E |  | 1022941-12 |  | TPE, 1 PAIR TWISTED SHIELDED
WI091F |  | 1022941-12 |  | TPE, 1 PAIR TWISTED SHIELDED
WI3200A |  | 1022941-12 |  | TPE, 1 PAIR TWISTED SHIELDED
WI3200B |  | 1022941-12 |  | TPE, 1 PAIR TWISTED SHIELDED
WI4501 |  | 1022941-12 |  | TPE, 1 PAIR TWISTED SHIELDED
WI6161 |  | 1022941-13 |  | TPE, 1 TRIAD TWISTED SHIELDED
WI6163 |  | 1022941-13 |  | TPE, 1 TRIAD TWISTED SHIELDED
WI6171 |  | 1022941-13 |  | TPE, 1 TRIAD TWISTED SHIELDED
WI6172 |  | 1022941-13 |  | TPE, 1 TRIAD TWISTED SHIELDED
WI6173 |  | 1022941-13 |  | TPE, 1 TRIAD TWISTED SHIELDED
WI6174 |  | 1022941-13 |  | TPE, 1 TRIAD TWISTED SHIELDED
WI6181 |  | 1022941-13 |  | TPE, 1 TRIAD TWISTED SHIELDED
WI6182 |  | 1022941-13 |  | TPE, 1 TRIAD TWISTED SHIELDED
WI6211 |  | 1022941-13 |  | TPE, 1 TRIAD TWISTED SHIELDED
WI6213 |  | 1022941-13 |  | TPE, 1 TRIAD TWISTED SHIELDED
WI6224 |  | 1022941-12 |  | TPE, 1 PAIR TWISTED SHIELDED
WI6241 |  | 1022941-13 |  | TPE, 1 TRIAD TWISTED SHIELDED
WI6242 |  | 1022941-13 |  | TPE, 1 TRIAD TWISTED SHIELDED
WI6243 |  | 1022941-13 |  | TPE, 1 TRIAD TWISTED SHIELDED
WI6244 |  | 1022941-13 |  | TPE, 1 TRIAD TWISTED SHIELDED

## Part Number List
Part Number List |  | SolarTools ver. 24.0.84.26264 (Jun 3, 2025)
Project # | G9440
Report date: 7/10/2025 2:58 PM
Project Name | NOC AL SHAHEEN T130
Revision | A.5
Controls DE | G. Colby
Phone:
Controls ME | R. Duran
Phone:
Device ID | Part Number | Description | Location
GR9121 | 903849C1 | RAIL GROUND, DIN RAIL GROUNDING | 1 BAY BACK WALL
GR9122 | 903849C1 | RAIL GROUND, DIN RAIL GROUNDING | 1 BAY BACK WALL
GR9123 | 903849C1 | RAIL GROUND, DIN RAIL GROUNDING | 1 BAY BACK WALL
KA0135 | 1061979-1 | RELAY, AC PRE/POST PUMP DRIVE | 1 BAY BACK WALL
KA121A | 1061979-1 | RELAY, 90% SPEED | 1 BAY BACK WALL
KA121C | 1061979-1 | RELAY, DRIVER MAIN LIQUID^FUEL PUMP | 1 BAY BACK WALL
KA3103 | 1061979-1 | RELAY, LUBE OIL TANK HEATER | 1 BAY BACK WALL
KA3420 | 1061979-1 | RELAY, GENERATOR JACKING OIL | 1 BAY BACK WALL
KA4100 | 1061979-1 | RELAY, GENERATOR HEATER^DISABLED | 1 BAY BACK WALL
KA6211 | 1061979-1 | RELAY, DRIVER ENCLOSURE^VENT FAN #1 | 1 BAY BACK WALL
KA6212 | 1061979-1 | RELAY, DRIVER ENCLOSURE^VENT FAN #2 | 1 BAY BACK WALL
RS0106 | 969787C1 | RESISTIVE SHUNT, EXCITER FIELD CURRENT REGULATOR | 1 BAY BACK WALL
VD0121 | 1013487 | DIODE | 1 BAY BACK WALL
VD0122 | 1013487 | DIODE | 1 BAY BACK WALL
VD0123 | 1013487 | DIODE | 1 BAY BACK WALL
VD0124 | 1013487 | DIODE | 1 BAY BACK WALL
XT0106 | 1066730-7,1066730-8,1067996-4 | TERMINAL BLOCK, SPRING, 4 CONDUCTOR,30-12 AWG (0.05-3.31 MM2),NON-IS | 1 BAY BACK WALL
XT-9103 | 1066730-7,1066730-8,1067996-4 | TERMINAL BLOCK, SPRING, 4 CONDUCTOR,30-12 AWG (0.05-3.31 MM2),NON-IS | 1 BAY BACK WALL
XT-9104 | 1066730-7,1066730-8,1067996-4 | TERMINAL BLOCK, SPRING, 4 CONDUCTOR,30-12 AWG (0.05-3.31 MM2),NON-IS | 1 BAY BACK WALL
XT-9105 | 1074259-1 | TERMINAL STRIP, IS, 2 CONDUCTOR | 1 BAY BACK WALL
XT-9106 | 1066730-16,1067996-18 | TERMINAL STRIP, 2 CONDUCTOR | 1 BAY BACK WALL
XT-9107 | 1074259-1 | TERMINAL BLOCK, SPRING, 4 CONDUCTOR,30-12 AWG (0.05-3.31 MM2),NON-IS | 1 BAY BACK WALL
XT-9110 | 1066730-7,1067996-4 | TERMINAL BLOCK, SPRING, 4 CONDUCTOR,30-12 AWG (0.05-3.31 MM2),NON-IS | 1 BAY BACK WALL
XT-9113 | 1066730-7,1067996-4 | TERMINAL BLOCK, SPRING, 4 CONDUCTOR,30-12 AWG (0.05-3.31 MM2),NON-IS | 1 BAY BACK WALL
XT-9114 | 1074259-1 | TERMINAL STRIP, SYSTEM FUNCTION (USE) | 1 BAY BACK WALL
XT-9115 | 1074259-1 | TERMINAL STRIP, SYSTEM FUNCTION (USE) | 1 BAY BACK WALL
XT-9116 | 1074259-1 | TERMINAL STRIP, SYSTEM FUNCTION (USE) | 1 BAY BACK WALL
XT-9117 | 1074259-1 | TERMINAL STRIP, SYSTEM FUNCTION (USE) | 1 BAY BACK WALL
XT-9118 | 1074259-1 | TERMINAL STRIP, SYSTEM FUNCTION (USE) | 1 BAY BACK WALL
XT-9120 | 1074259-1 | TERMINAL STRIP, SYSTEM FUNCTION (USE) | 1 BAY BACK WALL
XT-9127 | 1066730-16,1066730-17,1066730-18,1067996-40 | TERMINAL STRIP, 2 CONDUCTOR | 1 BAY BACK WALL
XT-9150 | 1074259-1 | TERMINAL STRIP, SYSTEM FUNCTION (USE) | 1 BAY BACK WALL
AT0140 | 2769310-1,2769310-4 | MODULE, DECS-250 | 1 BAY LEFT WALL
AT0220 | 2769310-1,2769310-4 | MODULE, DECS-250 | 1 BAY LEFT WALL
GR9111 | 903849C1 | RAIL GROUND, DIN RAIL GROUNDING | 1 BAY LEFT WALL
GR9112 | 903849C1 | RAIL GROUND, DIN RAIL GROUNDING | 1 BAY LEFT WALL
KA0364 | 1031741-4 | RELAY, SYNCHRONIZATION CHECK | 1 BAY LEFT WALL
XT0340 | 1066730-7,1066730-8,1067996-4 | TERMINAL BLOCK, SPRING, 4 CONDUCTOR,30-12 AWG (0.05-3.31 MM2),NON-IS | 1 BAY LEFT WALL
XT0341 | 1066730-7,1066730-8,1067996-4,1067996-82 | TERMINAL BLOCK, SPRING, 4 CONDUCTOR,30-12 AWG (0.05-3.31 MM2),NON-IS | 1 BAY LEFT WALL
XT0342 | 1066730-7,1066730-8,1067996-4 | TERMINAL BLOCK, SPRING, 4 CONDUCTOR,30-12 AWG (0.05-3.31 MM2),NON-IS | 1 BAY LEFT WALL
XT0343 | 1066730-7,1066730-8,1067996-4 | TERMINAL BLOCK, SPRING, 4 CONDUCTOR,30-12 AWG (0.05-3.31 MM2),NON-IS | 1 BAY LEFT WALL
XT0930 | 1066730-7,1066730-8,1067996-4 | TERMINAL BLOCK, SPRING, 4 CONDUCTOR,30-12 AWG (0.05-3.31 MM2),NON-IS | 1 BAY LEFT WALL
XT-9390 | 1074259-1 | TERMINAL BLOCK, SPRING, 4 CONDUCTOR,30-12 AWG (0.05-3.31 MM2),NON-IS | 1 BAY LEFT WALL
AF0121 | 2684693-17,2684693-24 | 5094-OB16XT, 16 DISCRETE OUTPUT | 1 BAY RIGHT WALL
AF0122 | 2684693-17,2684693-23 | 5094-IB16XT, 16 DISCRETE INPUT | 1 BAY RIGHT WALL
AF0123 | 2684693-19,2684693-33 | 5094-IY8XT, 8 ANALOG INPUT, TC/RTD/ I&V | 1 BAY RIGHT WALL
AU0120 | 2684693-22 | 5094-AENTRXT, FLEX 5000 I/O | 1 BAY RIGHT WALL
FU0031 | 1043265-1,1043265-9 | FUSE, 30A | 1 BAY RIGHT WALL
FU0032 | 1043265-1,1043265-9 | FUSE, 30A | 1 BAY RIGHT WALL
FU0120 | 1043265-1,1043265-5 | FUSE, 10A | 1 BAY RIGHT WALL
FU0121 | 1043265-1,1043265-5 | FUSE, 10A | 1 BAY RIGHT WALL
FU0313 | 1043265-1,1043265-7 | FUSE, 20A | 1 BAY RIGHT WALL
FU0314 | 1043265-1,1043265-7 | FUSE, 20A | 1 BAY RIGHT WALL
FU0321 | 1043265-1,1043265-7 | FUSE, 20A | 1 BAY RIGHT WALL
FU0322 | 1043265-1,1043265-7 | FUSE, 20A | 1 BAY RIGHT WALL
FU0332 | 1043265-1,1043265-7 | FUSE, 20A | 1 BAY RIGHT WALL
FU0333 | 1043265-1,1043265-4 | FUSE, 5A | 1 BAY RIGHT WALL
FU0334 | 1043265-1,1043265-4 | FUSE, 5A | 1 BAY RIGHT WALL
FU0335 | 1043265-1,1043265-4 | FUSE, 5A | 1 BAY RIGHT WALL
GR8131 | 903849C1 | RAIL GROUND, DIN RAIL GROUNDING | 1 BAY RIGHT WALL
GR9131 | 903849C1 | RAIL GROUND, DIN RAIL GROUNDING | 1 BAY RIGHT WALL
GR9132 | 903849C1 | RAIL GROUND, DIN RAIL GROUNDING | 1 BAY RIGHT WALL
GR9133 | 903849C1 | RAIL GROUND, DIN RAIL GROUNDING | 1 BAY RIGHT WALL
IEG8130 | 232941-200 | BUS BAR, 1-BAY (PANEL NO.3) - INST. EARTH GROUNDING | 1 BAY RIGHT WALL
KA0121 | 1061979-1 | RELAY, AUTOMATIC CLOSE CIRCUIT BREAKER | 1 BAY RIGHT WALL
KA0123 | 1061979-1 | RELAY, CGCM #1 ENABLED | 1 BAY RIGHT WALL
KA0124 | 1119193-1 | RELAY, EXCITER OUTPUT #1 | 1 BAY RIGHT WALL
KA0125 | 1119193-1 | RELAY, EXCITER OUTPUT #2 | 1 BAY RIGHT WALL
KA0126 | 1061979-1 | RELAY, CGCM #2 ENABLED | 1 BAY RIGHT WALL
KA0128 | 1061979-1 | RELAY, GENERATOR TRIP SUMMARY CIRCUIT BREAKER | 1 BAY RIGHT WALL
KA0310 | 1061979-1 | RELAY, CGCM #1 FAULT | 1 BAY RIGHT WALL
KA0313 | 1076251-1,1076251-2 | RELAY, PMG INPUT #1 | 1 BAY RIGHT WALL
KA0314 | 1076251-1,1076251-2 | RELAY, PMG INPUT #1 | 1 BAY RIGHT WALL
KA0320 | 1061979-1 | RELAY, CGCM #2 FAULT | 1 BAY RIGHT WALL
KA0323 | 1076251-1,1076251-2 | RELAY, PMG INPUT #2 | 1 BAY RIGHT WALL
KA0324 | 1076251-1,1076251-2 | RELAY, PMG INPUT #2 | 1 BAY RIGHT WALL
KA0330 | 1061979-1 | RELAY, CLOSED CIRCUIT BREAKER | 1 BAY RIGHT WALL
KA0331 | 1061979-1 | RELAY, MAIN UTILITY BREAKER AUXILIARY CONTACT CLOSED | 1 BAY RIGHT WALL
KA0332 | 1061979-1 | RELAY, CLOSE CONTROL CIRCUIT BREAKER | 1 BAY RIGHT WALL
KA0333 | 1061979-1 | RELAY, TRIP CONTROL CIRCUIT BREAKER | 1 BAY RIGHT WALL
KA0335 | 1061979-1 | RELAY, NO EMERGENCY SHUTDOWN SUMMARY | 1 BAY RIGHT WALL
KA0336 | 1061979-1 | RELAY, CONTROLLER ACTIVE | 1 BAY RIGHT WALL
KA0337 | 1061979-1 | RELAY, NO EMERGENCY SHUTDOWN SUMMARY | 1 BAY RIGHT WALL
KA121B | 1061979-1 | RELAY, PERMISSIVE CLOSE CIRCUIT BREAKER | 1 BAY RIGHT WALL
PEG0130 | 232941-300 | BUS BAR, PANEL A - POWER EARTH GROUNDING | 1 BAY RIGHT WALL
QS0031 | 1126803 | CIRCUIT BREAKER, DOUBLE POLE - RAIL MOUNTABLE | 1 BAY RIGHT WALL
QS0131 | 1126803 | CIRCUIT BREAKER, DOUBLE POLE - RAIL MOUNTABLE | 1 BAY RIGHT WALL
RR0851 | 981090C1 | RESISTOR, 3.01K OHM | 1 BAY RIGHT WALL
RR0852 | 981089C1 | RESISTOR, 1.0K OHM | 1 BAY RIGHT WALL
UJ0031 | 1286570-1 | POWER CONVERTER, AC/DC INPUT TO 28V DC OUTPUT | 1 BAY RIGHT WALL
UJ0131 | 1286570-1 | POWER CONVERTER, AC/DC INPUT TO 28V DC OUTPUT | 1 BAY RIGHT WALL
XT0031 | 1066730-16,1066730-17,1066730-18 | TERMINAL STRIP, 2 CONDUCTOR | 1 BAY RIGHT WALL
XT0032 | 1066730-16,1066730-17,1066730-18 | TERMINAL STRIP, 2 CONDUCTOR | 1 BAY RIGHT WALL
XT0085 | 1066730-7,1066730-8,1067996-4 | TERMINAL BLOCK, SPRING, 4 CONDUCTOR,30-12 AWG (0.05-3.31 MM2),NON-IS | 1 BAY RIGHT WALL
XT0120 | 1066730-7,1067996-4 | TERMINAL BLOCK, SPRING, 4 CONDUCTOR,30-12 AWG (0.05-3.31 MM2),NON-IS | 1 BAY RIGHT WALL
XT0124 | 1066730-7 | TERMINAL BLOCK, SPRING, 4 CONDUCTOR,30-12 AWG (0.05-3.31 MM2),NON-IS | 1 BAY RIGHT WALL
XT0130 | 1066730-7,1067996-53 | TERMINAL BLOCK, SPRING, 4 CONDUCTOR,30-12 AWG (0.05-3.31 MM2),NON-IS | 1 BAY RIGHT WALL
XT0313 | 1066730-7 | TERMINAL BLOCK, SPRING, 4 CONDUCTOR,30-12 AWG (0.05-3.31 MM2),NON-IS | 1 BAY RIGHT WALL
XT0332 | 1066730-7,1067996-4 | TERMINAL BLOCK, SPRING, 4 CONDUCTOR,30-12 AWG (0.05-3.31 MM2),NON-IS | 1 BAY RIGHT WALL
XT0334 | 1066730-7,1067996-4 | TERMINAL BLOCK, SPRING, 4 CONDUCTOR,30-12 AWG (0.05-3.31 MM2),NON-IS | 1 BAY RIGHT WALL
XT0335 | 1066730-7,1067996-4 | TERMINAL BLOCK, SPRING, 4 CONDUCTOR,30-12 AWG (0.05-3.31 MM2),NON-IS | 1 BAY RIGHT WALL
XT0336 | 1066730-7,1067996-4 | TERMINAL BLOCK, SPRING, 4 CONDUCTOR,30-12 AWG (0.05-3.31 MM2),NON-IS | 1 BAY RIGHT WALL
XT0337 | 1066730-7,1067996-4 | TERMINAL BLOCK, SPRING, 4 CONDUCTOR,30-12 AWG (0.05-3.31 MM2),NON-IS | 1 BAY RIGHT WALL
XT0360 | 1066730-7,1066730-8,1067996-4 | TERMINAL BLOCK, SPRING, 4 CONDUCTOR,30-12 AWG (0.05-3.31 MM2),NON-IS | 1 BAY RIGHT WALL
XT-QS0031 | 1066730-16,1066730-17,1066730-18 | TERMINAL STRIP, 2 CONDUCTOR | 1 BAY RIGHT WALL
XT-QS0131 | 1066730-16,1066730-17,1066730-18 | TERMINAL STRIP, 2 CONDUCTOR | 1 BAY RIGHT WALL
GR9221 | 903849C1 | RAIL GROUND, DIN RAIL GROUNDING | 2 BAY BACK LEFT WALL
GR9222 | 903849C1 | RAIL GROUND, DIN RAIL GROUNDING | 2 BAY BACK LEFT WALL
GR9223 | 903849C1 | RAIL GROUND, DIN RAIL GROUNDING | 2 BAY BACK LEFT WALL
GR9224 | 903849C1 | RAIL GROUND, DIN RAIL GROUNDING | 2 BAY BACK LEFT WALL
HIEG8220 | 232941-200 | BUS BAR, 2-BAY (PANEL NO.2) - I.S. INST. EARTH GROUNDING | 2 BAY BACK LEFT WALL
IEG8220 | 232941-200 | BUS BAR, 2-BAY (PANEL NO.2) - INST. EARTH GROUNDING | 2 BAY BACK LEFT WALL
UAI1520 | 1105411-5 | ISOLATOR, BAM 2 | 2 BAY BACK LEFT WALL
UAI9210-1 | 1053038-55 | ISOLATOR, 4-20mA ANALOG SIGNAL | 2 BAY BACK LEFT WALL
UAI9210-2 | 1053038-55 | ISOLATOR, SMART TRANSMITTER POWER SUPPLY | 2 BAY BACK LEFT WALL
UAI9210-3 | 1053038-26,1053038-55 | ISOLATOR, SMART TRANSMITTER POWER SUPPLY | 2 BAY BACK LEFT WALL
UAI9210-4 | 1053038-55 | ISOLATOR, SMART TRANSMITTER POWER SUPPLY | 2 BAY BACK LEFT WALL
UAI9210-5 | 1053038-55 | ISOLATOR, SMART TRANSMITTER POWER SUPPLY | 2 BAY BACK LEFT WALL
UAI9210-6 | 1053038-55 | ISOLATOR, SMART TRANSMITTER POWER SUPPLY | 2 BAY BACK LEFT WALL
UAI9210-7 | 1053038-55 | ISOLATOR, SMART TRANSMITTER POWER SUPPLY | 2 BAY BACK LEFT WALL
UAI9211-1 | 1053038-55 | ISOLATOR, SMART TRANSMITTER POWER SUPPLY | 2 BAY BACK LEFT WALL
UAI9212-1 | 1053038-55 | ISOLATOR, SMART TRANSMITTER POWER SUPPLY | 2 BAY BACK LEFT WALL
UAI9212-2 | 1053038-55 | ISOLATOR, SMART TRANSMITTER POWER SUPPLY | 2 BAY BACK LEFT WALL
UAI9214-1 | 1053038-28 | ISOLATOR, DISCRETE INPUT SIGNAL | 2 BAY BACK LEFT WALL
UAI9214-3 | 1053038-28 | ISOLATOR, DISCRETE INPUT SIGNAL | 2 BAY BACK LEFT WALL
UAI9215-1 | 1053038-28 | ISOLATOR, DISCRETE INPUT SIGNAL | 2 BAY BACK LEFT WALL
UAI9216-1 | 1053038-28 | ISOLATOR, DISCRETE INPUT SIGNAL | 2 BAY BACK LEFT WALL
UAI9216-3 | 1053038-28 | ISOLATOR, DISCRETE INPUT SIGNAL | 2 BAY BACK LEFT WALL
UAI9217-1 | 1053038-55 | ISOLATOR, SMART TRANSMITTER POWER SUPPLY | 2 BAY BACK LEFT WALL
UAI9217-2 | 1053038-55 | ISOLATOR, SMART TRANSMITTER POWER SUPPLY | 2 BAY BACK LEFT WALL
UAI9217-5 | 1053038-55 | ISOLATOR, SMART TRANSMITTER POWER SUPPLY | 2 BAY BACK LEFT WALL
UAI9217-6 | 1053038-55 | ISOLATOR, SMART TRANSMITTER POWER SUPPLY | 2 BAY BACK LEFT WALL
UAI9217-7 | 1053038-55 | ISOLATOR, 4-20mA ANALOG SIGNAL | 2 BAY BACK LEFT WALL
UAI9218-6 | 1053038-55 | ISOLATOR, SMART TRANSMITTER POWER SUPPLY | 2 BAY BACK LEFT WALL
UAI9218-7 | 1053038-55 | ISOLATOR, SMART TRANSMITTER POWER SUPPLY | 2 BAY BACK LEFT WALL
UAI9219-1 | 1053038-55 | ISOLATOR, SMART TRANSMITTER POWER SUPPLY | 2 BAY BACK LEFT WALL
UAI9219A-1 | 1053038-55 | ISOLATOR, SMART TRANSMITTER POWER SUPPLY | 2 BAY BACK LEFT WALL
UAI9220-1 | 1053038-28 | ISOLATOR, DISCRETE INPUT SIGNAL | 2 BAY BACK LEFT WALL
UAI9221-1 | 1106298-11 | ISOLATOR, RESISTIVE TEMPERATURE DEVICE | 2 BAY BACK LEFT WALL
UAI9221-2 | 1106298-11 | ISOLATOR, RESISTIVE TEMPERATURE DEVICE | 2 BAY BACK LEFT WALL
UAI9221-3 | 1106298-11 | ISOLATOR, RESISTIVE TEMPERATURE DEVICE | 2 BAY BACK LEFT WALL
UAI9221-4 | 1106298-11 | ISOLATOR, RESISTIVE TEMPERATURE DEVICE | 2 BAY BACK LEFT WALL
UAI9221-5 | 1106298-11 | ISOLATOR, RESISTIVE TEMPERATURE DEVICE | 2 BAY BACK LEFT WALL
UAI9221A-1 | 1106298-11 | ISOLATOR, RESISTIVE TEMPERATURE DEVICE | 2 BAY BACK LEFT WALL
UAI9222-1 | 1053038-28 | ISOLATOR, DISCRETE INPUT SIGNAL | 2 BAY BACK LEFT WALL
UAI9222A-1 | 1106298-11 | ISOLATOR, RESISTIVE TEMPERATURE DEVICE | 2 BAY BACK LEFT WALL
UAI9223-1 | 1053038-18 | ISOLATOR, VOLTAGE REPEATER | 2 BAY BACK LEFT WALL
UAI9223-2 | 1053038-18 | ISOLATOR, VOLTAGE REPEATER | 2 BAY BACK LEFT WALL
UAI9223-3 | 1053038-18 | ISOLATOR, VOLTAGE REPEATER | 2 BAY BACK LEFT WALL
UAI9223-4 | 1053038-18 | ISOLATOR, VOLTAGE REPEATER | 2 BAY BACK LEFT WALL
UAI9223-5 | 1053038-18 | ISOLATOR, VOLTAGE REPEATER | 2 BAY BACK LEFT WALL
UAI9223A-1 | 1053038-10 | ISOLATOR, VOLTAGE REPEATER | 2 BAY BACK LEFT WALL
UAI9242-1 | 1053038-55 | ISOLATOR, SMART TRANSMITTER POWER SUPPLY | 2 BAY BACK LEFT WALL
UAI9270-1 | 1053038-28 | ISOLATOR, DISCRETE INPUT SIGNAL | 2 BAY BACK LEFT WALL
UAI9271-1 | 1053038-28 | ISOLATOR, DISCRETE INPUT SIGNAL | 2 BAY BACK LEFT WALL
UAI9290-1 | 1053038-55 | ISOLATOR, 4-20mA ANALOG SIGNAL | 2 BAY BACK LEFT WALL
UAI9290-2 | 1053038-55 | ISOLATOR, 4-20mA ANALOG SIGNAL | 2 BAY BACK LEFT WALL
UAI9290-3 | 1053038-55 | ISOLATOR, SMART TRANSMITTER POWER SUPPLY | 2 BAY BACK LEFT WALL
UAI9290-4 | 1053038-55 | ISOLATOR, SMART TRANSMITTER POWER SUPPLY | 2 BAY BACK LEFT WALL
UAI9290-5 | 1053038-55 | ISOLATOR, 4-20mA ANALOG SIGNAL | 2 BAY BACK LEFT WALL
UAI9290-6 | 1053038-55 | ISOLATOR, SMART TRANSMITTER POWER SUPPLY | 2 BAY BACK LEFT WALL
UAI9290-7 | 1053038-55 | ISOLATOR, SMART TRANSMITTER POWER SUPPLY | 2 BAY BACK LEFT WALL
UAI9291-1 | 1053038-28 | ISOLATOR, DISCRETE INPUT SIGNAL | 2 BAY BACK LEFT WALL
UV0281 | 1053038-19 | POWER FEED MODULE, INTRINSIC SAFETY | 2 BAY BACK LEFT WALL
UV0282 | 1053038-19 | POWER FEED MODULE, INTRINSIC SAFETY | 2 BAY BACK LEFT WALL
UV0291 | 1053038-19 | POWER FEED MODULE, INTRINSIC SAFETY | 2 BAY BACK LEFT WALL
UV0292 | 1053038-19 | POWER FEED MODULE, INTRINSIC SAFETY | 2 BAY BACK LEFT WALL
XT-9210 | 1074259-2 | TERMINAL STRIP, IS, 2 CONDUCTOR | 2 BAY BACK LEFT WALL
XT-9211 | 1074259-2 | TERMINAL STRIP, IS, 2 CONDUCTOR | 2 BAY BACK LEFT WALL
XT-9212 | 1074259-2 | TERMINAL STRIP, IS, 2 CONDUCTOR | 2 BAY BACK LEFT WALL
XT-9214 | 1074259-2 | TERMINAL STRIP, IS, 2 CONDUCTOR | 2 BAY BACK LEFT WALL
XT-9215 | 1074259-2 | TERMINAL STRIP, IS, 2 CONDUCTOR | 2 BAY BACK LEFT WALL
XT-9216 | 1074259-2 | TERMINAL STRIP, IS, 2 CONDUCTOR | 2 BAY BACK LEFT WALL
XT-9217 | 1074259-2 | TERMINAL STRIP, IS, 2 CONDUCTOR | 2 BAY BACK LEFT WALL
XT-9218 | 1074259-2 | TERMINAL STRIP, IS, 2 CONDUCTOR | 2 BAY BACK LEFT WALL
XT-9219 | 1074259-2 | TERMINAL STRIP, IS, 2 CONDUCTOR | 2 BAY BACK LEFT WALL
XT-9219A | 1074259-2 | TERMINAL STRIP, IS, 2 CONDUCTOR | 2 BAY BACK LEFT WALL
XT-9220 | 1074259-2 | TERMINAL STRIP, IS, 2 CONDUCTOR | 2 BAY BACK LEFT WALL
XT-9221 | 1074259-2 | TERMINAL STRIP, IS, 2 CONDUCTOR | 2 BAY BACK LEFT WALL
XT-9221A | 1074259-2 | TERMINAL STRIP, IS, 2 CONDUCTOR | 2 BAY BACK LEFT WALL
XT-9222 | 1074259-2 | TERMINAL STRIP, IS, 2 CONDUCTOR | 2 BAY BACK LEFT WALL
XT-9222A | 1074259-2 | TERMINAL STRIP, IS, 2 CONDUCTOR | 2 BAY BACK LEFT WALL
XT-9223 | 1074259-2 | TERMINAL STRIP, IS, 2 CONDUCTOR | 2 BAY BACK LEFT WALL
XT-9223A | 1074259-2 | TERMINAL STRIP, IS, 2 CONDUCTOR | 2 BAY BACK LEFT WALL
XT-9242 | 1074259-2 | TERMINAL STRIP, IS, 2 CONDUCTOR | 2 BAY BACK LEFT WALL
XT-9270 | 1074259-2 | TERMINAL STRIP, IS, 2 CONDUCTOR | 2 BAY BACK LEFT WALL
XT-9271 | 1074259-2 | TERMINAL STRIP, IS, 2 CONDUCTOR | 2 BAY BACK LEFT WALL
XT-9290 | 1074259-2 | TERMINAL STRIP, IS, 2 CONDUCTOR | 2 BAY BACK LEFT WALL
XT-9291 | 1074259-2 | TERMINAL STRIP, IS, 2 CONDUCTOR | 2 BAY BACK LEFT WALL
AF0081 | 2684693-18,2684693-28 | 5094-IB16SXT, 16 DISCRETE INPUT, S | 2 BAY BACK RIGHT PANEL
AF0082 | 2684693-17,2684693-23 | 5094-IB16XT, 16 DISCRETE INPUT | 2 BAY BACK RIGHT PANEL
AF0083 | 2684693-14,2684693-19,2684693-33 | 5094-IY8XT, 8 ANALOG INPUT, TC/RTD/ I&V | 2 BAY BACK RIGHT PANEL
AF0084 | 2684693-14,2684693-19,2684693-33 | 5094-IY8XT, 8 ANALOG INPUT, TC/RTD/ I&V | 2 BAY BACK RIGHT PANEL
AF0085 | 2684693-18,2684693-26 | 5094-IF8IHXT, 8 ANALOG INPUT, ISOLATED | 2 BAY BACK RIGHT PANEL
AF0086 | 2684693-18,2684693-26 | 5094-IF8IHXT, 8 ANALOG INPUT, ISOLATED | 2 BAY BACK RIGHT PANEL
AF0087 | 2684693-17,2684693-23 | 5094-IB16XT, 16 DISCRETE INPUT | 2 BAY BACK RIGHT PANEL
AF0091 | 2684693-17,2684693-23 | 5094-IB16XT, 16 DISCRETE INPUT | 2 BAY BACK RIGHT PANEL
AF0092 | 2684693-17,2684693-24 | 5094-OB16XT, 16 DISCRETE OUTPUT | 2 BAY BACK RIGHT PANEL
AF0093 | 2684693-17,2684693-24 | 5094-OB16XT, 16 DISCRETE OUTPUT | 2 BAY BACK RIGHT PANEL
AF0094 | 2684693-17,2684693-25 | 5094-OB8XT, 8 DISCRETE OUTPUT | 2 BAY BACK RIGHT PANEL
AF0095 | 2684693-18,2684693-28 | 5094-IB16SXT, 16 DISCRETE INPUT, S | 2 BAY BACK RIGHT PANEL
AP0601 | 1089241-20 | MODULE, BLANK FILLER | 2 BAY BACK RIGHT PANEL
AP0602 | 1089241-45 | 1756-EN4TRXT, ETHERNET | 2 BAY BACK RIGHT PANEL
AP0603 | 1089241-45 | 1756-EN4TRXT, ETHERNET | 2 BAY BACK RIGHT PANEL
AP0604 | 1089241-14 | MVI 56E-MCMXT, MODBUS | 2 BAY BACK RIGHT PANEL
AP0605 | 1089241-15 | MVI 56-MNETXT, ETHERNET/MODBUS | 2 BAY BACK RIGHT PANEL
AP0606 | 1089241-40 | 1756-EN2TRXT, ETHERNET | 2 BAY BACK RIGHT PANEL
AR0600 | 1089241-29 | RACK CHASSIS, 1756-A7XT (7 SLOT) | 2 BAY BACK RIGHT PANEL
AT0600 | 1089241-30,1089241-43 | 1756-L83EXTS, CONTROLLER^GUARDLOGIX | 2 BAY BACK RIGHT PANEL
AU0080 | 2684693-22 | 5094-AENTRXT, FLEX 5000 I/O | 2 BAY BACK RIGHT PANEL
AU0090 | 2684693-22 | 5094-AENTRXT, FLEX 5000 I/O | 2 BAY BACK RIGHT PANEL
FU0080 | 1043265-1,1043265-5 | FUSE, 10A | 2 BAY BACK RIGHT PANEL
FU0081 | 1043265-1,1043265-5 | FUSE, 10A | 2 BAY BACK RIGHT PANEL
FU0082 | 1043265-1,1043265-5 | FUSE, 10A | 2 BAY BACK RIGHT PANEL
FU0090 | 1043265-1,1043265-5 | FUSE, 10A | 2 BAY BACK RIGHT PANEL
FU0091 | 1043265-1,1043265-5 | FUSE, 10A | 2 BAY BACK RIGHT PANEL
FU0092 | 1043265-1,1043265-5 | FUSE, 10A | 2 BAY BACK RIGHT PANEL
FU0093 | 1043265-1,1043265-5 | FUSE, 10A | 2 BAY BACK RIGHT PANEL
GR8231 | 903849C1 | RAIL GROUND, DIN RAIL GROUNDING | 2 BAY BACK RIGHT PANEL
GR8232 | 903849C1 | RAIL GROUND, DIN RAIL GROUNDING | 2 BAY BACK RIGHT PANEL
GR9231 | 903849C1 | RAIL GROUND, DIN RAIL GROUNDING | 2 BAY BACK RIGHT PANEL
GR9232 | 903849C1 | RAIL GROUND, DIN RAIL GROUNDING | 2 BAY BACK RIGHT PANEL
GR9233 | 903849C1 | RAIL GROUND, DIN RAIL GROUNDING | 2 BAY BACK RIGHT PANEL
IEG8230 | 232941-110 | BUS BAR, 2-BAY (PANEL NO.3) - INST. EARTH GROUNDING | 2 BAY BACK RIGHT PANEL
KA0130 | 1061979-1 | RELAY, LOWSPEED/OPEN PROBE SETPOINT | 2 BAY BACK RIGHT PANEL
KA0176 | 1061979-1 | RELAY, VENTILATION REQUIRED | 2 BAY BACK RIGHT PANEL
KA0177 | 1061979-1 | RELAY, VENTILATION REQUIRED | 2 BAY BACK RIGHT PANEL
KA0220 | 1016767 | RELAY, LIQUID FUEL CONTROL VALVE | 2 BAY BACK RIGHT PANEL
KA0221 | 1061979-1 | RELAY, PRIMARY GAS FUEL^SHUTOFF VALVE | 2 BAY BACK RIGHT PANEL
KA0222 | 1061979-1 | RELAY, SECONDARY GAS FUEL^ SHUTOFF VALVE | 2 BAY BACK RIGHT PANEL
KA0224 | 1061979-1 | RELAY, LIQUID FUEL PRIMARY SHUTOFF | 2 BAY BACK RIGHT PANEL
KA0225 | 1061979-1 | RELAY, LIQUID FUEL SECONDARY SHUTOFF | 2 BAY BACK RIGHT PANEL
KA0701 | 1061979-1 | RELAY, ORBIT60 TRIP MULTIPLY | 2 BAY BACK RIGHT PANEL
KA076E | 1061979-1 | RELAY, PURGE FLOW ESTABLISHED | 2 BAY BACK RIGHT PANEL
KA0817 | 1061979-1 | RELAY, TURBINE SHUTDOWN (SCADA) | 2 BAY BACK RIGHT PANEL
KA0870 | 1061979-1 | RELAY, FUEL LINE READY (SCADA) | 2 BAY BACK RIGHT PANEL
KA0871 | 1061979-1 | RELAY, TRANSFER TO LIQUID | 2 BAY BACK RIGHT PANEL
KA0923 | 1061979-1 | RELAY, LIQ. FUEL OPERATION AVAIL. | 2 BAY BACK RIGHT PANEL
KA0924 | 1061979-1 | RELAY, COMMON ALARM (SCADA) | 2 BAY BACK RIGHT PANEL
KA0925 | 1061979-1 | RELAY, GTG IN PMS CONTROL | 2 BAY BACK RIGHT PANEL
KA0927 | 1061979-1 | RELAY, COMMON ALARM (PMS) | 2 BAY BACK RIGHT PANEL
KA0929 | 1061979-1 | RELAY, GAS FUEL SELECTED | 2 BAY BACK RIGHT PANEL
KA0936 | 1061979-1 | RELAY, LIQ. FUEL SELECTED | 2 BAY BACK RIGHT PANEL
KA0937 | 1061979-1 | RELAY, FUEL LINE WARMUP REQ. | 2 BAY BACK RIGHT PANEL
KA0938 | 1061979-1 | RELAY, EMISSION MODE NO.1 | 2 BAY BACK RIGHT PANEL
KA0939 | 1061979-1 | RELAY, EMISSION MODE NO.2 | 2 BAY BACK RIGHT PANEL
KA093A | 1061979-1 | RELAY, NON-NORMAL STOP | 2 BAY BACK RIGHT PANEL
KA0942 | 1061979-1 | RELAY, GAS FUEL ACTIVATED | 2 BAY BACK RIGHT PANEL
KA0943 | 1061979-1 | RELAY, LIQUID FUEL ACTIVATED | 2 BAY BACK RIGHT PANEL
KA0944 | 1061979-1 | RELAY, T5 HIGH ALARM | 2 BAY BACK RIGHT PANEL
KA1020 | 1061979-1 | RELAY, IGNITION START | 2 BAY BACK RIGHT PANEL
KA9982 | 1061979-1 | RELAY, FIRE CONFIRMED | 2 BAY BACK RIGHT PANEL
KA9984 | 1061979-1 | RELAY, GAS CONFIRMED | 2 BAY BACK RIGHT PANEL
UV0600 | 1089241-28 | POWER SUPPLY, RSLOGIX CHASSIS | 2 BAY BACK RIGHT PANEL
VD6211 | 960592C1 | DIODE, 15 pF | 2 BAY BACK RIGHT PANEL
VD6212 | 960592C1 | DIODE, 15 pF | 2 BAY BACK RIGHT PANEL
XT0080 | 1066730-7,1066730-8 | TERMINAL BLOCK, SPRING, 4 CONDUCTOR,30-12 AWG (0.05-3.31 MM2),NON-IS | 2 BAY BACK RIGHT PANEL
XT0090 | 1066730-7,1066730-8 | TERMINAL BLOCK, SPRING, 4 CONDUCTOR,30-12 AWG (0.05-3.31 MM2),NON-IS | 2 BAY BACK RIGHT PANEL
XT0171 | 1066730-7,1066730-8,1067996-11 | TERMINAL BLOCK, SPRING, 4 CONDUCTOR,30-12 AWG (0.05-3.31 MM2),NON-IS | 2 BAY BACK RIGHT PANEL
XT-9300 | 1074259-1 | TERMINAL BLOCK, SPRING, 4 CONDUCTOR,30-12 AWG (0.05-3.31 MM2),NON-IS | 2 BAY BACK RIGHT PANEL
XT-9300A | 1074259-1 | TERMINAL BLOCK, SPRING, 4 CONDUCTOR,30-12 AWG (0.05-3.31 MM2),NON-IS | 2 BAY BACK RIGHT PANEL
XT-9311 | 1074259-1 | TERMINAL BLOCK, SPRING, 4 CONDUCTOR,30-12 AWG (0.05-3.31 MM2),NON-IS | 2 BAY BACK RIGHT PANEL
XT-9312 | 1074259-1 | TERMINAL BLOCK, SPRING, 4 CONDUCTOR,30-12 AWG (0.05-3.31 MM2),NON-IS | 2 BAY BACK RIGHT PANEL
XT-9319 | 1074259-1 | TERMINAL STRIP, SYSTEM FUNCTION (USE) | 2 BAY BACK RIGHT PANEL
XT-9324 | 1074259-1 | TERMINAL BLOCK, SPRING, 4 CONDUCTOR,30-12 AWG (0.05-3.31 MM2),NON-IS | 2 BAY BACK RIGHT PANEL
XT-9325A | 1074259-1 | TERMINAL BLOCK, SPRING, 4 CONDUCTOR,30-12 AWG (0.05-3.31 MM2),NON-IS | 2 BAY BACK RIGHT PANEL
XT-9326 | 1074259-1 | TERMINAL BLOCK, SPRING, 4 CONDUCTOR,30-12 AWG (0.05-3.31 MM2),NON-IS | 2 BAY BACK RIGHT PANEL
XT-9326A | 1074259-1 | TERMINAL BLOCK, SPRING, 4 CONDUCTOR,30-12 AWG (0.05-3.31 MM2),NON-IS | 2 BAY BACK RIGHT PANEL
XT-9327 | 1074259-1 | TERMINAL BLOCK, SPRING, 4 CONDUCTOR,30-12 AWG (0.05-3.31 MM2),NON-IS | 2 BAY BACK RIGHT PANEL
XT-9328 | 1074259-1 | TERMINAL BLOCK, SPRING, 4 CONDUCTOR,30-12 AWG (0.05-3.31 MM2),NON-IS | 2 BAY BACK RIGHT PANEL
XT-9329 | 1074259-1 | TERMINAL BLOCK, SPRING, 4 CONDUCTOR,30-12 AWG (0.05-3.31 MM2),NON-IS | 2 BAY BACK RIGHT PANEL
XT-9330 | 1074259-1 | TERMINAL BLOCK, SPRING, 4 CONDUCTOR,30-12 AWG (0.05-3.31 MM2),NON-IS | 2 BAY BACK RIGHT PANEL
FU0010 | 1043265-1,1043265-5 | FUSE, 10A | 2 BAY LEFT WALL
FU0136 | 1043265-1,1043265-9 | FUSE, 30A | 2 BAY LEFT WALL
FU0137 | 1043265-1,1043265-7 | FUSE, 20A | 2 BAY LEFT WALL
FU0139 | 1043265-1,1043265-4 | FUSE, 5A | 2 BAY LEFT WALL
FU0170 | 1043265-1,1043265-4 | FUSE, 5A | 2 BAY LEFT WALL
FU0210 | 1043265-1,1043265-7 | FUSE, 20A | 2 BAY LEFT WALL
FU0211 | 1043265-1,1043265-4 | FUSE, 5A | 2 BAY LEFT WALL
FU0212 | 1043265-1,1043265-4 | FUSE, 5A | 2 BAY LEFT WALL
FU0271 | 1043265-1,1043265-4 | FUSE, 5A | 2 BAY LEFT WALL
FU0274 | 1043265-1,1043265-4 | FUSE, 5A | 2 BAY LEFT WALL
FU0281 | 1043265-1,1043265-4 | FUSE, 5A | 2 BAY LEFT WALL
FU0291 | 1043265-1,1043265-4 | FUSE, 5A | 2 BAY LEFT WALL
GR9211 | 903849C1 | RAIL GROUND, DIN RAIL GROUNDING | 2 BAY LEFT WALL
GR9212 | 903849C1 | RAIL GROUND, DIN RAIL GROUNDING | 2 BAY LEFT WALL
GR9213 | 903849C1 | RAIL GROUND, DIN RAIL GROUNDING | 2 BAY LEFT WALL
HIEG8210 | 232941-200 | BUS BAR, 2-BAY (PANEL NO.1) - I.S. INST. EARTH GROUNDING | 2 BAY LEFT WALL
IEG8210 | 232941-200 | BUS BAR, 2-BAY (PANEL NO.1) - INST. EARTH GROUNDING | 2 BAY LEFT WALL
KA0131 | 1061979-1 | RELAY, CONTROLLER ACTIVE | 2 BAY LEFT WALL
KA0132 | 1061979-1 | RELAY, CONTROLLER ACTIVE | 2 BAY LEFT WALL
KA0133 | 1061979-1 | RELAY, POST LUBE NOT REQUIRED | 2 BAY LEFT WALL
KA0134 | 1061979-1 | RELAY, BACKUP COMMAND OFF | 2 BAY LEFT WALL
KA0136 | 1061979-1 | RELAY, LUBE OIL HEADER PRESSURE HIGH | 2 BAY LEFT WALL
KA0137 | 1061979-1 | RELAY, LUBE PUMP INHIBIT | 2 BAY LEFT WALL
KA0138 | 1061979-1 | RELAY, BACKUP LUBE OIL PUMP OFF | 2 BAY LEFT WALL
KA0141 | 1061979-1 | RELAY, CONTROLLER ACTIVE | 2 BAY LEFT WALL
KA0144 | 1061979-1 | RELAY, AC PRE/POST PUMP DRIVE | 2 BAY LEFT WALL
KA0231 | 1061979-1 | RELAY, CONTROLLER ACTIVE | 2 BAY LEFT WALL
KA0232 | 1061979-1 | RELAY, CONTROLLER ACTIVE | 2 BAY LEFT WALL
KA0233 | 1061979-1 | RELAY, CONTROLLER ACTIVE | 2 BAY LEFT WALL
KA0234 | 1061979-1 | RELAY, CONTROLLER ACTIVE | 2 BAY LEFT WALL
KA0235 | 1061979-1 | RELAY, NO EMERGENCY SHUTDOWN SUMMARY | 2 BAY LEFT WALL
KA0236 | 1061979-1 | RELAY, NO EMERGENCY SHUTDOWN SUMMARY | 2 BAY LEFT WALL
KA0237 | 1061979-1 | RELAY, NO EMERGENCY SHUTDOWN SUMMARY | 2 BAY LEFT WALL
KA0238 | 1061979-1 | RELAY, NO EMERGENCY SHUTDOWN SUMMARY | 2 BAY LEFT WALL
KA0239 | 1061979-1 | RELAY, NO EMERGENCY SHUTDOWN SUMMARY | 2 BAY LEFT WALL
KA0240 | 1061979-1 | RELAY, NO EMERGENCY SHUTDOWN SUMMARY | 2 BAY LEFT WALL
KA0241 | 1061979-1 | RELAY, BACKUP SYSTEM RESET | 2 BAY LEFT WALL
KA0242 | 1061979-1 | RELAY, BACKUP SYSTEM RESET | 2 BAY LEFT WALL
KA0243 | 1061979-1 | RELAY, NO FIRE DETECTED | 2 BAY LEFT WALL
KA0244 | 1061979-1 | RELAY, NO FIRE DETECTED | 2 BAY LEFT WALL
KA0245 | 1061979-1 | RELAY, NO GAS DETECTED | 2 BAY LEFT WALL
KA0246 | 1061979-1 | RELAY, NO FIRE DETECTED | 2 BAY LEFT WALL
KA0247 | 1061979-1 | RELAY, NO FIRE DETECTED | 2 BAY LEFT WALL
KA0248 | 1061979-1 | RELAY, NO EMERGENCY SHUTDOWN SUMMARY | 2 BAY LEFT WALL
KA0249 | 1061979-1 | RELAY, NO GAS DETECTED | 2 BAY LEFT WALL
KA0250 | 1061979-1 | RELAY, NO EMERGENCY SHUTDOWN SUMMARY | 2 BAY LEFT WALL
KA0621 | 1061979-1 | RELAY, TURBINE RUNNING STATUS | 2 BAY LEFT WALL
KA0622 | 1061979-1 | RELAY, WASTE HEAT READY | 2 BAY LEFT WALL
KA0810 | 1061979-1 | RELAY, IGNITION PERMISSIVE | 2 BAY LEFT WALL
KA0811 | 1061979-1 | RELAY, WHRS FAST-STOP SHUTDOWN | 2 BAY LEFT WALL
KA0822 | 1061979-1 | RELAY, START PERMISSIVE | 2 BAY LEFT WALL
KA0823 | 1061979-1 | RELAY, WHRS ALARM SUMMARY | 2 BAY LEFT WALL
KA0877 | 1061979-1 | RELAY, AUTOMATIC SYNC. INITIATE | 2 BAY LEFT WALL
KA0878 | 1061979-1 | RELAY, START AND AUTO-SYNC | 2 BAY LEFT WALL
KA1820 | 1061979-1 | RELAY, START | 2 BAY LEFT WALL
KA1821 | 1061979-1 | RELAY, NORMAL STOP | 2 BAY LEFT WALL
KT0140 | 2651077-1 | TIMER RELAY, BACKUP PUMP POST LUBE OFF CYCLE | 2 BAY LEFT WALL
KT0141 | 2651077-1 | TIMER RELAY, BACKUP POST LUBE CONTINUOUS | 2 BAY LEFT WALL
KT0142 | 2651077-1 | TIMER RELAY, TOTAL POST LUBE | 2 BAY LEFT WALL
KT0143 | 2651077-1 | TIMER RELAY, BACKUP PUMP POST LUBE ON CYCLE | 2 BAY LEFT WALL
KT0144 | 2651077-1 | TIMER RELAY, HEADER PRESSURE HIGH BACKUP PUMP OFF | 2 BAY LEFT WALL
KT0145 | 2651077-1 | TIMER RELAY, FIRE DETECTED ROLLDOWN LUBE | 2 BAY LEFT WALL
KT0146 | 2651077-3 | TIMER RELAY, WATCHDOG | 2 BAY LEFT WALL
PC0470 | 1025156-1,1025156-2,2271605-1 | TIMER/COUNTER, ENGINE HOUR / START COUNTER | 2 BAY LEFT WALL
PC0471 | 2271605-1 | TIMER/COUNTER, LIQUID FUEL COUNTER HOUR / START | 2 BAY LEFT WALL
UAI9201-1 | 1053038-35 | ISOLATOR, THERMOCOUPLE ELEMENT | 2 BAY LEFT WALL
UAI9201-10 | 1053038-35 | ISOLATOR, THERMOCOUPLE ELEMENT | 2 BAY LEFT WALL
UAI9201-2 | 1053038-35 | ISOLATOR, THERMOCOUPLE ELEMENT | 2 BAY LEFT WALL
UAI9201-3 | 1053038-35 | ISOLATOR, THERMOCOUPLE ELEMENT | 2 BAY LEFT WALL
UAI9201-4 | 1053038-35 | ISOLATOR, THERMOCOUPLE ELEMENT | 2 BAY LEFT WALL
UAI9201-5 | 1053038-35 | ISOLATOR, THERMOCOUPLE ELEMENT | 2 BAY LEFT WALL
UAI9201-6 | 1053038-35 | ISOLATOR, THERMOCOUPLE ELEMENT | 2 BAY LEFT WALL
UAI9201-7 | 1053038-35 | ISOLATOR, THERMOCOUPLE ELEMENT | 2 BAY LEFT WALL
UAI9201-8 | 1053038-35 | ISOLATOR, THERMOCOUPLE ELEMENT | 2 BAY LEFT WALL
UAI9201-9 | 1053038-35 | ISOLATOR, THERMOCOUPLE ELEMENT | 2 BAY LEFT WALL
UAI9202-1 | 1053038-35 | ISOLATOR, THERMOCOUPLE ELEMENT | 2 BAY LEFT WALL
UAI9202-2 | 1053038-35 | ISOLATOR, THERMOCOUPLE ELEMENT | 2 BAY LEFT WALL
UAI9203-1 | 1053038-55 | ISOLATOR, 4-20mA ANALOG SIGNAL | 2 BAY LEFT WALL
UAI9204-1 | 1053038-55 | ISOLATOR, SMART TRANSMITTER POWER SUPPLY | 2 BAY LEFT WALL
UAI9205-1 | 1106298-11 | ISOLATOR, RESISTIVE TEMPERATURE DEVICE | 2 BAY LEFT WALL
UAI9205-2 | 1106298-11,1106298-29 | ISOLATOR, RESISTIVE TEMPERATURE DEVICE | 2 BAY LEFT WALL
UAI9205-3 | 1106298-11,1106298-29 | ISOLATOR, RESISTIVE TEMPERATURE DEVICE | 2 BAY LEFT WALL
UAI9205-4 | 1106298-11,1106298-29 | ISOLATOR, RESISTIVE TEMPERATURE DEVICE | 2 BAY LEFT WALL
UAI9205-5 | 1106298-11,1106298-29 | ISOLATOR, RESISTIVE TEMPERATURE DEVICE | 2 BAY LEFT WALL
UAI9205-6 | 1106298-11,1106298-29 | ISOLATOR, RESISTIVE TEMPERATURE DEVICE | 2 BAY LEFT WALL
UAI9206-1 | 1106298-11 | ISOLATOR, RESISTIVE TEMPERATURE DEVICE | 2 BAY LEFT WALL
UAI9207-1 | 1106298-11,1106298-29 | ISOLATOR, RESISTIVE TEMPERATURE DEVICE | 2 BAY LEFT WALL
UAI9207-2 | 1106298-11,1106298-29 | ISOLATOR, RESISTIVE TEMPERATURE DEVICE | 2 BAY LEFT WALL
UAI9208-1 | 1053038-18 | ISOLATOR, VOLTAGE REPEATER | 2 BAY LEFT WALL
UAI9208-2 | 1053038-18 | ISOLATOR, VOLTAGE REPEATER | 2 BAY LEFT WALL
UAI9208-3 | 1053038-18 | ISOLATOR, VOLTAGE REPEATER | 2 BAY LEFT WALL
UAI9208-4 | 1053038-18 | ISOLATOR, VOLTAGE REPEATER | 2 BAY LEFT WALL
UAI9208-5 | 1053038-18 | ISOLATOR, VOLTAGE REPEATER | 2 BAY LEFT WALL
UAI9208-6 | 1053038-18 | ISOLATOR, VOLTAGE REPEATER | 2 BAY LEFT WALL
UAI9208-7 | 1053038-18 | ISOLATOR, VOLTAGE REPEATER | 2 BAY LEFT WALL
UAI9208-8 | 1053038-18 | ISOLATOR, VOLTAGE REPEATER | 2 BAY LEFT WALL
UAI9209-1 | 1053038-18 | ISOLATOR, VOLTAGE REPEATER | 2 BAY LEFT WALL
UV0271 | 1053038-19 | POWER FEED MODULE, INTRINSIC SAFETY | 2 BAY LEFT WALL
UV0272 | 1053038-19 | POWER FEED MODULE, INTRINSIC SAFETY | 2 BAY LEFT WALL
XT0134 | 1066730-16,1066730-17 | TERMINAL STRIP, 2 CONDUCTOR | 2 BAY LEFT WALL
XT0135 | 1066730-7,1066730-8 | TERMINAL BLOCK, SPRING, 4 CONDUCTOR,30-12 AWG (0.05-3.31 MM2),NON-IS | 2 BAY LEFT WALL
XT0136 | 1066730-7,1066730-8,1067996-82 | TERMINAL BLOCK, SPRING, 4 CONDUCTOR,30-12 AWG (0.05-3.31 MM2),NON-IS | 2 BAY LEFT WALL
XT0138 | 1066730-16,1066730-17 | TERMINAL STRIP, 2 CONDUCTOR | 2 BAY LEFT WALL
XT0139 | 1066730-7,1066730-8 | TERMINAL BLOCK, SPRING, 4 CONDUCTOR,30-12 AWG (0.05-3.31 MM2),NON-IS | 2 BAY LEFT WALL
XT0233 | 1066730-7,1066730-8 | TERMINAL BLOCK, SPRING, 4 CONDUCTOR,30-12 AWG (0.05-3.31 MM2),NON-IS | 2 BAY LEFT WALL
XT0235 | 1066730-7,1066730-8 | TERMINAL BLOCK, SPRING, 4 CONDUCTOR,30-12 AWG (0.05-3.31 MM2),NON-IS | 2 BAY LEFT WALL
XT0237 | 1066730-10,1066730-9,1067996-2,1067996-4,1067996-7 | DIODE TERMINAL STRIP, 4 CONDUCTOR | 2 BAY LEFT WALL
XT0240 | 1066730-7,1066730-8,1067996-4 | TERMINAL BLOCK, SPRING, 4 CONDUCTOR,30-12 AWG (0.05-3.31 MM2),NON-IS | 2 BAY LEFT WALL
XT-9201 | 1074259-2 | TERMINAL STRIP, IS, 2 CONDUCTOR | 2 BAY LEFT WALL
XT-9202 | 1074259-2 | TERMINAL STRIP, IS, 2 CONDUCTOR | 2 BAY LEFT WALL
XT-9203 | 1074259-2 | TERMINAL STRIP, IS, 2 CONDUCTOR | 2 BAY LEFT WALL
XT-9204 | 1074259-2 | TERMINAL STRIP, IS, 2 CONDUCTOR | 2 BAY LEFT WALL
XT-9205 | 1074259-2 | TERMINAL STRIP, IS, 2 CONDUCTOR | 2 BAY LEFT WALL
XT-9206 | 1074259-2 | TERMINAL STRIP, IS, 2 CONDUCTOR | 2 BAY LEFT WALL
XT-9207 | 1074259-2 | TERMINAL STRIP, IS, 2 CONDUCTOR | 2 BAY LEFT WALL
XT-9208 | 1074259-2 | TERMINAL STRIP, IS, 2 CONDUCTOR | 2 BAY LEFT WALL
XT-9209 | 1074259-2 | TERMINAL STRIP, IS, 2 CONDUCTOR | 2 BAY LEFT WALL
AF0051 | 2684693-17,2684693-25 | 5094-OB8XT, 8 DISCRETE OUTPUT | 2 BAY RIGHT WALL
AF0052 | 2684693-17,2684693-25 | 5094-OB8XT, 8 DISCRETE OUTPUT | 2 BAY RIGHT WALL
AF0053 | 2684693-17,2684693-25 | 5094-OB8XT, 8 DISCRETE OUTPUT | 2 BAY RIGHT WALL
AF0054 | 2684693-17,2684693-23 | 5094-IB16XT, 16 DISCRETE INPUT | 2 BAY RIGHT WALL
AF0055 | 2684693-18,2684693-26 | 5094-IF8IHXT, 8 ANALOG INPUT, ISOLATED | 2 BAY RIGHT WALL
AF0056 | 2684693-18,2684693-26 | 5094-IF8IHXT, 8 ANALOG INPUT, ISOLATED | 2 BAY RIGHT WALL
AF0057 | 2684693-18,2684693-27 | 5094-OF8IHXT, 8 ANALOG OUTPUT, ISOLATED | 2 BAY RIGHT WALL
AF0061 | 2684693-17,2684693-25 | 5094-OB8XT, 8 DISCRETE OUTPUT | 2 BAY RIGHT WALL
AF0062 | 2684693-17,2684693-25 | 5094-OB8XT, 8 DISCRETE OUTPUT | 2 BAY RIGHT WALL
AF0063 | 2684693-17,2684693-23 | 5094-IB16XT, 16 DISCRETE INPUT | 2 BAY RIGHT WALL
AF0064 | 2684693-18,2684693-30 | 5094-IF4IHSXT, 4 ANALOG INPUT, S | 2 BAY RIGHT WALL
AF0065 | 2684693-18,2684693-30 | 5094-IF4IHSXT, 4 ANALOG INPUT, S | 2 BAY RIGHT WALL
AF0066 | 2684693-18,2684693-27 | 5094-OF8IHXT, 8 ANALOG OUTPUT, ISOLATED | 2 BAY RIGHT WALL
AF0067 | 2684693-17,2684693-25 | 5094-OB8XT, 8 DISCRETE OUTPUT | 2 BAY RIGHT WALL
AF0068 | [2]2684693-21,2684693-36 | 5094-IRT8SXT, 8 RTD/TC ANALOG INPUT, S | 2 BAY RIGHT WALL
AF0071 | 2684693-18,2684693-32 | 5094-IJ2ISXT, 2 FAST COUNTER INPUT, S | 2 BAY RIGHT WALL
AF0072 | 2684693-18,2684693-30 | 5094-IF4IHSXT, 4 ANALOG INPUT, S | 2 BAY RIGHT WALL
AF0073 | 2684693-21,2684693-36 | 5094-IRT8SXT, 8 RTD/TC ANALOG INPUT, S | 2 BAY RIGHT WALL
AF0074 | 2684693-18,2684693-26 | 5094-IF8IHXT, 8 ANALOG INPUT, ISOLATED | 2 BAY RIGHT WALL
AF0075 | 2684693-18,2684693-30 | 5094-IF4IHSXT, 4 ANALOG INPUT, S | 2 BAY RIGHT WALL
AF0076 | 2684693-18,2684693-55 | 5094-OB16SXT, 16 DISCRETE OUTPUT, S | 2 BAY RIGHT WALL
AF0450 | 1322418-11,1322418-20,1322418-70,1322418-71,1322418-80,1322418-81 | 1444-DYN04-01RA, 4-CH VIBRATION INPUT^DYNAMIX 1444 VIBRATION | 2 BAY RIGHT WALL
AU0050 | 2684693-22 | 5094-AENTRXT, DEVICE LEVEL RING | 2 BAY RIGHT WALL
AU0060 | 2684693-22 | 5094-AENTRXT, FLEX 5000 I/O | 2 BAY RIGHT WALL
AU0070 | 2684693-22 | 5094-AENTRXT, FLEX 5000 I/O | 2 BAY RIGHT WALL
FU0050 | 1043265-1,1043265-5 | FUSE, 10A | 2 BAY RIGHT WALL
FU0051 | 1043265-1,1043265-5 | FUSE, 10A | 2 BAY RIGHT WALL
FU0052 | 1043265-1,1043265-5 | FUSE, 10A | 2 BAY RIGHT WALL
FU0053 | 1043265-1,1043265-5 | FUSE, 10A | 2 BAY RIGHT WALL
FU0054 | 1043265-1,1043265-5 | FUSE, 10A | 2 BAY RIGHT WALL
FU0055 | 1043265-1,1043265-3 | FUSE, 2A | 2 BAY RIGHT WALL
FU0060 | 1043265-1,1043265-5 | FUSE, 10A | 2 BAY RIGHT WALL
FU0061 | 1043265-1,1043265-5 | FUSE, 10A | 2 BAY RIGHT WALL
FU0062 | 1043265-1,1043265-5 | FUSE, 10A | 2 BAY RIGHT WALL
FU0063 | 1043265-1,1043265-5 | FUSE, 10A | 2 BAY RIGHT WALL
FU0064 | 1043265-1,1043265-5 | FUSE, 10A | 2 BAY RIGHT WALL
FU0070 | 1043265-1,1043265-5 | FUSE, 10A | 2 BAY RIGHT WALL
FU0071 | 1043265-1,1043265-5 | FUSE, 10A | 2 BAY RIGHT WALL
FU0110 | 1043265-1,1043265-7 | FUSE, 20A | 2 BAY RIGHT WALL
FU0111 | 1043265-1,1043265-5 | FUSE, 10A | 2 BAY RIGHT WALL
FU0112 | 1043265-1,1043265-3,1043265-5 | FUSE, 10A | 2 BAY RIGHT WALL
FU0450 | 1043265-1,1043265-4 | FUSE, 5A | 2 BAY RIGHT WALL
GR8241 | 903849C1 | RAIL GROUND, DIN RAIL GROUNDING | 2 BAY RIGHT WALL
GR8242 | 903849C1 | RAIL GROUND, DIN RAIL GROUNDING | 2 BAY RIGHT WALL
GR8243 | 903849C1 | RAIL GROUND, DIN RAIL GROUNDING | 2 BAY RIGHT WALL
GR9241 | 903849C1 | RAIL GROUND, DIN RAIL GROUNDING | 2 BAY RIGHT WALL
GR9242 | 903849C1 | RAIL GROUND, DIN RAIL GROUNDING | 2 BAY RIGHT WALL
IEG8240 | 232941-300 | BUS BAR, 2-BAY (PANEL NO.4) - INST. EARTH GROUNDING | 2 BAY RIGHT WALL
XT0050 | 1066730-7,1066730-8 | TERMINAL BLOCK, SPRING, 4 CONDUCTOR,30-12 AWG (0.05-3.31 MM2),NON-IS | 2 BAY RIGHT WALL
XT0060 | 1066730-7,1066730-8,1067996-4 | TERMINAL BLOCK, SPRING, 4 CONDUCTOR,30-12 AWG (0.05-3.31 MM2),NON-IS | 2 BAY RIGHT WALL
XT0070 | 1066730-7,1066730-8,1067996-4 | TERMINAL BLOCK, SPRING, 4 CONDUCTOR,30-12 AWG (0.05-3.31 MM2),NON-IS | 2 BAY RIGHT WALL
XT0110 | 1066730-7,1066730-8,1067996-4 | TERMINAL BLOCK, SPRING, 4 CONDUCTOR,30-12 AWG (0.05-3.31 MM2),NON-IS | 2 BAY RIGHT WALL
XT0400 | 1066730-1,1066730-2,1066730-67 | TERMINAL STRIP, 4 CONDUCTOR | 2 BAY RIGHT WALL
XT0450 | 1066730-7,1066730-8,1067996-4 | TERMINAL BLOCK, SPRING, 4 CONDUCTOR,30-12 AWG (0.05-3.31 MM2),NON-IS | 2 BAY RIGHT WALL
XT-9331 | 1074259-1 | TERMINAL BLOCK, SPRING, 4 CONDUCTOR,30-12 AWG (0.05-3.31 MM2),NON-IS | 2 BAY RIGHT WALL
XT-9334 | 1074259-1 | TERMINAL BLOCK, SPRING, 4 CONDUCTOR,30-12 AWG (0.05-3.31 MM2),NON-IS | 2 BAY RIGHT WALL
XT-9335 | 1074259-1 | TERMINAL BLOCK, SPRING, 4 CONDUCTOR,30-12 AWG (0.05-3.31 MM2),NON-IS | 2 BAY RIGHT WALL
XT-9336 | 1074259-1 | TERMINAL BLOCK, SPRING, 4 CONDUCTOR,30-12 AWG (0.05-3.31 MM2),NON-IS | 2 BAY RIGHT WALL
XT-9337 | 1074259-1 | TERMINAL STRIP, IS, 2 CONDUCTOR | 2 BAY RIGHT WALL
XT-9338 | 1074259-1 | TERMINAL STRIP, IS, 2 CONDUCTOR | 2 BAY RIGHT WALL
XT-9338A | 1074259-1 | TERMINAL BLOCK, SPRING, 4 CONDUCTOR,30-12 AWG (0.05-3.31 MM2),NON-IS | 2 BAY RIGHT WALL
XT-9350 | 1074259-1 | TERMINAL BLOCK, SPRING, 4 CONDUCTOR,30-12 AWG (0.05-3.31 MM2),NON-IS | 2 BAY RIGHT WALL
XT-9355 | 1074259-1 | TERMINAL STRIP, SYSTEM FUNCTION (USE) | 2 BAY RIGHT WALL
XT-9360 | 1074259-1 | TERMINAL STRIP, SYSTEM FUNCTION (USE) | 2 BAY RIGHT WALL
XT-9370 | 1074259-1 | TERMINAL BLOCK, SPRING, 4 CONDUCTOR,30-12 AWG (0.05-3.31 MM2),NON-IS | 2 BAY RIGHT WALL
XT-9380 | 1074259-1 | TERMINAL STRIP, IS, 2 CONDUCTOR | 2 BAY RIGHT WALL
XT-9381 | 1074259-1 | TERMINAL STRIP, SYSTEM FUNCTION (USE) | 2 BAY RIGHT WALL
EL0273 | 1022899,22690R1 | LIGHT, LED, WHITE | ASSEMBLY CONSOLE
EL0274 | 1022899,22690R1 | LIGHT, LED, WHITE | ASSEMBLY CONSOLE
HA0273 | 1015162-10,1113568-100 | HORN, AUDIBLE ALARM | ASSEMBLY CONSOLE
ZS0273 | 1113474-1 | LIMIT SWITCH, CONSOLE DOOR OPEN | ASSEMBLY CONSOLE
ZS0274 | 1113474-1 | LIMIT SWITCH, CONSOLE DOOR OPEN | ASSEMBLY CONSOLE
AF0201 | 2684693-48,2684693-51 | 5094-IB32XT, 32 DISCRETE INPUT | ASSEMBLY^CONTROL PANEL
AF0202 | PARTOFTCPASSY | 5094-OB32XT, 32 DISCRETE OUTPUT | ASSEMBLY^CONTROL PANEL
AU0200 | PARTOFTCPASSY | 5094-AENTRXT, FLEX 5000 I/O | ASSEMBLY^CONTROL PANEL
GR0200 | PARTOFTCPASSY | RAIL LUG, DIN RAIL GROUNDING | ASSEMBLY^CONTROL PANEL
HL0400 | PARTOFTCPASSY | LIGHT, READY, GREEN | ASSEMBLY^CONTROL PANEL
HL0401 | PARTOFTCPASSY | LIGHT, STARTING, WHITE | ASSEMBLY^CONTROL PANEL
HL0402 | PARTOFTCPASSY | LIGHT, READY TO LOAD, WHITE | ASSEMBLY^CONTROL PANEL
HL0403 | PARTOFTCPASSY | LIGHT, ON LOAD, WHITE | ASSEMBLY^CONTROL PANEL
HL0404 | 1035040-1497,PARTOFTCPASSY | LIGHT, WHRU SERVICE, WHITE | ASSEMBLY^CONTROL PANEL
HL0405 | 1035040-1279,PARTOFTCPASSY | LIGHT, LOCAL/PMS SELECT, WHITE | ASSEMBLY^CONTROL PANEL
HL0406 | PARTOFTCPASSY | LIGHT, SPARE, WHITE | ASSEMBLY^CONTROL PANEL
HL0407 | PARTOFTCPASSY | LIGHT, COOLDOWN, WHITE | ASSEMBLY^CONTROL PANEL
HL0408 | PARTOFTCPASSY | LIGHT, STOPPING, WHITE | ASSEMBLY^CONTROL PANEL
HL0409 | PARTOFTCPASSY | LIGHT, ALARM SUMMARY, AMBER | ASSEMBLY^CONTROL PANEL
HL0410 | PARTOFTCPASSY | LIGHT, BACKUP ACTIVE, AMBER | ASSEMBLY^CONTROL PANEL
HL0411 | PARTOFTCPASSY | LIGHT, SHUTDOWN SUMMARY, RED | ASSEMBLY^CONTROL PANEL
SA0400 | 1035040-32,1064851-10,PART OF TCP ASSEMBLY | SELECTOR SWITCH, OFF/LOCAL/PMS | ASSEMBLY^CONTROL PANEL
SA0401 | PARTOFTCPASSY | SELECTOR SWITCH, BACKUP SYSTEM RESET | ASSEMBLY^CONTROL PANEL
SB0400 | 1035040-694,PARTOFTCPASSY | PUSHBUTTON SWITCH, EMERGENCY STOP | ASSEMBLY^CONTROL PANEL
SB0401 | PARTOFTCPASSY | PUSHBUTTON SWITCH, HORN SILENCE | ASSEMBLY^CONTROL PANEL
SB0402 | PARTOFTCPASSY | PUSHBUTTON SWITCH, ACKNOWLEDGE | ASSEMBLY^CONTROL PANEL
SB0403 | PARTOFTCPASSY | PUSHBUTTON SWITCH, RESET | ASSEMBLY^CONTROL PANEL
SB0404 | PARTOFTCPASSY | PUSHBUTTON SWITCH, LAMP TEST | ASSEMBLY^CONTROL PANEL
SB0405 | 1035040-18,PARTOFTCPASSY | PUSHBUTTON SWITCH, START | ASSEMBLY^CONTROL PANEL
SB0406 | 1035040-34,PARTOFTCPASSY | PUSHBUTTON SWITCH, NORMAL STOP | ASSEMBLY^CONTROL PANEL
SB0407 | PARTOFTCPASSY | PUSHBUTTON SWITCH, SPEED/LOAD DECREASE | ASSEMBLY^CONTROL PANEL
SB0408 | PARTOFTCPASSY | PUSHBUTTON SWITCH, SPEED/LOAD INCREASE | ASSEMBLY^CONTROL PANEL
SH0400 | PARTOFTCPASSY | LIGHTED SWITCH, SPARE, WHITE | ASSEMBLY^CONTROL PANEL
SH0401 | PARTOFTCPASSY | LIGHTED SWITCH, SPARE, WHITE | ASSEMBLY^CONTROL PANEL
SH0404 | 1035040-617,PARTOFTCPASSY | LIGHTED SWITCH, AUTO SYNC INIT, WHITE | ASSEMBLY^CONTROL PANEL
SH0405 | PARTOFTCPASSY | LIGHTED SWITCH, SPARE, WHITE | ASSEMBLY^CONTROL PANEL
SH0408 | 1035040-1277,1035040-1278,PARTOFTCPASSY | LIGHTED SWITCH, REMOTE START ENABLE/DISABLE, WHITE | ASSEMBLY^CONTROL PANEL
SH0409 | 1035040-8,PARTOFTCPASSY | LIGHTED SWITCH, GAS/LIQUID FUEL SELECT, WHITE | ASSEMBLY^CONTROL PANEL
SH0410 | 1035040-6,PARTOFTCPASSY | LIGHTED SWITCH, SPD ISOCH/SPD DROOP, WHITE | ASSEMBLY^CONTROL PANEL
SH0411 | 1035040-340,PARTOFTCPASSY | LIGHTED SWITCH, VOLTAGE DECREASE SELECT, WHITE | ASSEMBLY^CONTROL PANEL
SH0412 | 1035040-341,PARTOFTCPASSY | LIGHTED SWITCH, VOLTAGE INCREASE SELECT, WHITE | ASSEMBLY^CONTROL PANEL
XT0564 | PARTOFTCPASSY | TERMINAL STRIP, SYSTEM FUNCTION (USE) | ASSEMBLY^CONTROL PANEL
AT0190 | 1577354-5300 | WORKSTATION, PANEL COMPUTER, TT4000 | CONSOLE DOOR^PANEL
AT0190K | 1068334 | KEYBOARD, TYPING INTERFACE | CONSOLE DOOR^PANEL
GF4000 | CUSTOMER SUPPLIED | GROUND FAULT RELAY, FIELD GROUND | CONSOLE DOOR^PANEL
TM0102 | 908539C1 | TRANSFORMER, PHASE SHIFTING | CONSOLE DOOR^PANEL
UA1200 | REFERENCE | SIGNAL CONVERTER, BACKUP OVERSPEED | JB44
XT1200 | 1066730-7 | TERMINAL BLOCK, SPRING, 4 CONDUCTOR,30-12 AWG (0.05-3.31 MM2),NON-IS | JB44
XT0400 | 1066730-1,1066730-2,1066730-67 | TERMINAL STRIP, 4 CONDUCTOR | JB70
PA0700 | 1565287-16 | AMMETER, CURRENT MEASUREMENT | METER PANEL
PA0701 | 1035040-200,1616415-2,186583-2 | AMMETER, EXCITER FIELD CURRENT | METER PANEL
PA0703 | 1620357-G9440 | METER, POWER | METER PANEL
PA0771 | 1035040-207,1616419-3,962317C1 | WATT METER, POWER FACTOR | METER PANEL
PF0701 | 1035040-208,1616418-1,962308C1 | METER, FREQUENCY MEASUREMENT | METER PANEL
PV0700 | 1035040-211,1620356-34,186533-1 | VOLT METER, VOLTAGE MEASUREMENT | METER PANEL
PV0701 | 1035040-206,1616416-2,186891-10 | VOLT METER, EXCITER FIELD VOLTAGE | METER PANEL
AP0612 | 2762566-6 | ORBIT 60, SYSTEM INTERFACE MODULE (SIM) | ORBIT 60^DOOR PANEL
AP0613 | 2762566-7 | ORBIT 60, PROTECTION PROCESSING MODULE (PPM) | ORBIT 60^DOOR PANEL
AP0614 | 2762566-19 | ORBIT 60, BLANK MODULE SLOT COVER | ORBIT 60^DOOR PANEL
AP0615 | 2762566-9 | ORBIT 60, COMMUNICATION GATEWAY MODULE (CGW) | ORBIT 60^DOOR PANEL
AP0616 | 2762566-11 | ORBIT 60, KEYPHASOR INPUT MODULE (KPH) | ORBIT 60^DOOR PANEL
AP0617 | 2762566-12 | ORBIT 60, DYNAMIC INPUT MODULE (PAV) | ORBIT 60^DOOR PANEL
AP0618 | 2762566-12 | ORBIT 60, DYNAMIC INPUT MODULE (PAV) | ORBIT 60^DOOR PANEL
AP0619 | 2762566-19 | ORBIT 60, BLANK MODULE SLOT COVER | ORBIT 60^DOOR PANEL
AP0620 | 2762566-19 | ORBIT 60, BLANK MODULE SLOT COVER | ORBIT 60^DOOR PANEL
AP0621 | 2762566-12 | ORBIT 60, DYNAMIC INPUT MODULE (PAV) | ORBIT 60^DOOR PANEL
AP0622 | 2762566-13 | ORBIT 60, DYNAMIC INPUT MODULE (PAS) | ORBIT 60^DOOR PANEL
AP0623 | 2762566-19 | ORBIT 60, BLANK MODULE SLOT COVER | ORBIT 60^DOOR PANEL
AP0624 | 2762566-12 | ORBIT 60, DYNAMIC INPUT MODULE (PAV) | ORBIT 60^DOOR PANEL
AP0625 | 2762566-19 | ORBIT 60, BLANK MODULE SLOT COVER | ORBIT 60^DOOR PANEL
AP0626 | 2762566-19 | ORBIT 60, BLANK MODULE SLOT COVER | ORBIT 60^DOOR PANEL
AP0627 | 2762566-19 | ORBIT 60, BLANK MODULE SLOT COVER | ORBIT 60^DOOR PANEL
AP0628 | 2762566-17 | ORBIT 60, SOLID STATE RELAY MODULE (SSR) | ORBIT 60^DOOR PANEL
AP0629 | 2762566-8 | ORBIT 60, CONDITIONING MONITORING MODULE (CCM) | ORBIT 60^DOOR PANEL
AR0610 | 2762566-1 | PANEL MOUNT CHASSIS, ORBIT 60 3U 19 SLOT, 20 TOTAL | ORBIT 60^DOOR PANEL
UV0610 | 2762566-5 | POWER SUPPLY, ORBIT 60 RACK | ORBIT 60^DOOR PANEL
UV0611 | 2762566-5 | POWER SUPPLY, ORBIT 60 RACK | ORBIT 60^DOOR PANEL
BA0543 | 1271449-1 | MEDIA CONVERTER, ETHERNET-FIBER OPTIC | PANEL
BUOSM | CUSTOMER DEFINED |  | PANEL
CCGB0523 | CUSTOMER DEFINED | CUSTOMER CONNECTION, VOLTAGE INPUT: 100-240VAC/90-340VDC^FREQ INPUT: 50/60HZ^UPS POWER-1 | PANEL
CC-KA7500 | CUSTOMER SUPPLIED | CUSTOMER CONNECTION, AUTOMATIC SYNCHRONIZE^INITIATE (REMOTE)^(PULSE SIGNAL) | PANEL
CC-KA7505 | CUSTOMER SUPPLIED | CUSTOMER CONNECTION, START AND AUTO-SYNC^(REMOTE)^(PULSE SIGNAL) | PANEL
CCPS6670 | CUSTOMER DEFINED | CUSTOMER CONNECTION, H20#1 RELEASE CONFIRM | PANEL
CCPS6675 | CUSTOMER DEFINED | CUSTOMER CONNECTION, N2#1 PRESSURE | PANEL
CCPS6680 | CUSTOMER DEFINED | CUSTOMER CONNECTION, H20 #2 RELEASE CONFIRM | PANEL
CCPS6685 | CUSTOMER DEFINED | CUSTOMER CONNECTION, N2 #2 PRESSURE | PANEL
CC-SM7632 | < no partnumber assigned > | CUSTOMER CONNECTION, GAS FUEL FLOW (MASS)^4/20MA = 0 - 12000 LB/H^4/20MA = 0 - 5443 KG/H | PANEL
CC-SM7633 | CUSTOMER SUPPLIED | CUSTOMER CONNECTION, GAS FUEL TEMPERATURE^4/20MA = 32 - 392 DEG F^4/20MA = 0 - 200 DEG C | PANEL
CC-SM7634 | CUSTOMER SUPPLIED | CUSTOMER CONNECTION, T1 TEMPERATURE^4/20MA = 32 - 212 DEG F^4/20MA = 0 - 100 DEG C | PANEL
CC-SM7635 | CUSTOMER SUPPLIED | CUSTOMER CONNECTION, GENERATOR CAPACITY^4/20MA = 8000 - 15000 KW | PANEL
CCSV6671 | CUSTOMER DEFINED | CUSTOMER CONNECTION, PRIMARY RELEASE#1 | PANEL
CCSV6681 | CUSTOMER DEFINED | CUSTOMER CONNECTION, PRIMARY RELEASE #2^WATER MIST | PANEL
CCZSO6671 | CUSTOMER DEFINED | CUSTOMER CONNECTION, DISCHARGE LIMIT SWITCH | PANEL
CCZSO6672 | CUSTOMER DEFINED | CUSTOMER CONNECTION, DRAIN LIMIT SWITCH | PANEL
JB-TS304 | 1067996-2,1067996-4,1067996-7 | TERMINAL STRIP, 4 CONDUCTOR | PANEL
SB3150 | 1015163-7 | PUSHBUTTON MAINTAINED, PRE/POST LUBE MOTOR^START INTERRUPT SWITCH | PANEL
SB3420 | DPR | PUSHBUTTON MAINTAINED, GENERATOR JACKING OIL MOTOR START INTERRUPT SWITCH | PANEL
AT0680 | 1634974-100 | GATEWAY MODULE, TURBOTRONIC GATEWAY | PWR,DISTRIBUTION RAIL^LEFT DOOR
FU0190 | 1043265-1,1043265-5 | FUSE, 10A | PWR,DISTRIBUTION RAIL^LEFT DOOR
FU0200 | 1043265-1,1043265-5 | FUSE, 10A | PWR,DISTRIBUTION RAIL^LEFT DOOR
FU0201 | 1043265-1,1043265-5 | FUSE, 10A | PWR,DISTRIBUTION RAIL^LEFT DOOR
FU0273 | 1043265-1,1043265-4 | FUSE, 5A | PWR,DISTRIBUTION RAIL^LEFT DOOR
FU0560 | 1043265-1,1043265-7 | FUSE, 20A | PWR,DISTRIBUTION RAIL^LEFT DOOR
FU0680 | 1043265-1,1043265-4 | FUSE, 5A | PWR,DISTRIBUTION RAIL^LEFT DOOR
XT0560 | 1066730-16,1066730-17 | TERMINAL STRIP, 2 CONDUCTOR | PWR,DISTRIBUTION RAIL^LEFT DOOR
XT0561 | 1066730-53,1066730-7 | TERMINAL BLOCK, SPRING, 4 CONDUCTOR,30-12 AWG (0.05-3.31 MM2),NON-IS | PWR,DISTRIBUTION RAIL^LEFT DOOR
XT0562 | 1066730-53,1066730-7 | TERMINAL BLOCK, SPRING, 4 CONDUCTOR,30-12 AWG (0.05-3.31 MM2),NON-IS | PWR,DISTRIBUTION RAIL^LEFT DOOR
XT0563 | 1066730-7,1066730-8 | TERMINAL BLOCK, SPRING, 4 CONDUCTOR,30-12 AWG (0.05-3.31 MM2),NON-IS | PWR,DISTRIBUTION RAIL^LEFT DOOR
XT0680 | 1066730-7,1066730-8,1067996-4 | TERMINAL BLOCK, SPRING, 4 CONDUCTOR,30-12 AWG (0.05-3.31 MM2),NON-IS | PWR,DISTRIBUTION RAIL^LEFT DOOR
HL0701 | 1035040-201,1751651-2 | LIGHT, GENERATOR CIRCUIT BREAKER OPEN, GREEN | SWITCH PANEL
HL0702 | 1035040-202,1751651-1 | LIGHT, GENERATOR CIRCUIT BREAKER CLOSED, RED | SWITCH PANEL
HL0703 | 910087C1 | LIGHT, GENERATOR SYNCHRONIZING - PHASE A, CLEAR | SWITCH PANEL
HL0704 | 910087C1 | LIGHT, GENERATOR SYNCHRONIZING - PHASE C, CLEAR | SWITCH PANEL
PF0700 | 1035040-209,1614318-1 | GAGE, SYNCHROSCOPE | SWITCH PANEL
SA0700 | 1035040-218,1051149-3 | SELECTOR SWITCH, MANUAL SYNCHRONIZATION | SWITCH PANEL
SA0701 | 1035040-203,1051149-5 | SELECTOR SWITCH, CIRCUIT BREAKER CONTROL | SWITCH PANEL
SA0710 | 1035040-213,1051149-4 | SELECTOR SWITCH, VOLTAGE SELECT | SWITCH PANEL
SA0740 | 1035040-212,1051149-2 | SELECTOR SWITCH, CURRENT SELECT | SWITCH PANEL
SA0770 | 1035040-1048,1051149-1 | SELECTOR SWITCH, KW/KVAR SELECT | SWITCH PANEL