## Blue Labels
(SHT 1) JB147 | (SHT 2) JB147
AF0794 | SB0147
AF0793 | XP0019
AF0792 | XP0125
AF0791 | XP0791
AU0790
GR0112
KA1241
KA1240
KA0254
KA0255
KA2200
KA0253
KA0505
FU0194
FU0193
FU0192
FU0191
FU0794
FU0793
FU0792
FU0791
FU0790
XT0790
XT0791
XT0792
XT0793
GR0113
AU0190
AF0191
AF0192
PC0471
GR0114

## Panel Errors
Panel Errors
Project # | 3382734-100
Project Name
Revision
Controls DE | M.ELAMIN
Phone:
Controls ME
Phone:
From | [6 empty] | To
Device ID | Location | Cable (W) Conductor (SC) Jumper Clip (JC) | Wire ID | Wire No. | Gauge/Size | Page/Zone | Device ID | Location | Page/Zone
XP0019:1 | JB147 | SC |  | AT0170L1 |  | 3.C4 | CC1?:1 | PANEL | 3.C5
XP0125:1 | JB147 | SC |  | UF6242E2 |  | 3.A6 | CC2?:1 | PANEL | 3.A6
XP0791:1 | JB147 | WC3179 | RED | ESTOPF | 3x 14 AWG , 6x 18 AWG | 5.C4 | XP0790:1 | PANEL | 5.C6
XP0790:3 | JB147 | WC3179 | WHT/BLK | * | 3x 14 AWG , 6x 18 AWG | 4.A3 | XP0791:3 | PANEL | 4.A5
XP0791:2 | JB147 | WC3179 | WHT | ESTOPC | 3x 14 AWG , 6x 18 AWG | 5.C4 | XP0790:2 | PANEL | 5.C6
XP0791:4 | JB147 | WC3179 | BLU | 0V1 | 3x 14 AWG , 6x 18 AWG | 3.A4 | XP0790:4 | PANEL | 3.A5
XP0791:6 | JB147 | WC3179 | BLK | QS0790LI-4 | 3x 14 AWG , 6x 18 AWG | 3.A4 | XP0790:6 | PANEL | 3.A5
SolarTools ver. 24.0.84.17940 (Apr 3, 2025)
Report date: 5/20/2025 9:27 AM

## Cable Part Numbers
Cable Part Numbers |  |  | SolarTools ver. 24.0.84.17940 (Apr 3, 2025)
Project # | 3382734-100
Report date: 5/20/2025 9:27 AM
Project Name
Revision
Controls DE | M.ELAMIN
Phone:
Controls ME
Phone:
Device ID |  | Part Number |  | Description
WC0190 |  | 1302073-36 |  | CABLE, ETHERNET - 36 INCHES
WC0790 |  | 1302073-36 |  | CABLE, ETHERNET - 36 INCHES

## Part Number List
Part Number List |  | SolarTools ver. 24.0.84.17940 (Apr 3, 2025)
Project # | 3382734-100
Report date: 5/20/2025 9:27 AM
Project Name
Revision
Controls DE | M.ELAMIN
Phone:
Controls ME
Phone:
Device ID | Part Number | Description | Location
AF0191 | 2684693-17,2684693-25 | 5094-OB8XT, 8 DISCRETE OUTPUT | JB147
AF0192 | 2684693-17,2684693-23 | 5094-IB16XT, 16 DISCRETE INPUT | JB147
AF0791 | 2684693-17,2684693-25 | 5094-OB8XT, 8 DISCRETE OUTPUT | JB147
AF0792 | 2684693-18,2684693-28 | 5094-IB16SXT, 16 DISCRETE INPUT, S | JB147
AF0793 | 2684693-18,2684693-56 | 5094-IF8IHXT, 8 ANALOG INPUT, ISOLATED | JB147
AF0794 | 2684693-18,2684693-55 | 5094-OB16SXT, 16 DISCRETE OUTPUT, S | JB147
AU0190 | 2684693-22 | 5094-AENTRXT, FLEX 5000 I/O | JB147
AU0790 | 2684693-22 | 5094-AENTRXT, FLEX 5000 I/O | JB147
FU0191 | 1043265-1,1043265-5 | FUSE, 10A | JB147
FU0192 | 1043265-1,1043265-5 | FUSE, 10A | JB147
FU0193 | 1043265-1,1043265-5 | FUSE, 10A | JB147
FU0194 | 1043265-1,1043265-4,1043265-5 | FUSE, 5A | JB147
FU0790 | 1043265-1,1043265-6 | FUSE, 15A | JB147
FU0791 | 1043265-1,1043265-5 | FUSE, 10A | JB147
FU0792 | 1043265-1,1043265-5 | FUSE, 10A | JB147
FU0793 | 1043265-1,1043265-5 | FUSE, 10A | JB147
FU0794 | 1043265-1,1043265-5 | FUSE, 10A | JB147
GR0112 | 903849C1 | RAIL GROUND, DIN RAIL GROUNDING | JB147
GR0113 | 903849C1 | RAIL GROUND, DIN RAIL GROUNDING | JB147
GR0114 | 903849C1 | RAIL GROUND, DIN RAIL GROUNDING | JB147
KA0253 | 1061979-1 | RELAY, NO EMERGENCY SHUTDOWN SUMMARY | JB147
KA0254 | 1061979-1 | RELAY, NO EMERGENCY SHUTDOWN SUMMARY | JB147
KA0255 | 1061979-1 | RELAY, NO EMERGENCY SHUTDOWN SUMMARY | JB147
KA1240 | 1061979-1 | RELAY, SECONDARY LIQUID FUEL SHUTOFF | JB147
KA1241 | 1061979-1 | RELAY, LIQUID FUEL PRIMARY SHUTOFF | JB147
KA2200 | 1061979-1 | RELAY, LIQUID FUEL BOOST PUMP DRIVE | JB147
PC0471 | 2271605-1 | TIMER/COUNTER, LIQUID FUEL COUNTER HOUR / START | JB147
SB0147 | 2380746-4 | PUSHBUTTON SWITCH, EMERGENCY STOP | JB147
XP0019 | 2737835-6 | RJ45 RECEPTACLE, CIRCUIT CONTINUITY | JB147
XP0125 | 2737835-6 | RJ45 RECEPTACLE, CIRCUIT CONTINUITY | JB147
XP0791 | 1899205-1 | CONNECTOR, CIRCUIT CONTINUITY | JB147
XT0790 | 1066730-7,1066730-8 | TERMINAL BLOCK, SPRING, 4 CONDUCTOR,30-12 AWG (0.05-3.31 MM2),NON-IS | JB147
XT0791 | 1066730-7,1066730-8 | TERMINAL BLOCK, SPRING, 4 CONDUCTOR,30-12 AWG (0.05-3.31 MM2),NON-IS | JB147
XT0792 | 1066730-7 | TERMINAL BLOCK, SPRING, 4 CONDUCTOR,30-12 AWG (0.05-3.31 MM2),NON-IS | JB147
XT0793 | 1066730-7 | TERMINAL BLOCK, SPRING, 4 CONDUCTOR,30-12 AWG (0.05-3.31 MM2),NON-IS | JB147
CC1? | < no partnumber assigned > | CUSTOMER CONNECTION, SYSTEM FUNCTION | PANEL
CC2? | < no partnumber assigned > | CUSTOMER CONNECTION, SYSTEM FUNCTION | PANEL
XP0790 | < no partnumber assigned > | ONSKID INTERCONNECT, CONTROLS RECEPTACLE | PANEL

## JB147_S
JB147 LIQUID FUEL PANEL
Project # | 3382734-100
Project Name
Revision
Controls DE | M.ELAMIN
Phone:
Controls ME
Phone:
From | [5 empty] | To
Device ID | Wire No. | Wire ID | Gauge/Size | Length | Device ID | Location | Bundle Name
AF0792:02 | SB0147B112 | WHT | 20 | 100 | SB0147:B1-12 | JB147 | SB0147
AF0792:34 | SB0147B111 | WHT | 20 | 100 | SB0147:B1-11 | JB147
SB0147:B2-11 | ESTOPF | WHT | 20 | 100 | XT0792:1 | JB147
SB0147:B2-12 | ESTOPC | WHT | 20 | 100 | XT0792:2 | JB147
KA1240:A1 | -079401 | WHT | 20 | 40 | AF0794:01 | JB147 | KA A1/A2
KA1241:A1 | -079400 | WHT | 20 | 40 | AF0794:00 | JB147
KA2200:A1 | -079108 | WHT | 20 | 40 | AF0791:08 | JB147
KA0253:A2 | -0V1 | WHT | 20 | 40 | KA0254:A2 | JB147
KA0255:A2 | -0V1 | WHT | 20 | 40 | XT0790:4 | JB147
KA1240:A2 | -079417 | WHT | 20 | 40 | AF0794:17 | JB147
KA1241:A2 | -079416 | WHT | 20 | 40 | AF0794:16 | JB147
KA2200:A2 | -079124 | WHT | 20 | 40 | AF0791:24 | JB147
KA0254:24 | KA1241 | WHT | 16 | 40 | KA1241:11 | JB147 | KA
KA0255:14 | KA124011 | WHT | 16 | 40 | KA1240:11 | JB147
KA1240:14 | -019100 | WHT | 16 | 40 | AF0191:00 | JB147
KA1241:14 | -019102 | WHT | 16 | 40 | AF0191:02 | JB147
PC0471:+PWR | -079136 | WHT | 20 | 40 | XT0793:1 | JB147 | PC0471
PC0471:INP_A | -079104 | WHT | 20 | 40 | XT0793:2 | JB147
PC0471:INP_B | -079134 | WHT | 20 | 40 | XT0793:3 | JB147
PC0471:-PWR | -079102 | GRY | 20 | 40 | XT0793:4 | JB147
AF0791:02 | -079102 | WHT | 20 | 40 | XT0793:4 | JB147 | AU/AF0790
AF0791:04 | -079104 | WHT | 20 | 40 | XT0793:2 | JB147
AF0791:34 | -079134 | WHT | 20 | 40 | XT0793:3 | JB147
AF0791:36 | -079136 | WHT | 20 | 40 | XT0793:1 | JB147
AF0791:COM | -0V1 | WHT | 16 | 40 | XT0790:2 | JB147
AF0792:COM | -0V1 | WHT | 16 | 40 | XT0790:1 | JB147
AF0794:COM | -0V1 | WHT | 16 | 40 | XT0790:2 | JB147
AU0790:COM | -0V1 | WHT | 16 | 60 | XT0790:1 | JB147
AU0790:V+ | FU0791 | WHT | 16 | 60 | FU0791:LD | JB147
AF0791:V+ | FU0792 | WHT | 16 | 60 | FU0792:LD | JB147
AF0792:V+ | FU0793 | WHT | 16 | 60 | FU0793:LD | JB147
AF0794:V+ | FU0794 | WHT | 16 | 60 | FU0794:LD | JB147
AF0192:V+ | FU0193 | WHT | 16 | 60 | FU0193:LD | JB147 | AU/AF0190
AF0192:COM | -0V1 | WHT | 16 | 40 | XT0790:4 | JB147
AF0191:COM | -0V1 | WHT | 14 | 40 | XT0790:3 | JB147
AU0190:COM | -0V1 | WHT | 14 | 40 | XT0790:3 | JB147
AU0190:V+ | FU0191 | WHT | 14 | 40 | FU0191:LD | JB147
AF0191:V+ | FU0192 | WHT | 14 | 40 | FU0192:LD | JB147
FU0191:LI | FU0790 | WHT | 14 | 40 | FU0794:LI | JB147 | FU
FU0791:LI | FU0790 | WHT | 14 | 60 | FU0790:LD | JB147
FU0790:LI | QS0790LI-4 | WHT | 14 | 40 | XT0791:2 | JB147
XT0790:1 | -0V1 | WHT | 14 | 40 | XT0791:1 | JB147 | XT

## Bundle Tag Info
JB147 LIQUID FUEL #7
PD #
Revision
JB147 LIQUID FUEL | Panel Name | Panel Name | Panel Name | Panel Name | Panel Name | Panel Name | Panel Name | Panel Name | Panel Name | Panel Name | Panel Name | Panel Name | Panel Name | Panel Name | Panel Name | Panel Name | Panel Name | Panel Name | Panel Name | Panel Name | Panel Name | Panel Name | Panel Name | Panel Name | Panel Name | Panel Name | Panel Name | Panel Name | Panel Name
SB0147
KA A1/A2
KA
PC0471
AU/AF0790
AU/AF0190
FU
XT

## Bundle Tags 1
JB147 LIQUID FUEL
JB147 LIQUID FUEL #7 PD # Revision JB147 LIQUID FUEL SB0147
JB147 LIQUID FUEL #7 PD # Revision JB147 LIQUID FUEL KA A1/A2
JB147 LIQUID FUEL #7 PD # Revision JB147 LIQUID FUEL KA
JB147 LIQUID FUEL #7 PD # Revision JB147 LIQUID FUEL PC0471
JB147 LIQUID FUEL #7 PD # Revision JB147 LIQUID FUEL AU/AF0790
JB147 LIQUID FUEL #7 PD # Revision JB147 LIQUID FUEL AU/AF0190
JB147 LIQUID FUEL #7 PD # Revision JB147 LIQUID FUEL FU
JB147 LIQUID FUEL #7 PD # Revision JB147 LIQUID FUEL XT

## ALL
JB147 LIQUID FUEL #7 PD # Revision JB147 LIQUID FUEL SB0147
JB147 LIQUID FUEL #7 PD # Revision JB147 LIQUID FUEL KA A1/A2
JB147 LIQUID FUEL #7 PD # Revision JB147 LIQUID FUEL KA
JB147 LIQUID FUEL #7 PD # Revision JB147 LIQUID FUEL PC0471
JB147 LIQUID FUEL #7 PD # Revision JB147 LIQUID FUEL AU/AF0790
JB147 LIQUID FUEL #7 PD # Revision JB147 LIQUID FUEL AU/AF0190
JB147 LIQUID FUEL #7 PD # Revision JB147 LIQUID FUEL FU
JB147 LIQUID FUEL #7 PD # Revision JB147 LIQUID FUEL XT