## Blue Labels
(SHT 1) TURBINE CONTROL^JB70 | (SHT 10) FG&E CTRL,SMT130 | (SHT 11) POWERDIST, PANEL | (SHT 12) MCC PNL,SMT130 | (SHT 13) GEN CMPNT | (SHT 14) PROX,TURB | (SHT 2) PNL A,SMT130 | (SHT 3) PNL B,SMT130 | (SHT 4) PNL,DOOR,2-BAY | (SHT 5) CONTROL,2-BAY | (SHT 6) BECKWITH RELAY,SMT130 | (SHT 7) TCP, SMT130 | (SHT 8) PWR DST,DR,SMT130 | (SHT 9) PLC, PANEL
XTFGA | UV0170 | FU2700 | FU0290 | AT0140 | UA1263 | FU0080 | XT0400 | AT0190K | EL0273 | KA0460 | HL0411 | XT2930 | UV0600
GR1100 | AT0170 | FU2701 | FU0291 | KA0313 | UA1211 | FU0081 | AF0400 | SB6500 |  |  | HL0410 | FU2610 | AR0600
GR1000 | FU0170 | FU2703 | FU0294 | KA0314 | UA1210 | FU0082 | AF0410 | AT0190 |  |  | HL0409 | FU2620 | AT0600
HA0472 | FU0171 | XT0027 | XT0295 | FU0332 | UA1262 | XT0080 | AF0420 | HA0273 |  |  | HL0408 | XT0563 | AP0601
| XT0170 | BA0700 | XT0290 | FU0333 | UA1221 | XT0082 | AF0450 | KA0461 |  |  | HL0407 | FU0560 | AP0602
| XT0171 | BA0703 | XT2920 | FU0334 | UA1220 | AF0081 | XT0070 |  |  |  | SB0400 | XT0561 | AP0603
| XT0172 | BA0701 | XT0292 | FU0335 | UA1231 | AF0082 | FU0070 |  |  |  | HL0406 | FU0200 | AP0604
| XT0173 | GR0146 | KA2960 | FU0336 | UA1230 | AF0083 | FU0071 |  |  |  | HL0405 | FU0201 | AP0605
| KA0172 | FU0136 | KA2970 | XT0130 | GR1210 | AF0084 | AU0070 |  |  |  | HL0404 | FU0190 | AP0606
| KA0174 | XT0102 | AU0290 | XT0190 | UA1520 | AF0085 | AF0071 |  |  |  | HL0403 | FU0273 | AP0607
| KA6510 | FU0010 | AF0291 | KA0121 | XT1521 | AF0086 | AF0072 |  |  |  | HL0402 | FU0701 | AP0608
| XT0550 | FU0460 | AF0292 | KA0128 | XTFGH | XT0137 | AF0073 |  |  |  | HL0401 | XT0562 | AP0609
| KA0179 | FU0500 | AF0293 | KA0185 | GR1211 | XT1135 | AF0074 |  |  |  | HL0400
| UAI6611 | XT0104 | AF0294 | KA0310 |  | KA0135 | AF0075 |  |  |  | SH0412
| UAI6621 | GR0145 | AF0295 | KA0330 |  | KA6211 | GR0244 |  |  |  | SH0411
| GR0170 | UJ0131 | AF0296 | KA0331 |  | KA6212 | FU0060 |  |  |  | SH0405
| AT0171 | XT0011 | AF0297 | KA0332 |  | KA6221 | FU0061 |  |  |  | SH0404
| AT0175 | FU0011 | GR0290 | KA0333 |  | KA6222 | FU0062 |  |  |  | SA0400
| AT0176 | IEG2240 | GR0291 | KA0335 |  | GR0111 | FU0063 |  |  |  | SH0410
| AT0178 | GR0144 | PEG2240 | KA0336 |  | FU0090 | FU0064 |  |  |  | SH0409
| GR0172 |  |  | XT0332 |  | FU0091 | XT0060 |  |  |  | SH0401
| FU0510 |  |  | XT0334 |  | FU0092 | AF0068 |  |  |  | SH0400
| XT0510 |  |  | XT0335 |  | FU0093 | AF0067 |  |  |  | XT0564
| AF0510 |  |  | XT0120 |  | XT0090 | AF0066 |  |  |  | AU0200
| AF0500 |  |  | FU0120 |  | AU0090 | AF0065 |  |  |  | AF0201
| XT0500 |  |  | FU0121 |  | AF0091 | AF0064 |  |  |  | AF0202
| IEG0356 |  |  | FU0180 |  | AF0092 | AF0063 |  |  |  | SB0408
|  |  |  | FU0181 |  | AF0093 | AF0062 |  |  |  | SB0407
|  |  |  | XT0180 |  | XT0136 | AF0061 |  |  |  | SH0408
|  |  |  | XT0181 |  | KA0130 | AU0060 |  |  |  | SB0405
|  |  |  | XT0183 |  | KA0131 | GR0251 |  |  |  | SB0406
|  |  |  | XT0460 |  | KA0132 | FU0110 |  |  |  | SA0401
|  |  |  | XT0337 |  | KA0141 | FU0113 |  |  |  | SB0404
|  |  |  | XT0336 |  | KA0133 | XT0110 |  |  |  | SB0403
|  |  |  | XT0370 |  | KA0134 | KA1020 |  |  |  | SB0402
|  |  |  | GR0139 |  | KA0136 | KA0235 |  |  |  | SB0401
|  |  |  | IEG0140 |  | KA0137 | KA0236 |  |  |  | GR0200
|  |  |  | XT0313 |  | KA0138 | KA0237
|  |  |  | FU0313 |  | KA0142 | KA0238
|  |  |  | FU0314 |  | KA0178 | KA0239
|  |  |  | FU0315 |  | KA0221 | KA0240
|  |  |  | XT0360 |  | KA0222 | KA0248
|  |  |  | XT0351 |  | KA0875 | KA0250
|  |  |  | XT0352 |  | KA0176 | KA0241
|  |  |  | XT0350 |  | KA0177 | KA0242
|  |  |  | XT0353 |  | KT0140 | KA0243
|  |  |  | XT0454 |  | KT0141 | KA0244
|  |  |  | XT2910 |  | KT0142 | KA0246
|  |  |  | KA3103 |  | KT0143 | KA0247
|  |  |  | KA0123 |  | KT0144 | KA0245
|  |  |  | KA2320 |  | KT0145 | KA0249
|  |  |  | KA3420 |  | KT0146 | KA0231
|  |  |  | KA4100 |  | GR0134 | KA0232
|  |  |  | GR0141 |  | PC0470 | KA0233
|  |  |  | AF0123 |  | FU0137 | KA0234
|  |  |  | AF0122 |  | XT0138 | KA0260
|  |  |  | AF0121 |  | XT0134 | XT0240
|  |  |  | AU0120 |  | FU0139 | FU0210
|  |  |  | KA0340 |  | FU0140 | FU0211
|  |  |  | AF0182 |  | FU2100 | FU0212
|  |  |  | AF0181 |  | XT0135 | FU0213
|  |  |  | AU0180 |  | XT0139 | XT0237
|  |  |  | KA2672 |  | GR0131 | XT0233
|  |  |  | KA2685 |  | XT0015 | XT0235
|  |  |  | GR0140 |  | XT0016 | GR0233
|  |  |  | PEG0140 |  | XT0017 | UA1200
[6 empty] | GR0132 | IEG0230
AU0080
PEG0130

## White Labels
(SHT 6) BECKWITH RELAY,SMT130 - (SHT 13) GEN CMPNT | (SHT 10) FG&E CTRL,SMT130 | (SHT 10) FG&E CTRL,SMT130 - (SHT 11) POWERDIST, PANEL | (SHT 13) GEN CMPNT | (SHT 13) GEN CMPNT - (SHT 12) MCC PNL,SMT130 | (SHT 13) GEN CMPNT - (SHT 9) PLC, PANEL | (SHT 13) GEN CMPNT - (SHT 11) POWERDIST, PANEL | (SHT 12) MCC PNL,SMT130 | (SHT 12) MCC PNL,SMT130 - (SHT 11) POWERDIST, PANEL | (SHT 9) PLC, PANEL | (SHT 2) PNL A,SMT130 | (SHT 2) PNL A,SMT130 - (SHT 3) PNL B,SMT130 | (SHT 3) PNL B,SMT130 | (SHT 11) POWERDIST, PANEL | (SHT 11) POWERDIST, PANEL - (SHT 7) TCP, SMT130
VGENN | IEG03562 | IEG224013 | AT0140LS(S) | PEG224014 | IEG01407 | IEG224014 | AF0294G | 0V | UV0600G | AF0083G | IEG02303 | AF0065G | GR0146 | AU0200G
| XT05002 |  | AU0120G |  |  |  | AF0295G | GR0290 |  | AF0084G | IEG02304 | AF0066G |  | IEG22404
|  |  | AU0180G |  |  |  | AU0290G | IEG22403 |  | AF0085G | IEG02305 | AF0067G
|  |  | EXCS | [6 empty] | AU0080G | IEG02307 | AF0071G
|  |  | IEG01401 | [8 empty] | AF0072G
|  |  | IEG01402 | [8 empty] | AF0073G
|  |  | IEG01404 | [8 empty] | AF045032
|  |  | PEG01404 | [8 empty] | AU0060G
|  |  | PEG01405 | [8 empty] | AU0070G
|  |  | PMGS | [8 empty] | IEG02301
|  |  | VBUSN | [8 empty] | IEG023011
|  |  | WC8101 | [8 empty] | IEG02302
|  |  | WC8102 | [8 empty] | IEG02306
|  |  | WC8201 | [8 empty] | IEG02308
|  |  | WC8301 | [8 empty] | IEG02309
XT04001

## Heat Shrink Labels
(SHT 10) FG&E CTRL,SMT130 | (SHT 13) GEN CMPNT | (SHT 13) GEN CMPNT - (SHT 12) MCC PNL,SMT130 | (SHT 3) PNL B,SMT130
WC1242 | WC8009 | WC7622 | WC4524
WC1243
WC1244
WC1245
WC1246
WC8066
WC8067
WC8069
WC8071

## BECKWITH RELAY,SMT130
BECKWITH RELAY,SMT130
Project # | 4L321
Project Name | Enterprise SMT130 M4 WTX
Revision | 0.1
Controls DE
Phone:
Controls ME
Phone:
From | [5 empty] | To
Device ID | Cable (W) Conductor (SC) Jumper Clip (JC) | Wire No. | Wire ID | Gauge/Size | Page/Zone | Device ID | Location | Page/Zone
KA0460:FG | SC | KA0460G | GRN/YEL | 8 | 40.A3 | FRAME | GEN CMPNT | 40.D5
KA0460:10 | SC | KA046010 | WHT | 20 | 40.A3 | KA0330:22 | GEN CMPNT | 40.A2
KA0460:11 | SC | KA046011 | WHT | 20 | 40.A3 | KA2672:11 | GEN CMPNT | 40.A2
KA0460:12 | SC | KA046012 | WHT | 20 | 40.A3 | AF0181:39 | GEN CMPNT | 40.A6
KA0460:13 | SC | KA046013 | WHT | 20 | 40.A3 | AF0181:07 | GEN CMPNT | 40.A6
KA0460:15 | SC | KA046015 | WHT | 20 | 40.A3 | AF0181:40 | GEN CMPNT | 40.B6
KA0460:16 | SC | KA046016 | WHT | 20 | 40.A3 | AF0181:08 | GEN CMPNT | 40.B6
KA0460:18 | SC | KA046018 | WHT | 20 | 40.A3 | AF0181:41 | GEN CMPNT | 40.B6
KA0460:19 | SC | KA046019 | WHT | 20 | 40.A3 | AF0181:09 | GEN CMPNT | 40.B6
KA0460:23 | SC | KA046023 | WHT | 20 | 40.A3 | AF0122:09 | GEN CMPNT | 40.C6
KA0460:24 | SC | KA046024 | WHT | 20 | 40.A3 | AF0122:41 | GEN CMPNT | 40.C6
KA0460:29 | SC | KA046029 | WHT | 20 | 40.A3 | AF0181:10 | GEN CMPNT | 40.C6
KA0460:30 | SC | KA046030 | WHT | 20 | 40.A3 | AF0181:42 | GEN CMPNT | 40.C6
KA0460:31 | SC | FU0460 | WHT | 14 | 40.A3 | XT0460:2 | GEN CMPNT | 40.C3
KA0460:32 | SC | KA046032 | WHT | 14 | 40.A3 | XT0460:4 | GEN CMPNT | 40.C3
KA0460:33 | SC | FU0460 | WHT | 14 | 40.A3 | XT0460:3 | GEN CMPNT | 40.C3
KA0460:34 | SC | KA0333A1 | WHT | 20 | 40.A3 | XT0460:5 | GEN CMPNT | 40.D3
KA0460:38 | SC | VGENN | GRN/YEL | 16 | 107.D7 | XT0351:13 | GEN CMPNT | 107.D5
KA0460:39 | SC | VGENA | RED | 16 | 107.D7 | XT0351:9 | GEN CMPNT | 107.C5
KA0460:40 | SC | VGENN | GRN/YEL | 16 | 107.D7 | XT0351:13 | GEN CMPNT | 107.D5
KA0460:41 | SC | VGENB | RED | 16 | 107.D7 | XT0351:10 | GEN CMPNT | 107.D5
KA0460:42 | SC | VGENN | GRN/YEL | 16 | 107.D7 | XT0351:14 | GEN CMPNT | 107.D5
KA0460:43 | SC | VGENC | RED | 16 | 107.D7 | XT0351:11 | GEN CMPNT | 107.D5
KA0460:46 | SC | DCTAX1 | BLU | 12 | 107.A7 | XT0353:1 | GEN CMPNT | 107.A5
KA0460:47 | SC | DCTX2N | BLU | 12 | 107.A7 | XT0353:4 | GEN CMPNT | 107.A6
KA0460:48 | SC | DCTBX1 | BLU | 12 | 107.A7 | XT0353:2 | GEN CMPNT | 107.A5
KA0460:49 | SC | DCTX2N | BLU | 12 | 107.A7 | XT0353:5 | GEN CMPNT | 107.A6
KA0460:5 | SC | KA04605 | WHT | 20 | 40.A3 | KA0330:24 | GEN CMPNT | 40.A2
KA0460:50 | SC | DCTCX1 | BLU | 12 | 107.A7 | XT0353:3 | GEN CMPNT | 107.A5
KA0460:51 | SC | DCTX2N | BLU | 12 | 107.A7 | XT0353:6 | GEN CMPNT | 107.A6
KA0460:54 | SC | DCT01 | BLU | 12 | 102.C7 | XT0454:4 | GEN CMPNT | 102.C4
KA0460:55 | SC | DCT02 | BLU | 12 | 102.C7 | XT0454:1 | GEN CMPNT | 102.C4
KA0460:56 | SC | DCT01 | BLU | 12 | 102.C7 | XT0454:5 | GEN CMPNT | 102.C4
KA0460:57 | SC | DCT03 | BLU | 12 | 102.C7 | XT0454:2 | GEN CMPNT | 102.C4
KA0460:58 | SC | DCT01 | BLU | 12 | 102.C7 | XT0454:6 | GEN CMPNT | 102.D4
KA0460:59 | SC | DCT06 | BLU | 12 | 102.C7 | XT0454:3 | GEN CMPNT | 102.D4
KA0460:6 | SC | KA04606 | WHT | 20 | 40.A3 | KA2672:14 | GEN CMPNT | 40.A2
KA0460:62 | SC | FU0460 | WHT | 14 | 40.A3 | XT0460:1 | GEN CMPNT | 40.C3
KA0460:64 | SC | VBUSB | RED | 16 | 107.C6 | XT0351:3 | GEN CMPNT | 107.B5
KA0460:65 | SC | VBUSA | RED | 16 | 107.C6 | XT0351:1 | GEN CMPNT | 107.B5
KA0460:63 | SC | 0V | WHT | 14 | 40.A3 | XT0104:6 | POWERDIST, PANEL | 19.C2
SolarTools ver. 24.0.84.24712 (Jul 31, 2025)
Report date: 2/3/2026 11:55 AM

## CONTROL,2-BAY
CONTROL,2-BAY
Project # | 4L321
Project Name | Enterprise SMT130 M4 WTX
Revision | 0.1
Controls DE
Phone:
Controls ME
Phone:
From | [5 empty] | To
Device ID | Cable (W) Conductor (SC) Jumper Clip (JC) | Wire No. | Wire ID | Gauge/Size | Page/Zone | Device ID | Location | Page/Zone
EL0273:SW- | SC | 0V | WHT | 16 | 35.B4 | XT0562:2 | PWR DST,DR,SMT130 | 35.B2
EL0273:SW+ | SC | FU0273 | WHT | 16 | 35.B4 | FU0273:LD | PWR DST,DR,SMT130 | 35.B3
SolarTools ver. 24.0.84.24712 (Jul 31, 2025)
Report date: 2/3/2026 11:55 AM

## FG&E CTRL,SMT130
FG&E CTRL,SMT130
Project # | 4L321
Project Name | Enterprise SMT130 M4 WTX
Revision | 0.1
Controls DE
Phone:
Controls ME
Phone:
From | [5 empty] | To
Device ID | Cable (W) Conductor (SC) Jumper Clip (JC) | Wire No. | Wire ID | Gauge/Size | Page/Zone | Device ID | Location | Page/Zone
XT0170:1 | JC | FU0170 | CLIP | --- | 34.A2 | XT0170:2 | FG&E CTRL,SMT130 | 34.A2
XT0170:3 | JC | 0V | CLIP | --- | 34.A2 | XT0170:4 | FG&E CTRL,SMT130 | 34.A2
XT0510:2 | JC | FU0500 | CLIP | --- | 33.A5 | XT0510:1 | FG&E CTRL,SMT130 | 33.A5
XT0510:3 | JC | 0V | CLIP | --- | 33.A5 | XT0510:4 | FG&E CTRL,SMT130 | 33.A5
AF0500:12 | SC | XT05002 | GRN | 16 | 33.B5 | XT0500:2 | FG&E CTRL,SMT130 | 33.C5
AF0510:32 | SC | XT05002 | GRN | 16 | 33.B4 | XT0500:2 | FG&E CTRL,SMT130 | 33.C5
AF0510:53 | SC | 0V | WHT | 16 | 33.B4 | XT0510:3 | FG&E CTRL,SMT130 | 33.A5
AF0510:55 | SC | FU0510 | WHT | 16 | 33.B4 | FU0510:LD | FG&E CTRL,SMT130 | 33.A4
AT0170:1 | SC | UV01705 | WHT | 14 | 34.A5 | UV0170:5(+) | FG&E CTRL,SMT130 | 34.A3
AT0170:11 | SC | SA017023 | WHT | 20 | 46.A6 | XT0170:5 | FG&E CTRL,SMT130 | 46.A6
AT0170:12 | SC | SA017024 | WHT | 20 | 46.A6 | XT0170:6 | FG&E CTRL,SMT130 | 46.A6
AT0170:2 | SC | UV01706 | WHT | 14 | 34.A5 | UV0170:6(-) | FG&E CTRL,SMT130 | 34.A3
AT0170:25 | SC | KA0172A1 | WHT | 20 | 34.B3 | KA0172:A1 | FG&E CTRL,SMT130 | 34.B2
AT0170:3 | SC | UV01707 | WHT | 14 | 34.A5 | UV0170:7(+) | FG&E CTRL,SMT130 | 34.A3
AT0170:31 | SC | KA0174A1 | WHT | 20 | 34.C3 | KA0174:A1 | FG&E CTRL,SMT130 | 34.C2
AT0170:4 | SC | UV01708 | WHT | 14 | 34.A5 | UV0170:8(-) | FG&E CTRL,SMT130 | 34.A3
AT0170:43 | SC | KA0179A1 | WHT | 20 | 34.C3 | KA0179:A1 | FG&E CTRL,SMT130 | 34.C2
AT0170:45 | SC | AT017045 | WHT | 20 | 131.A6 | XT0173:12 | FG&E CTRL,SMT130 | 131.A5
AT0170:46 | SC | AT017046 | WHT | 20 | 131.A6 | XT0173:13 | FG&E CTRL,SMT130 | 131.B5
AT0170:51 | SC | LON2S1 | WHT | 14 | 127.B6 | XT0172:3 | FG&E CTRL,SMT130 | 127.B6
AT0170:52 | SC | LON2B | WHT | 14 | 127.B6 | XT0172:2 | FG&E CTRL,SMT130 | 127.B6
AT0170:53 | SC | LON2A | WHT | 14 | 127.B6 | XT0172:1 | FG&E CTRL,SMT130 | 127.B6
AT0170:GND | SC | AT0170G | GRN/YEL | 14 | 34.A5 | FRAME | FG&E CTRL,SMT130 | 34.B6
AT0171:17 | SC | VD0975A | WHT | 20 | 48.A6 | XT0171:11 | FG&E CTRL,SMT130 | 48.A6
AT0171:18 | SC | HL09712 | WHT | 20 | 48.A6 | XT0171:12 | FG&E CTRL,SMT130 | 48.B6
AT0171:1P1 | SC | AT01784P1 | WHT | 14 | 34.D1 | AT0178:4P1 | FG&E CTRL,SMT130 | 34.D5
AT0171:2 | SC | SB097023 | WHT | 20 | 48.A6 | XT0171:9 | FG&E CTRL,SMT130 | 48.A6
AT0171:20 | SC | VD0975I | WHT | 20 | 48.B6 | XT0171:13 | FG&E CTRL,SMT130 | 48.B6
AT0171:21 | SC | HL09722 | WHT | 20 | 48.B6 | XT0171:14 | FG&E CTRL,SMT130 | 48.B6
AT0171:23 | SC | VD0975D | WHT | 20 | 48.B6 | XT0171:15 | FG&E CTRL,SMT130 | 48.B6
AT0171:24 | SC | HL09732 | WHT | 20 | 48.B6 | XT0171:16 | FG&E CTRL,SMT130 | 48.B6
AT0171:2P1 | SC | AT01785P1 | WHT | 14 | 34.D1 | AT0178:5P1 | FG&E CTRL,SMT130 | 34.D5
AT0171:3 | SC | SB097024 | WHT | 20 | 48.A6 | XT0171:10 | FG&E CTRL,SMT130 | 48.A6
AT0171:5 | SC | RR76135 | LEAD | --- | 112.B6 | RR7613: -10K OHM | FG&E CTRL,SMT130 | 112.B6
AT0171:6 | SC | RR76136 | LEAD | --- | 112.B6 | RR7613: -10K OHM | FG&E CTRL,SMT130 | 112.B6
AT0171:GND | SC | AT0171G | GRN/YEL | 14 | 34.D1 | FRAME | FG&E CTRL,SMT130 | 34.D2
AT0175:11 | SC | 017511 | WHT | 20 | 115.A6 | KA6510:12 | FG&E CTRL,SMT130 | 115.A6
AT0175:14 | SC | AT017514 | LEAD | --- | 115.A6 | RR1755: -10K OHM | FG&E CTRL,SMT130 | 115.A6
AT0175:15 | SC | AT017515 | LEAD | --- | 115.A6 | RR1755: -10K OHM | FG&E CTRL,SMT130 | 115.A6
AT0175:17 | SC | VD0175A | WHT | 20 | 46.B6 | XT0171:3 | FG&E CTRL,SMT130 | 46.B6
AT0175:18 | SC | HL01712 | WHT | 20 | 46.B6 | XT0171:4 | FG&E CTRL,SMT130 | 46.B6
AT0175:1P1 | SC | UV01709 | WHT | 14 | 34.B5 | UV0170:9(+) | FG&E CTRL,SMT130 | 34.A3
AT0175:2 | SC | SB017023 | WHT | 20 | 46.B6 | XT0171:1 | FG&E CTRL,SMT130 | 46.B6
AT0175:20 | SC | VD0175I | WHT | 20 | 46.C6 | XT0171:5 | FG&E CTRL,SMT130 | 46.C6
AT0175:21 | SC | HL01722 | WHT | 20 | 46.C6 | XT0171:6 | FG&E CTRL,SMT130 | 46.C6
AT0175:23 | SC | VD0175D | WHT | 20 | 46.C6 | XT0171:7 | FG&E CTRL,SMT130 | 46.C6
AT0175:24 | SC | HL01732 | WHT | 20 | 46.C6 | XT0171:8 | FG&E CTRL,SMT130 | 46.C6
AT0175:2P1 | SC | UV017010 | WHT | 14 | 34.B5 | UV0170:10(-) | FG&E CTRL,SMT130 | 34.A3
AT0175:3 | SC | SB017024 | WHT | 20 | 46.B6 | XT0171:2 | FG&E CTRL,SMT130 | 46.B6
AT0175:4P1 | SC | AT01754P1 | WHT | 20 | 34.B5 | XT0170:13 | FG&E CTRL,SMT130 | 46.A5
AT0175:5P1 | SC | KA6510A2 | WHT | 20 | 34.B5 | KA6510:A2 | FG&E CTRL,SMT130 | 46.A5
AT0175:GND | SC | AT0175G | GRN/YEL | 14 | 34.B5 | FRAME | FG&E CTRL,SMT130 | 34.C6
AT0176:14 | SC | RR761114 | LEAD | --- | 112.B6 | RR7611:-10K OHM | FG&E CTRL,SMT130 | 112.B6
AT0176:15 | SC | RR761115 | LEAD | --- | 112.B6 | RR7611:-10K OHM | FG&E CTRL,SMT130 | 112.B6
AT0176:17 | SC | 017617 | WHT | 20 | 115.B6 | KA6510:22 | FG&E CTRL,SMT130 | 115.B6
AT0176:1P1 | SC | UV017011 | WHT | 14 | 34.C5 | UV0170:11(+) | FG&E CTRL,SMT130 | 34.A3
AT0176:20 | SC | RR761020 | LEAD | --- | 112.C6 | RR7610:-10K OHM | FG&E CTRL,SMT130 | 112.C6
AT0176:21 | SC | RR761021 | LEAD | --- | 112.C6 | RR7610:-10K OHM | FG&E CTRL,SMT130 | 112.C6
AT0176:2P1 | SC | UV017012 | WHT | 14 | 34.C5 | UV0170:12(-) | FG&E CTRL,SMT130 | 34.A3
AT0176:4P1 | SC | AT01764P1 | WHT | 14 | 34.C5 | AT0178:1P1 | FG&E CTRL,SMT130 | 34.D5
AT0176:5P1 | SC | AT01765P1 | WHT | 14 | 34.C5 | AT0178:2P1 | FG&E CTRL,SMT130 | 34.D5
AT0176:GND | SC | AT0176G | GRN/YEL | 14 | 34.C5 | FRAME | FG&E CTRL,SMT130 | 34.C6
AT0178:23 | SC | AT017823 | WHT | 20 | 28.D6 | XT0170:11 | FG&E CTRL,SMT130 | 28.D6
AT0178:24 | SC | 017824 | WHT | 20 | 28.D6 | XT0170:12 | FG&E CTRL,SMT130 | 28.D6
AT0178:GND | SC | AT0178G | GRN/YEL | 14 | 34.D5 | FRAME | FG&E CTRL,SMT130 | 34.D6
FU0170:LD | SC | FU0170 | WHT | 14 | 34.A2 | XT0170:2 | FG&E CTRL,SMT130 | 34.A2
FU0171:LD | SC | FU0171 | WHT | 14 | 34.A2 | UV0170:3(+) | FG&E CTRL,SMT130 | 34.A3
FU0171:LD | SC | FU0171 | WHT | 14 | 34.A2 | UV0170:1(+) | FG&E CTRL,SMT130 | 34.A3
FU0171:LI | SC | FU0170 | WHT | 14 | 34.A2 | XT0170:2 | FG&E CTRL,SMT130 | 34.A2
FU0510:LI | SC | FU0500 | WHT | 14 | 33.A4 | XT0510:1 | FG&E CTRL,SMT130 | 33.A5
GR0170: | SC | GR0170 | GRN/YEL | 14 | 17.B4 | FRAME | FG&E CTRL,SMT130 | 17.B4
GR0172: | SC | GR0172 | GRN/YEL | 14 | 17.C4 | FRAME | FG&E CTRL,SMT130 | 17.C4
IEG0356:2 | SC | IEG03562 | GRN | 14 | 33.C5 | XT0500:1 | FG&E CTRL,SMT130 | 33.C5
KA0172:11 | SC | KA017211 | WHT | 20 | 131.B6 | XT0173:14 | FG&E CTRL,SMT130 | 131.B5
KA0172:12 | SC | KA017212 | WHT | 20 | 131.B6 | KA0179:11 | FG&E CTRL,SMT130 | 131.B6
KA0172:A2 | SC | 0V | WHT | 20 | 34.B2 | KA0174:A2 | FG&E CTRL,SMT130 | 34.C2
KA0172:A2 | SC | 0V | WHT | 20 | 34.B2 | XT0170:4 | FG&E CTRL,SMT130 | 34.A2
KA0174:11 | SC | KA017411 | WHT | 20 | 131.B6 | XT0173:16 | FG&E CTRL,SMT130 | 131.B5
KA0174:12 | SC | KA017412 | WHT | 20 | 131.B6 | XT0173:17 | FG&E CTRL,SMT130 | 131.B5
KA0174:A2 | SC | 0V | WHT | 20 | 34.C2 | KA0179:A2 | FG&E CTRL,SMT130 | 34.C2
KA0179:12 | SC | KA017912 | WHT | 20 | 131.B6 | XT0173:15 | FG&E CTRL,SMT130 | 131.B5
KA6510:A1 | SC | SA017013 | WHT | 20 | 46.A5 | XT0170:14 | FG&E CTRL,SMT130 | 46.A5
RR0178: -10K OHM | SC | AT017823 | LEAD | --- | 28.D6 | XT0170:11 | FG&E CTRL,SMT130 | 28.D6
RR0178: -10K OHM | SC | 017824 | LEAD | --- | 28.D6 | XT0170:12 | FG&E CTRL,SMT130 | 28.D6
RR7614: -10K OHM | SC | AT01782 | LEAD | --- | 113.B6 | UAI6611:7 | FG&E CTRL,SMT130 | 113.B5
RR7614: -10K OHM | SC | AT01783 | LEAD | --- | 113.B6 | UAI6611:8 | FG&E CTRL,SMT130 | 113.B5
RR7615: -10K OHM | SC | AT01785 | LEAD | --- | 113.B6 | UAI6611:10 | FG&E CTRL,SMT130 | 113.B5
RR7615: -10K OHM | SC | AT01786 | LEAD | --- | 113.B6 | UAI6611:11 | FG&E CTRL,SMT130 | 113.B5
RR7616: -10K OHM | SC | AT01788 | LEAD | --- | 113.D6 | UAI6621:7 | FG&E CTRL,SMT130 | 113.D5
RR7616: -10K OHM | SC | AT01789 | LEAD | --- | 113.D6 | UAI6621:8 | FG&E CTRL,SMT130 | 113.D5
RR7617: -10K OHM | SC | AT017811 | LEAD | --- | 113.D6 | UAI6621:10 | FG&E CTRL,SMT130 | 113.D5
RR7617: -10K OHM | SC | AT017812 | LEAD | --- | 113.D6 | UAI6621:11 | FG&E CTRL,SMT130 | 113.D5
UAI6611:10 | SC | AT01785 | WHT | 20 | 113.B5 | AT0178:5 | FG&E CTRL,SMT130 | 113.B6
UAI6611:11 | SC | AT01786 | WHT | 20 | 113.B5 | AT0178:6 | FG&E CTRL,SMT130 | 113.B6
UAI6611:14+ | SC | FU0170 | WHT | 14 | 113.B5 | XT0170:1 | FG&E CTRL,SMT130 | 34.A2
UAI6611:15- | SC | 0V | WHT | 14 | 113.B5 | XT0170:3 | FG&E CTRL,SMT130 | 34.A2
UAI6611:7 | SC | AT01782 | WHT | 20 | 113.B5 | AT0178:2 | FG&E CTRL,SMT130 | 113.B6
UAI6611:8 | SC | AT01783 | WHT | 20 | 113.B5 | AT0178:3 | FG&E CTRL,SMT130 | 113.B6
UAI6621:10 | SC | AT017811 | WHT | 20 | 113.D5 | AT0178:11 | FG&E CTRL,SMT130 | 113.D6
UAI6621:11 | SC | AT017812 | WHT | 20 | 113.D5 | AT0178:12 | FG&E CTRL,SMT130 | 113.D6
UAI6621:14+ | SC | FU0170 | WHT | 14 | 113.D5 | XT0170:1 | FG&E CTRL,SMT130 | 34.A2
UAI6621:15- | SC | 0V | WHT | 14 | 113.D5 | XT0170:4 | FG&E CTRL,SMT130 | 34.A2
UAI6621:7 | SC | AT01788 | WHT | 20 | 113.D5 | AT0178:8 | FG&E CTRL,SMT130 | 113.D6
UAI6621:8 | SC | AT01789 | WHT | 20 | 113.D5 | AT0178:9 | FG&E CTRL,SMT130 | 113.D6
UV0170:13(+) | SC | LON0P | WHT | 14 | 127.A6 | XT0170:15 | FG&E CTRL,SMT130 | 127.A6
UV0170:14(-) | SC | LON0N | WHT | 14 | 127.A6 | XT0170:16 | FG&E CTRL,SMT130 | 127.A6
UV0170:15(+) | SC | LON2P | WHT | 14 | 127.A6 | XT0170:18 | FG&E CTRL,SMT130 | 127.B6
UV0170:16(-) | SC | LON2N | WHT | 14 | 127.A6 | XT0170:19 | FG&E CTRL,SMT130 | 127.C6
UV0170:2(-) | SC | 0V | WHT | 14 | 34.A3 | XT0170:3 | FG&E CTRL,SMT130 | 34.A2
UV0170:4(-) | SC | 0V | WHT | 14 | 34.A3 | XT0170:3 | FG&E CTRL,SMT130 | 34.A2
UV0170:GND | SC | UV0170G | GRN/YEL | 14 | 34.A3 | FRAME | FG&E CTRL,SMT130 | 34.B4
VD0178:--1N4007 | SC | KA0178A1 | LEAD | --- | 28.D6 | XT0170:9 | FG&E CTRL,SMT130 | 28.D5
VD0178:+-1N4007 | SC | AT017823 | LEAD | --- | 28.D6 | XT0170:11 | FG&E CTRL,SMT130 | 28.D6
XT0170:10 | SC | 017824 | WHT | 20 | 28.D5 | XT0170:12 | FG&E CTRL,SMT130 | 28.D6
XT0171:17 | SC | FU0170 | WHT | 14 | 126.A6 | XT0170:2 | FG&E CTRL,SMT130 | 34.A2
XT0171:17 | SC | FU0170 | WHT | 14 | 126.A6 | XT0173:10 | FG&E CTRL,SMT130 | 126.B6
XT0171:18 | SC | 0V | WHT | 14 | 126.A6 | XT0170:4 | FG&E CTRL,SMT130 | 34.A2
XT0171:18 | SC | 0V | WHT | 14 | 126.A6 | XT0173:11 | FG&E CTRL,SMT130 | 126.B6
XT0171:19 | SC | LON1S2 | WHT | 14 | 126.A6 | XT0173:9 | FG&E CTRL,SMT130 | 126.B6
XT0173:10 | SC | FU0170 | WHT | 14 | 126.B6 | XT0173:6 | FG&E CTRL,SMT130 | 126.D6
XT0173:11 | SC | 0V | WHT | 14 | 126.B6 | XT0173:7 | FG&E CTRL,SMT130 | 126.D6
XT0173:9 | SC | LON1S2 | WHT | 14 | 126.B6 | XT0173:8 | FG&E CTRL,SMT130 | 126.D6
AF0500:01 | WC1242 | UA42011 | RED | 20 | 99.A6 | XT0550:1 | FG&E CTRL,SMT130 | 99.A5
AF0500:02 | WC1242 | UA42012 | WHT | 20 | 99.A6 | XT0550:2 | FG&E CTRL,SMT130 | 99.A5
AF0500:03 | WC1242 | UA42013 | BLK | 20 | 99.A6 | XT0550:3 | FG&E CTRL,SMT130 | 99.A5
AF0500:07 | WC1242 | UA4201S | SH | 20 | 99.A6 | XT0550:4 | FG&E CTRL,SMT130 | 99.A5
AF0510:09 | WC1243 | UA42311 | RED | 20 | 99.B6 | XT0550:5 | FG&E CTRL,SMT130 | 99.B5
AF0510:10 | WC1243 | UA42312 | WHT | 20 | 99.B6 | XT0550:6 | FG&E CTRL,SMT130 | 99.B5
AF0510:12 | WC1243 | UA42313 | BLK | 20 | 99.B6 | XT0550:7 | FG&E CTRL,SMT130 | 99.B5
AF0510:27 | WC1243 | UA4231S | SH | 20 | 99.B6 | XT0550:8 | FG&E CTRL,SMT130 | 99.B5
AF0510:13 | WC1244 | UA42301 | RED | 20 | 99.B6 | XT0550:9 | FG&E CTRL,SMT130 | 99.B5
AF0510:14 | WC1244 | UA42302 | WHT | 20 | 99.B6 | XT0550:10 | FG&E CTRL,SMT130 | 99.B5
AF0510:16 | WC1244 | UA42303 | BLK | 20 | 99.B6 | XT0550:11 | FG&E CTRL,SMT130 | 99.B5
AF0510:31 | WC1244 | UA4230S | SH | 20 | 99.B6 | XT0550:12 | FG&E CTRL,SMT130 | 99.B5
AF0510:01 | WC1245 | UA42411 | RED | 20 | 99.C6 | XT0550:13 | FG&E CTRL,SMT130 | 99.C5
AF0510:02 | WC1245 | UA42412 | WHT | 20 | 99.C6 | XT0550:14 | FG&E CTRL,SMT130 | 99.C5
AF0510:04 | WC1245 | UA42413 | BLK | 20 | 99.C6 | XT0550:15 | FG&E CTRL,SMT130 | 99.C5
AF0510:19 | WC1245 | UA4241S | SH | 20 | 99.C6 | XT0550:16 | FG&E CTRL,SMT130 | 99.C5
AF0510:05 | WC1246 | UA42401 | RED | 20 | 99.C6 | XT0550:17 | FG&E CTRL,SMT130 | 99.C5
AF0510:06 | WC1246 | UA42402 | WHT | 20 | 99.C6 | XT0550:18 | FG&E CTRL,SMT130 | 99.C5
AF0510:08 | WC1246 | UA42403 | BLK | 20 | 99.C6 | XT0550:19 | FG&E CTRL,SMT130 | 99.C5
AF0510:23 | WC1246 | UA4240S | SH | 20 | 99.C6 | XT0550:20 | FG&E CTRL,SMT130 | 99.C5
AF0500:LBUS | WC8050 | AF0510RBUS | BUS | CABLE | 33.B5 | AF0510:RBUS | FG&E CTRL,SMT130 | 33.B4
AT0175:1P2 | WC8066 | AT01751P2 | WHT | 16 | 34.C7 | AT0176:4P2 | FG&E CTRL,SMT130 | 34.C7
AT0175:2P2 | WC8066 | AT01752P2 | BLK | 16 | 34.C7 | AT0176:5P2 | FG&E CTRL,SMT130 | 34.C7
AT0175:3P2 | WC8066 | AT01753P2 | SH | 16 | 34.C7 | AT0176:6P2 | FG&E CTRL,SMT130 | 34.C7
AT0176:1P2 | WC8067 | AT01761P2 | WHT | 16 | 34.D7 | AT0178:4P2 | FG&E CTRL,SMT130 | 34.D7
AT0176:2P2 | WC8067 | AT01762P2 | BLK | 16 | 34.D7 | AT0178:5P2 | FG&E CTRL,SMT130 | 34.D7
AT0176:3P2 | WC8067 | AT01763P2 | SH | 16 | 34.D7 | AT0178:6P2 | FG&E CTRL,SMT130 | 34.D7
AT0170:50 | WC8069 | AT017050 | WHT | 16 | 34.A7 | AT0171:4P2 | FG&E CTRL,SMT130 | 34.A7
AT0170:49 | WC8069 | AT017049 | BLK | 16 | 34.A7 | AT0171:5P2 | FG&E CTRL,SMT130 | 34.A7
AT0170:48 | WC8069 | AT017048 | SH | 16 | 34.A7 | AT0171:6P2 | FG&E CTRL,SMT130 | 34.A7
AT0171:1P2 | WC8071 | AT01711P2 | WHT | 16 | 34.B7 | AT0175:4P2 | FG&E CTRL,SMT130 | 34.B7
AT0171:2P2 | WC8071 | AT01712P2 | BLK | 16 | 34.B7 | AT0175:5P2 | FG&E CTRL,SMT130 | 34.B7
AT0171:3P2 | WC8071 | AT01713P2 | SH | 16 | 34.B7 | AT0175:6P2 | FG&E CTRL,SMT130 | 34.B7
AF0510:L1 | WC0014 | AT0140P2 | ENET | CABLE | 2.C5 | AT0140:P2 | GEN CMPNT | 2.C4
AT0170:L2 | WC0017 | AT0170L2 | ENET | CABLE | 2.C2 | AP0602:L1 | PLC, PANEL | 2.C3
FU0170:LI | SC | FU0136 | WHT | 14 | 34.A2 | XT0102:5 | POWERDIST, PANEL | 19.B2
IEG0356:0 | SC | IEG224013 | GRN | 8 | 17.C2 | IEG2240:13 | POWERDIST, PANEL | 17.C2
XT0170:3 | SC | 0V | WHT | 14 | 34.A2 | XT0104:4 | POWERDIST, PANEL | 19.C2
XT0510:1 | SC | FU0500 | WHT | 14 | 33.A5 | FU0500:LD | POWERDIST, PANEL | 19.A2
XT0510:3 | SC | 0V | WHT | 14 | 33.A5 | XT0104:2 | POWERDIST, PANEL | 19.C2
SolarTools ver. 24.0.84.24712 (Jul 31, 2025)
Report date: 2/3/2026 11:55 AM

## GEN CMPNT
GEN CMPNT
Project # | 4L321
Project Name | Enterprise SMT130 M4 WTX
Revision | 0.1
Controls DE
Phone:
Controls ME
Phone:
From | [5 empty] | To
Device ID | Cable (W) Conductor (SC) Jumper Clip (JC) | Wire No. | Wire ID | Gauge/Size | Page/Zone | Device ID | Location | Page/Zone
XT0120:1 | JC | 0V | CLIP | --- | 32.B1 | XT0120:2 | GEN CMPNT | 32.B1
XT0130:3 | JC | 0V | CLIP | --- | 32.A4 | XT0130:2 | GEN CMPNT | 32.A4
XT0180:1 | JC | 0V | CLIP | --- | 32.D1 | XT0180:2 | GEN CMPNT | 32.D1
XT0190:3 | JC | 0V | CLIP | --- | 32.B4 | XT0190:2 | GEN CMPNT | 32.C4
XT0336:2 | JC | 0V | CLIP | --- | 29.C4 | XT0336:3 | GEN CMPNT | 29.C4
XT0336:3 | JC | 0V | CLIP | --- | 29.C4 | XT0336:4 | GEN CMPNT | 29.D4
XT0336:4 | JC | 0V | CLIP | --- | 29.D4 | XT0336:5 | GEN CMPNT | 29.D4
XT0350:2 | JC | CCT1(+) | CLIP | --- | 102.A4 | XT0350:1 | GEN CMPNT | 102.A4
XT0350:4 | JC | CCT1(-) | CLIP | --- | 102.A4 | XT0350:3 | GEN CMPNT | 102.A4
XT0351:1 | JC | VBUSA | CLIP | --- | 107.B5 | XT0351:2 | GEN CMPNT | 107.B5
XT0351:12 | JC | VGENN | CLIP | --- | 107.D5 | XT0351:13 | GEN CMPNT | 107.D5
XT0351:13 | JC | VGENN | CLIP | --- | 107.D5 | XT0351:14 | GEN CMPNT | 107.D5
XT0351:3 | JC | VBUSB | CLIP | --- | 107.B5 | XT0351:4 | GEN CMPNT | 107.B5
XT0351:5 | JC | VBUSC | CLIP | --- | 107.B5 | XT0351:6 | GEN CMPNT | 107.C5
XT0351:7 | JC | VBUSN | CLIP | --- | 107.C5 | XT0351:8 | GEN CMPNT | 107.C5
XT0353:4 | JC | DCTX2N | CLIP | --- | 107.A6 | XT0353:5 | GEN CMPNT | 107.A6
XT0353:5 | JC | DCTX2N | CLIP | --- | 107.A6 | XT0353:6 | GEN CMPNT | 107.A6
XT0370:1 | JC | EXC1 | CLIP | --- | 95.C4 | XT0370:2 | GEN CMPNT | 95.C5
XT0370:4 | JC | EXC2 | CLIP | --- | 95.C4 | XT0370:3 | GEN CMPNT | 95.C5
XT0370:5 | JC | EXCS | CLIP | --- | 95.C4 | XT0370:6 | GEN CMPNT | 95.C5
XT0454:4 | JC | DCT01 | CLIP | --- | 102.C4 | XT0454:5 | GEN CMPNT | 102.C4
XT0454:5 | JC | DCT01 | CLIP | --- | 102.C4 | XT0454:6 | GEN CMPNT | 102.D4
XT0460:1 | JC | FU0460 | CLIP | --- | 40.C3 | XT0460:2 | GEN CMPNT | 40.C3
XT0460:2 | JC | FU0460 | CLIP | --- | 40.C3 | XT0460:3 | GEN CMPNT | 40.C3
AF0121:01 | SC | 012101 | WHT | 20 | 31.B7 | KA0121:A1 | GEN CMPNT | 31.B5
AF0121:03 | SC | 012103 | WHT | 20 | 30.C7 | KA0123:A1 | GEN CMPNT | 30.C5
AF0121:04 | SC | 012104 | WHT | 20 | 129.D7 | KA0185:A1 | GEN CMPNT | 129.D6
AF0121:05 | SC | KA2685A1 | WHT | 20 | 108.B6 | KA2685:A1 | GEN CMPNT | 108.B6
AF0121:08 | SC | 012108 | WHT | 20 | 31.B7 | KA0128:A1 | GEN CMPNT | 31.B5
AF0121:10 | SC | KA0340A1 | WHT | 20 | 128.A6 | KA0340:A1 | GEN CMPNT | 128.A5
AF0121:12 | SC | 012112 | WHT | 20 | 40.A6 | KA2672:A1 | GEN CMPNT | 40.A5
AF0121:17 | SC | 012117 | WHT | 20 | 31.B7 | KA0121:A2 | GEN CMPNT | 31.B5
AF0121:19 | SC | 012119 | WHT | 20 | 30.C7 | KA0123:A2 | GEN CMPNT | 30.C5
AF0121:20 | SC | 012120 | WHT | 20 | 129.D7 | KA0185:A2 | GEN CMPNT | 129.D6
AF0121:21 | SC | KA2685A2 | WHT | 20 | 108.B6 | KA2685:A2 | GEN CMPNT | 108.B6
AF0121:24 | SC | 012124 | WHT | 20 | 31.B7 | KA0128:A2 | GEN CMPNT | 31.B5
AF0121:26 | SC | KA0340A2 | WHT | 20 | 128.A6 | KA0340:A2 | GEN CMPNT | 128.A5
AF0121:28 | SC | 012128 | WHT | 20 | 40.A6 | KA2672:A2 | GEN CMPNT | 40.A5
AF0121:30 | SC | KA4100A2 | WHT | 20 | 94.A6 | KA4100:A2 | GEN CMPNT | 94.B6
AF0121:46 | SC | 012146 | WHT | 20 | 94.A6 | KA0336:12 | GEN CMPNT | 94.A6
AF0121:COM | SC | 0V | WHT | 16 | 32.B2 | XT0120:2 | GEN CMPNT | 32.B1
AF0121:V+ | SC | FU0121 | WHT | 16 | 32.B2 | FU0121:LD | GEN CMPNT | 32.B1
AF0122:00 | SC | 012200 | WHT | 20 | 31.A7 | KA0330:11 | GEN CMPNT | 31.A6
AF0122:01 | SC | 012201 | WHT | 20 | 31.A7 | KA0331:11 | GEN CMPNT | 31.A6
AF0122:02 | SC | 012202 | WHT | 20 | 30.B7 | KA0310:11 | GEN CMPNT | 30.B6
AF0122:10 | SC | KA046111 | WHT | 20 | 40.D6 | XT0460:8 | GEN CMPNT | 40.D5
AF0122:32 | SC | 012232 | WHT | 20 | 31.A7 | KA0330:14 | GEN CMPNT | 31.A6
AF0122:33 | SC | 012233 | WHT | 20 | 31.A7 | KA0331:14 | GEN CMPNT | 31.A6
AF0122:34 | SC | 012234 | WHT | 20 | 30.B7 | KA0310:14 | GEN CMPNT | 30.B6
XT0352:4 | SC | JW03524 | CLIP | -- | 102.B4 | XT0352:5 | GEN CMPNT | 102.B4
XT0352:5 | SC | JW03525 | CLIP | -- | 102.B4 | XT0352:6 | GEN CMPNT | 102.B4
XT0352:6 | SC | JW03526 | CLIP | -- | 102.B4 | XT0352:7 | GEN CMPNT | 102.B4
XT0454:7 | SC | JW0454 | CLIP | --- | 102.D4 | XT0454:6 | GEN CMPNT | 102.D4
AF0122:05 | SC | JW012205 | VIO | 20 | 100.D7 | AF0122:37 | GEN CMPNT | 100.D7
AF0122:42 | SC | KA046113 | WHT | 20 | 40.D6 | XT0460:7 | GEN CMPNT | 40.D5
AF0122:COM | SC | AF0123N | WHT | 16 | 32.B3 | AF0123:COM | GEN CMPNT | 32.B3
AF0122:COM | SC | AU0120N | WHT | 16 | 32.B3 | AU0120:COM | GEN CMPNT | 32.A2
AF0122:V+ | SC | AF0123P | WHT | 16 | 32.B3 | AF0123:V+ | GEN CMPNT | 32.B3
AF0122:V+ | SC | AU0120P | WHT | 16 | 32.B3 | AU0120:V+ | GEN CMPNT | 32.A2
AF0123:SH | SC | IEG01401 | GRN | 14 | 32.B3 | IEG0140:1 | GEN CMPNT | 32.B4
AF0123:SH | SC | AU0120G | GRN | 14 | 32.B3 | AU0120:GND | GEN CMPNT | 32.A2
AF0181:02 | SC | SB75012 | WHT | 20 | 129.A7 | XT0183:2 | GEN CMPNT | 129.A5
AF0181:03 | SC | SB75022 | WHT | 20 | 129.A7 | XT0183:4 | GEN CMPNT | 129.A5
AF0181:04 | SC | SB75032 | WHT | 20 | 129.B7 | XT0181:6 | GEN CMPNT | 129.B5
AF0181:05 | SC | KA7500NO | WHT | 20 | 129.B7 | XT0181:2 | GEN CMPNT | 129.B5
AF0181:06 | SC | SB7500NO | WHT | 20 | 129.C7 | XT0181:4 | GEN CMPNT | 129.C5
AF0181:34 | SC | SB75011 | WHT | 20 | 129.A7 | XT0183:1 | GEN CMPNT | 129.A5
AF0181:35 | SC | SB75021 | WHT | 20 | 129.A7 | XT0183:3 | GEN CMPNT | 129.A5
AF0181:36 | SC | SB75031 | WHT | 20 | 129.B7 | XT0181:5 | GEN CMPNT | 129.B5
AF0181:37 | SC | KA7500C | WHT | 20 | 129.B7 | XT0181:1 | GEN CMPNT | 129.B5
AF0181:38 | SC | SB7500C | WHT | 20 | 129.C7 | XT0181:3 | GEN CMPNT | 129.C5
AF0181:COM | SC | AF0181N | WHT | 14 | 32.D2 | AF0182:COM | GEN CMPNT | 32.D3
AF0181:COM | SC | AU0180N | WHT | 16 | 32.D2 | AU0180:COM | GEN CMPNT | 32.C2
AF0181:V+ | SC | AF0181P | WHT | 16 | 32.D2 | AF0182:V+ | GEN CMPNT | 32.D3
AF0181:V+ | SC | AU0180P | WHT | 16 | 32.D2 | AU0180:V+ | GEN CMPNT | 32.C2
AF0182:SH | SC | IEG01404 | GRN | 14 | 32.D3 | IEG0140:4 | GEN CMPNT | 32.D4
AF0182:SH | SC | AU0180G | GRN | 14 | 32.D3 | AU0180:GND | GEN CMPNT | 32.C2
AT0140:13 VGEN-A | SC | VGENA | RED | 16 | 107.D7 | XT0351:9 | GEN CMPNT | 107.C5
AT0140:14 VGEN-B | SC | VGENB | RED | 16 | 107.D7 | XT0351:10 | GEN CMPNT | 107.D5
AT0140:15 VGEN-C | SC | VGENC | RED | 16 | 107.D7 | XT0351:11 | GEN CMPNT | 107.D5
AT0140:16 VGEN-N | SC | VGENN | GRN/YEL | 16 | 107.D7 | XT0351:12 | GEN CMPNT | 107.D5
AT0140:17 VBUS-A | SC | VBUSA | RED | 16 | 107.C7 | XT0351:1 | GEN CMPNT | 107.B5
AT0140:18 VBUS-B | SC | VBUSB | RED | 16 | 107.C7 | XT0351:3 | GEN CMPNT | 107.B5
AT0140:19 VBUS-C | SC | VBUSC | RED | 16 | 107.C7 | XT0351:5 | GEN CMPNT | 107.B5
AT0140:20 VBUS-N | SC | VBUSN | GRN/YEL | 16 | 107.C7 | XT0351:7 | GEN CMPNT | 107.C5
AT0140:27 ID RLY | SC | CCT1(+) | BLU | 12 | 102.A7 | XT0350:2 | GEN CMPNT | 102.A4
AT0140:28 ID RLY | SC | CCT1(-) | BLU | 12 | 102.A7 | XT0350:4 | GEN CMPNT | 102.A4
AT0140:3 EX-D(-) | SC | 0V | WHT | 16 | 100.C7 | XT0336:4 | GEN CMPNT | 29.D4
AT0140:33 ID RES(+) | SC | CCT1(+) | BLU | 12 | 102.A7 | XT0350:1 | GEN CMPNT | 102.A4
AT0140:34 ID RES(-) | SC | AT014034 | WHT | 16 | 102.A7 | AT0140:42 ID(+) | GEN CMPNT | 102.A7
AT0140:36 I1(+) | SC | MCTA | BLU | 12 | 102.B7 | XT0352:1 | GEN CMPNT | 102.B4
AT0140:37 I1(-) | SC | MCTAN | BLU | 12 | 102.B7 | XT0352:6 | GEN CMPNT | 102.B4
AT0140:38 I2(+) | SC | MCTB | BLU | 12 | 102.B7 | XT0352:2 | GEN CMPNT | 102.B4
AT0140:39 I2(-) | SC | MCTBN | BLU | 12 | 102.B7 | XT0352:5 | GEN CMPNT | 102.B4
AT0140:4 EX-D(+) | SC | KA012314 | WHT | 16 | 100.C7 | KA0123:14 | GEN CMPNT | 30.A6
AT0140:40 I3(+) | SC | MCTC | BLU | 12 | 102.B7 | XT0352:3 | GEN CMPNT | 102.B4
AT0140:41 I3(-) | SC | MCTN | BLU | 12 | 102.B7 | XT0352:4 | GEN CMPNT | 102.B4
AT0140:43 ID(-) | SC | CCT1(-) | BLU | 12 | 102.A7 | XT0350:3 | GEN CMPNT | 102.A4
AT0140:56 FG | SC | AT0140G | GRN/YEL | 12 | 30.B3 | FRAME | GEN CMPNT | 30.B2
AT0140:BAT(-) 48 | SC | 0V | WHT | 16 | 30.B3 | XT0336:4 | GEN CMPNT | 29.D4
AT0140:BAT(+) 47 | SC | FU0334 | WHT | 20 | 30.B3 | XT0335:2 | GEN CMPNT | 30.B5
AT0140:FLT 29 | SC | KA0310A2 | WHT | 20 | 30.B3 | KA0310:A2 | GEN CMPNT | 30.B4
AT0140:FLT 30 | SC | 0V | WHT | 16 | 30.B3 | XT0336:5 | GEN CMPNT | 29.D4
AU0120:COM | SC | 0V | WHT | 16 | 32.A2 | XT0120:1 | GEN CMPNT | 32.B1
AU0120:V+ | SC | FU0120 | WHT | 16 | 32.A2 | FU0120:LD | GEN CMPNT | 32.B1
AU0180:COM | SC | 0V | WHT | 16 | 32.C2 | XT0180:1 | GEN CMPNT | 32.D1
AU0180:V+ | SC | FU0180 | WHT | 16 | 32.C2 | FU0180:LD | GEN CMPNT | 32.D1
FU0120:LI | SC | FU0332 | WHT | 14 | 32.B1 | XT0130:1 | GEN CMPNT | 32.A4
FU0120:LI | SC | FU0332 | WHT | 14 | 32.B1 | FU0121:LI | GEN CMPNT | 32.B1
FU0180:LI | SC | FU0335 | WHT | 14 | 32.D1 | XT0190:1 | GEN CMPNT | 32.C4
FU0180:LI | SC | FU0335 | WHT | 14 | 32.D1 | FU0181:LI | GEN CMPNT | 32.D1
FU0332:LD | SC | FU0332 | WHT | 14 | 29.B3 | XT0130:1 | GEN CMPNT | 32.A4
FU0332:LD | SC | FU0332 | WHT | 14 | 29.B3 | FU0333:LI | GEN CMPNT | 29.B3
FU0332:LI | SC | FU0136 | WHT | 14 | 29.B3 | XT0332:1 | GEN CMPNT | 29.B2
FU0333:LD | SC | FU0333 | WHT | 14 | 29.B3 | XT0335:1 | GEN CMPNT | 29.B4
FU0333:LI | SC | FU0332 | WHT | 14 | 29.B3 | FU0334:LI | GEN CMPNT | 30.A6
FU0334:LD | SC | FU0334 | WHT | 16 | 30.A6 | XT0335:2 | GEN CMPNT | 30.B5
FU0334:LI | SC | FU0332 | WHT | 14 | 30.A6 | FU0335:LI | GEN CMPNT | 29.A3
FU0335:LD | SC | FU0335 | WHT | 14 | 29.A3 | XT0335:3 | GEN CMPNT | 29.A4
FU0335:LI | SC | FU0332 | WHT | 14 | 29.A3 | FU0336:LI | GEN CMPNT | 29.A3
FU0336:LD | SC | FU0336 | WHT | 14 | 29.A3 | XT0335:4 | GEN CMPNT | 29.A4
GR0139: | SC | GR0139 | GRN/YEL | 14 | 17.B4 | FRAME | GEN CMPNT | 17.B4
GR0140: | SC | IEG01402 | GRN | 14 | 17.B4 | IEG0140:2 | GEN CMPNT | 17.B4
GR0141: | SC | GR0141 | GRN/YEL | 14 | 17.B4 | FRAME | GEN CMPNT | 17.B4
IEG0140:3 | SC | AT0140LS(S) | GRN | 14 | 100.C6 | XT0337:3 | GEN CMPNT | 100.C4
KA0121:11 | SC | KA012111 | WHT | 20 | 130.D5 | XT0337:17 | GEN CMPNT | 130.D4
KA0121:14 | SC | FU0333 | WHT | 20 | 130.D5 | XT0337:16 | GEN CMPNT | 130.C3
KA0123:11 | SC | FU0334 | WHT | 16 | 30.A6 | XT0335:2 | GEN CMPNT | 30.B5
KA0123:A1 | SC | 012103 | WHT | 20 | 30.C5 | KA0313:2 | GEN CMPNT | 30.C5
KA0123:A2 | SC | 012119 | WHT | 20 | 30.C5 | KA0313:7 | GEN CMPNT | 30.C5
KA0128:11 | SC | KA0333A1 | WHT | 20 | 130.B4 | KA0335:21 | GEN CMPNT | 130.B4
KA0128:14 | SC | FU0333 | WHT | 20 | 130.B4 | KA0335:22 | GEN CMPNT | 130.B4
KA0128:14 | SC | FU0333 | WHT | 20 | 130.B4 | XT0337:11 | GEN CMPNT | 130.B3
KA0185:11 | SC | KA012111 | WHT | 20 | 130.D4 | XT0337:17 | GEN CMPNT | 130.D4
KA0185:14 | SC | KA0332A1 | WHT | 20 | 130.D4 | XT0337:18 | GEN CMPNT | 130.D4
KA0310:21 | SC | KA0333A1 | WHT | 20 | 130.B4 | KA0335:21 | GEN CMPNT | 130.B4
KA0310:21 | SC | KA0333A1 | WHT | 20 | 130.B4 | XT0337:12 | GEN CMPNT | 130.B3
KA0310:24 | SC | FU0333 | WHT | 20 | 130.B4 | KA0335:22 | GEN CMPNT | 130.B4
KA0310:A1 | SC | FU0334 | WHT | 20 | 30.B4 | XT0335:2 | GEN CMPNT | 30.B5
KA0313:2 | SC | 012103 | WHT | 20 | 30.C5 | KA0314:2 | GEN CMPNT | 30.C5
KA0313:7 | SC | 012119 | WHT | 20 | 30.C5 | KA0314:7 | GEN CMPNT | 30.C5
KA0330:21 | SC | KA046011 | WHT | 20 | 40.A2 | KA2672:11 | GEN CMPNT | 40.A2
KA0330:A1 | SC | KA0330A1 | WHT | 20 | 130.B6 | XT0337:13 | GEN CMPNT | 130.B3
KA0330:A2 | SC | 0V | WHT | 20 | 130.B6 | KA0333:A2 | GEN CMPNT | 130.B6
KA0330:A2 | SC | 0V | WHT | 20 | 130.B6 | KA0331:A2 | GEN CMPNT | 130.C6
KA0331:A1 | SC | KA0331A1 | WHT | 16 | 130.C6 | XT0337:14 | GEN CMPNT | 130.C3
KA0331:A2 | SC | 0V | WHT | 20 | 130.C6 | KA0332:A2 | GEN CMPNT | 130.D6
KA0332:11 | SC | KA033211 | WHT | 20 | 31.D6 | XT0337:7 | GEN CMPNT | 31.D5
KA0332:14 | SC | KA033214 | WHT | 20 | 31.D6 | XT0337:8 | GEN CMPNT | 31.D5
KA0332:A1 | SC | KA0332A1 | WHT | 20 | 130.D6 | XT0337:18 | GEN CMPNT | 130.D4
KA0332:A2 | SC | 0V | WHT | 20 | 130.D6 | XT0337:19 | GEN CMPNT | 130.D3
KA0333:11 | SC | KA033311 | WHT | 20 | 31.D6 | KA0335:11 | GEN CMPNT | 31.D6
KA0333:11 | SC | KA033311 | WHT | 20 | 31.D6 | XT0337:10 | GEN CMPNT | 31.D5
KA0333:14 | SC | KA033314 | WHT | 20 | 31.D6 | KA0335:12 | GEN CMPNT | 31.D6
KA0333:14 | SC | KA033314 | WHT | 20 | 31.D6 | XT0337:9 | GEN CMPNT | 31.D5
KA0333:A1 | SC | KA0333A1 | WHT | 20 | 130.B6 | XT0337:12 | GEN CMPNT | 130.B3
KA0335:A1 | SC | ESTOP | WHT | 20 | 29.C5 | XT0336:1 | GEN CMPNT | 29.C4
KA0335:A2 | SC | 0V | WHT | 20 | 29.C5 | XT0336:2 | GEN CMPNT | 29.C4
KA0336:11 | SC | KA033611 | WHT | 20 | 94.A6 | AF0121:14 | GEN CMPNT | 94.A6
KA0336:11 | SC | KA033611 | WHT | 20 | 94.A6 | KA4100:A1 | GEN CMPNT | 94.B6
KA0336:A1 | SC | KA0231A1 | WHT | 16 | 29.C3 | XT0334:2 | GEN CMPNT | 29.C2
KA0336:A2 | SC | 0V | WHT | 20 | 29.C3 | XT0336:2 | GEN CMPNT | 29.C4
KA2320:11 | SC | KM3220EP | RED | 16 | 91.C5 | XT2910:9 | GEN CMPNT | 91.B5
KA2320:14 | SC | KM3220EN | RED | 16 | 91.C5 | XT2910:10 | GEN CMPNT | 91.C5
KA3103:11 | SC | KM3103EN | RED | 16 | 80.A5 | XT2910:2 | GEN CMPNT | 80.A5
KA3103:14 | SC | KM3103EP | RED | 16 | 80.A5 | XT2910:1 | GEN CMPNT | 80.A5
KA3420:11 | SC | KM3420EN | RED | 16 | 101.C5 | XT2910:8 | GEN CMPNT | 101.C5
KA3420:14 | SC | KM3420EP | RED | 16 | 101.C5 | XT2910:7 | GEN CMPNT | 101.B5
KA4100:11 | SC | KM4100EN | RED | 16 | 94.A5 | XT2910:6 | GEN CMPNT | 94.A5
KA4100:14 | SC | KM4100EP | RED | 16 | 94.A5 | XT2910:5 | GEN CMPNT | 94.A5
PEG0140:2 | SC | PMGS | GRN/YEL | 16 | 95.A6 | XT0313:1 | GEN CMPNT | 95.A6
PEG0140:3 | SC | EXCS | GRN/YEL | 16 | 95.C5 | XT0370:6 | GEN CMPNT | 95.C5
PEG0140:4 | SC | PEG01404 | GRN/YEL | 12 | 102.B5 | XT0352:7 | GEN CMPNT | 102.B4
PEG0140:5 | SC | PEG01405 | GRN/YEL | 12 | 102.D5 | XT0454:7 | GEN CMPNT | 102.D4
XT0120:1 | SC | 0V | WHT | 14 | 32.B1 | XT0130:2 | GEN CMPNT | 32.A4
XT0180:1 | SC | 0V | WHT | 14 | 32.D1 | XT0190:2 | GEN CMPNT | 32.C4
XT0334:1 | SC | 0V | WHT | 20 | 29.C2 | XT0336:2 | GEN CMPNT | 29.C4
XT0335:3 | SC | FU0335 | WHT | 14 | 29.A4 | XT0190:1 | GEN CMPNT | 32.C4
XT0336:3 | SC | 0V | WHT | 14 | 29.C4 | XT0130:2 | GEN CMPNT | 32.A4
XT0336:3 | SC | 0V | WHT | 14 | 29.C4 | XT0190:2 | GEN CMPNT | 32.C4
XT0337:11 | SC | FU0333 | WHT | 20 | 130.B3 | XT0337:15 | GEN CMPNT | 130.C3
XT0337:15 | SC | FU0333 | WHT | 20 | 130.C3 | XT0337:16 | GEN CMPNT | 130.C3
XT0337:16 | SC | FU0333 | WHT | 20 | 130.C3 | XT0335:1 | GEN CMPNT | 29.B4
XT0337:19 | SC | 0V | WHT | 14 | 130.D3 | XT0336:3 | GEN CMPNT | 29.C4
AU0120:L2 | WC0012 | AU0120L2 | ENET | CABLE | 2.C2 | AU0180:L1 | GEN CMPNT | 2.C3
AT0140:P1 | WC0018 | AU0180L2 | ENET | CABLE | 2.C4 | AU0180:L2 | GEN CMPNT | 2.C3
AT0140:1 LS(+) | WC8009 | AT0140LS(+) | WHT | 16 | 100.C7 | XT0337:1 | GEN CMPNT | 100.C4
AT0140:2 LS(-) | WC8009 | AT0140LS(-) | BLK | 16 | 100.C7 | XT0337:2 | GEN CMPNT | 100.C4
FW5:1 | WC8009 | AT0140LS(S) | SH | 16 | 100.C6 | XT0337:3 | GEN CMPNT | 100.C4
FU0315:LD | WC8101 | PMG1 | RED | 12 | 95.A5 | XT0360:1 | GEN CMPNT | 95.A4
FU0313:LD | WC8101 | PMG2 | WHT | 12 | 95.A5 | XT0360:2 | GEN CMPNT | 95.A4
FU0314:LD | WC8101 | PMG3 | BLK | 12 | 95.A5 | XT0360:3 | GEN CMPNT | 95.A4
XT0360:5 | WC8101 | PMGS | SH | 12 | 95.A4 | XT0360:4 | GEN CMPNT | 95.A5
AT0140:54 EXC(+) | WC8102 | EXC1 | WHT | 12 | 95.C7 | XT0370:2 | GEN CMPNT | 95.C5
AT0140:55 EXC(-) | WC8102 | EXC2 | BLK | 12 | 95.C7 | XT0370:3 | GEN CMPNT | 95.C5
XT0370:6 | WC8102 | EXCS | SH | 12 | 95.C5 | FLOATING | GEN CMPNT | 95.C6
FU0315:LI | WC8201 | FU0315 | RED | 12 | 95.A5 | KA0314:1 | GEN CMPNT | 95.A6
FU0313:LI | WC8201 | FU0313 | WHT | 12 | 95.A5 | KA0313:1 | GEN CMPNT | 95.A6
FU0314:LI | WC8201 | FU0314 | BLK | 12 | 95.A5 | KA0313:8 | GEN CMPNT | 95.A6
XT0360:4 | WC8201 | PMGS | SH | 12 | 95.A5 | XT0313:1 | GEN CMPNT | 95.A6
AT0140:49 PMG-A | WC8301 | KA03143 | RED | 12 | 95.A7 | KA0314:3 | GEN CMPNT | 95.A6
AT0140:50 PMG-B | WC8301 | KA03133 | WHT | 12 | 95.A7 | KA0313:3 | GEN CMPNT | 95.A6
AT0140:51 PMG-C | WC8301 | KA03136 | BLK | 12 | 95.A7 | KA0313:6 | GEN CMPNT | 95.A6
FLOATING | WC8301 | PMGS | SH | 12 | 95.A6 | XT0313:1 | GEN CMPNT | 95.A6
XT0350:1 | SC | CCT1(+) | BLU | 12 | 102.A4 | XT7720:1 | JB772 | 100.A3
XT0350:4 | SC | CCT1(-) | BLU | 12 | 102.A4 | XT7720:2 | JB772 | 100.B3
XT0337:1 | WC7701 | AT0140LS(+) | WHT-PR1 | 18 | 100.C4 | XT7701:5 | JB770 | 100.C3
XT0337:2 | WC7701 | AT0140LS(-) | BLK-PR1 | 18 | 100.C4 | XT7701:6 | JB770 | 100.C3
XT0337:3 | WC7701 | AT0140LS(S) | SH-PR1 | 18 | 100.C4 | XT7701:7 | JB770 | 100.C3
XT0337:4 | WC7701 | 029338 | WHT-PR2 | 18 | 129.C5 | XT7701:18 | JB770 | 129.C4
XT0337:5 | WC7701 | 029306 | BLK-PR2 | 18 | 129.C5 | XT7701:19 | JB770 | 129.C4
XT0337:6 | WC7701 | 029354 | SH-PR2 | 18 | 129.C5 | XT7701:20 | JB770 | 129.C4
KA0340:11 | WC7901 | KA034011 | 1 | 16GA | 128.A6 | XT7701:1 | JB770 | 128.A3
KA0340:12 | WC7901 | KA034012 | 2 | 16GA | 128.A6 | XT7701:2 | JB770 | 128.A3
XT0337:14 | WC7901 | KA0331A1 | 11 | 16GA | 130.C3 | XT7701:27 | JB770 | 130.C2
XT0337:16 | WC7901 | FU0333 | 12 | 16GA | 130.C3 | XT7701:28 | JB770 | 130.C2
XT2920:5 | WC7901 | SB951211 | 13 | 16GA | 135.B5 | XT7701:31 | JB770 | 135.B5
XT2920:6 | WC7901 | SB951212 | 14 | 16GA | 135.B5 | XT7701:32 | JB770 | 135.B5
XT2920:7 | WC7901 | SB047211 | 15 | 16GA | 135.B5 | XT7701:33 | JB770 | 135.B5
XT2920:8 | WC7901 | SB951222 | 16 | 16GA | 135.B5 | XT7701:34 | JB770 | 135.B5
XT0183:1 | WC7901 | SB75011 | 17 | 16GA | 129.A5 | XT7701:8 | JB770 | 129.A4
XT0183:2 | WC7901 | SB75012 | 18 | 16GA | 129.A5 | XT7701:9 | JB770 | 129.A4
XT0183:3 | WC7901 | SB75021 | 19 | 16GA | 129.A5 | XT7701:10 | JB770 | 129.A4
XT0183:4 | WC7901 | SB75022 | 20 | 16GA | 129.A5 | XT7701:11 | JB770 | 129.A4
XT0181:5 | WC7901 | SB75031 | 21 | 16GA | 129.B5 | XT7701:12 | JB770 | 129.B4
XT0181:6 | WC7901 | SB75032 | 22 | 16GA | 129.B5 | XT7701:13 | JB770 | 129.B4
XT0181:1 | WC7901 | KA7500C | 23 | 16GA | 129.B5 | XT7701:14 | JB770 | 129.B4
XT0181:2 | WC7901 | KA7500NO | 24 | 16GA | 129.B5 | XT7701:15 | JB770 | 129.B4
XT0181:3 | WC7901 | SB7500C | 25 | 16GA | 129.C5 | XT7701:16 | JB770 | 129.C4
XT0181:4 | WC7901 | SB7500NO | 26 | 16GA | 129.C5 | XT7701:17 | JB770 | 129.C4
AF0122:38 | WC7901 | KA96041 | 27 | 16GA | 100.D7 | XT7701:21 | JB770 | 100.D3
AF0122:06 | WC7901 | KA96042 | 28 | 16GA | 100.D7 | XT7701:22 | JB770 | 100.D3
XT0173:12 | WC7901 | AT017045 | 29 | 16GA | 131.A5 | XT7701:35 | JB770 | 131.A4
XT0173:13 | WC7901 | AT017046 | 30 | 16GA | 131.B5 | XT7701:36 | JB770 | 131.B4
XT0173:14 | WC7901 | KA017211 | 31 | 16GA | 131.B5 | XT7701:37 | JB770 | 131.B4
XT0173:15 | WC7901 | KA017912 | 32 | 16GA | 131.B5 | XT7701:38 | JB770 | 131.B4
XT0173:16 | WC7901 | KA017411 | 33 | 16GA | 131.B5 | XT7701:39 | JB770 | 131.B4
XT0173:17 | WC7901 | KA017412 | 34 | 16GA | 131.B5 | XT7701:40 | JB770 | 131.B4
XT0351:2 | WC8085 | VBUSA | 1 | 12 | 107.B5 | XT7720:3 | JB772 | 107.B4
XT0351:4 | WC8085 | VBUSB | 2 | 12 | 107.B5 | XT7720:4 | JB772 | 107.B4
XT0351:6 | WC8085 | VBUSC | 3 | 12 | 107.C5 | XT7720:5 | JB772 | 107.C4
XT0351:8 | WC8085 | VBUSN | GY | 12 | 107.C5 | XT7720:6 | JB772 | 107.C4
AF0122:09 | SC | KA046023 | WHT | 20 | 40.C6 | KA0460:23 | BECKWITH RELAY,SMT130 | 40.A3
AF0122:41 | SC | KA046024 | WHT | 20 | 40.C6 | KA0460:24 | BECKWITH RELAY,SMT130 | 40.A3
AF0181:07 | SC | KA046013 | WHT | 20 | 40.A6 | KA0460:13 | BECKWITH RELAY,SMT130 | 40.A3
AF0181:08 | SC | KA046016 | WHT | 20 | 40.B6 | KA0460:16 | BECKWITH RELAY,SMT130 | 40.A3
AF0181:09 | SC | KA046019 | WHT | 20 | 40.B6 | KA0460:19 | BECKWITH RELAY,SMT130 | 40.A3
AF0181:10 | SC | KA046029 | WHT | 20 | 40.C6 | KA0460:29 | BECKWITH RELAY,SMT130 | 40.A3
AF0181:39 | SC | KA046012 | WHT | 20 | 40.A6 | KA0460:12 | BECKWITH RELAY,SMT130 | 40.A3
AF0181:40 | SC | KA046015 | WHT | 20 | 40.B6 | KA0460:15 | BECKWITH RELAY,SMT130 | 40.A3
AF0181:41 | SC | KA046018 | WHT | 20 | 40.B6 | KA0460:18 | BECKWITH RELAY,SMT130 | 40.A3
AF0181:42 | SC | KA046030 | WHT | 20 | 40.C6 | KA0460:30 | BECKWITH RELAY,SMT130 | 40.A3
KA0330:22 | SC | KA046010 | WHT | 20 | 40.A2 | KA0460:10 | BECKWITH RELAY,SMT130 | 40.A3
KA0330:24 | SC | KA04605 | WHT | 20 | 40.A2 | KA0460:5 | BECKWITH RELAY,SMT130 | 40.A3
KA2672:11 | SC | KA046011 | WHT | 20 | 40.A2 | KA0460:11 | BECKWITH RELAY,SMT130 | 40.A3
KA2672:14 | SC | KA04606 | WHT | 20 | 40.A2 | KA0460:6 | BECKWITH RELAY,SMT130 | 40.A3
XT0351:1 | SC | VBUSA | RED | 16 | 107.B5 | KA0460:65 | BECKWITH RELAY,SMT130 | 107.C6
XT0351:10 | SC | VGENB | RED | 16 | 107.D5 | KA0460:41 | BECKWITH RELAY,SMT130 | 107.D7
XT0351:11 | SC | VGENC | RED | 16 | 107.D5 | KA0460:43 | BECKWITH RELAY,SMT130 | 107.D7
XT0351:13 | SC | VGENN | GRN/YEL | 16 | 107.D5 | KA0460:40 | BECKWITH RELAY,SMT130 | 107.D7
XT0351:13 | SC | VGENN | GRN/YEL | 16 | 107.D5 | KA0460:38 | BECKWITH RELAY,SMT130 | 107.D7
XT0351:14 | SC | VGENN | GRN/YEL | 16 | 107.D5 | KA0460:42 | BECKWITH RELAY,SMT130 | 107.D7
XT0351:3 | SC | VBUSB | RED | 16 | 107.B5 | KA0460:64 | BECKWITH RELAY,SMT130 | 107.C6
XT0351:9 | SC | VGENA | RED | 16 | 107.C5 | KA0460:39 | BECKWITH RELAY,SMT130 | 107.D7
XT0353:1 | SC | DCTAX1 | BLU | 12 | 107.A5 | KA0460:46 | BECKWITH RELAY,SMT130 | 107.A7
XT0353:2 | SC | DCTBX1 | BLU | 12 | 107.A5 | KA0460:48 | BECKWITH RELAY,SMT130 | 107.A7
XT0353:3 | SC | DCTCX1 | BLU | 12 | 107.A5 | KA0460:50 | BECKWITH RELAY,SMT130 | 107.A7
XT0353:4 | SC | DCTX2N | BLU | 12 | 107.A6 | KA0460:47 | BECKWITH RELAY,SMT130 | 107.A7
XT0353:5 | SC | DCTX2N | BLU | 12 | 107.A6 | KA0460:49 | BECKWITH RELAY,SMT130 | 107.A7
XT0353:6 | SC | DCTX2N | BLU | 12 | 107.A6 | KA0460:51 | BECKWITH RELAY,SMT130 | 107.A7
XT0454:1 | SC | DCT02 | BLU | 12 | 102.C4 | KA0460:55 | BECKWITH RELAY,SMT130 | 102.C7
XT0454:2 | SC | DCT03 | BLU | 12 | 102.C4 | KA0460:57 | BECKWITH RELAY,SMT130 | 102.C7
XT0454:3 | SC | DCT06 | BLU | 12 | 102.D4 | KA0460:59 | BECKWITH RELAY,SMT130 | 102.C7
XT0454:4 | SC | DCT01 | BLU | 12 | 102.C4 | KA0460:54 | BECKWITH RELAY,SMT130 | 102.C7
XT0454:5 | SC | DCT01 | BLU | 12 | 102.C4 | KA0460:56 | BECKWITH RELAY,SMT130 | 102.C7
XT0454:6 | SC | DCT01 | BLU | 12 | 102.D4 | KA0460:58 | BECKWITH RELAY,SMT130 | 102.C7
XT0460:1 | SC | FU0460 | WHT | 14 | 40.C3 | KA0460:62 | BECKWITH RELAY,SMT130 | 40.A3
XT0460:2 | SC | FU0460 | WHT | 14 | 40.C3 | KA0460:31 | BECKWITH RELAY,SMT130 | 40.A3
XT0460:3 | SC | FU0460 | WHT | 14 | 40.C3 | KA0460:33 | BECKWITH RELAY,SMT130 | 40.A3
XT0460:4 | SC | KA046032 | WHT | 14 | 40.C3 | KA0460:32 | BECKWITH RELAY,SMT130 | 40.A3
XT0460:5 | SC | KA0333A1 | WHT | 20 | 40.D3 | KA0460:34 | BECKWITH RELAY,SMT130 | 40.A3
AT0140:P2 | WC0014 | AT0140P2 | ENET | CABLE | 2.C4 | AF0510:L1 | FG&E CTRL,SMT130 | 2.C5
AF0182:09 | SC | 018209 | WHT | 16 | 18.C7 | XT0292:2 | MCC PNL,SMT130 | 18.C6
AF0182:25 | SC | 0V | WHT | 16 | 18.C7 | XT0292:3 | MCC PNL,SMT130 | 18.C6
FU0181:LD | SC | FU0181 | WHT | 16 | 32.D1 | XT0292:1 | MCC PNL,SMT130 | 18.C6
KA2320:A1 | SC | 029104 | WHT | 20 | 91.C6 | AF0291:04 | MCC PNL,SMT130 | 91.B7
KA2320:A2 | SC | 029120 | WHT | 20 | 91.C6 | AF0291:20 | MCC PNL,SMT130 | 91.B7
KA3103:A1 | SC | KA3103A1 | WHT | 20 | 80.A5 | AF0291:05 | MCC PNL,SMT130 | 80.A6
KA3103:A2 | SC | KA3103A2 | WHT | 20 | 80.A5 | AF0291:21 | MCC PNL,SMT130 | 80.A6
KA3420:A1 | SC | KA3420A1 | WHT | 20 | 101.B5 | AF0291:00 | MCC PNL,SMT130 | 101.B7
KA3420:A2 | SC | KA3420A2 | WHT | 20 | 101.B5 | AF0291:16 | MCC PNL,SMT130 | 101.B7
PEG0140:0 | SC | PEG224014 | GRN/YEL | 8 | 17.B2 | PEG2240:14 | MCC PNL,SMT130 | 17.B2
XT0180:2 | SC | 0V | WHT | 16 | 32.D1 | XT0292:3 | MCC PNL,SMT130 | 18.C6
XT0336:1 | SC | ESTOP | WHT | 16 | 29.C4 | XT2920:13 | MCC PNL,SMT130 | 29.C2
XT0337:4 | WC7622 | 029338 | RED | 20 | 129.C5 | AF0293:38 | MCC PNL,SMT130 | 129.C7
XT0337:5 | WC7622 | 029306 | BLK | 20 | 129.C5 | AF0293:06 | MCC PNL,SMT130 | 129.C7
XT0337:6 | WC7622 | 029354 | SH | 20 | 129.C5 | AF0293:54 | MCC PNL,SMT130 | 129.C7
IEG0140:7 | SC | IEG01407 | GRN | 12 | 4.B6 | AR0600:IE2 | PLC, PANEL | 4.A1
XT0337:12 | SC | KA0333A1 | WHT | 20 | 130.B3 | KA0461:16 | PNL,DOOR,2-BAY | 40.D3
XT0460:2 | SC | FU0460 | WHT | 14 | 40.C3 | KA0461:14 | PNL,DOOR,2-BAY | 40.D3
XT0460:4 | SC | KA046032 | WHT | 14 | 40.C3 | KA0461:G | PNL,DOOR,2-BAY | 40.D3
XT0460:5 | SC | KA0333A1 | WHT | 20 | 40.D3 | KA0461:16 | PNL,DOOR,2-BAY | 40.D3
XT0460:6 | SC | 0V | WHT | 14 | 40.D5 | KA0461:B | PNL,DOOR,2-BAY | 40.D3
XT0460:7 | SC | KA046113 | WHT | 20 | 40.D5 | KA0461:13 | PNL,DOOR,2-BAY | 40.D3
XT0460:8 | SC | KA046111 | WHT | 20 | 40.D5 | KA0461:11 | PNL,DOOR,2-BAY | 40.D3
IEG0140:0 | SC | IEG224014 | GRN | 8 | 17.B2 | IEG2240:14 | POWERDIST, PANEL | 17.B2
XT0332:1 | SC | FU0136 | WHT | 14 | 29.B2 | XT0102:4 | POWERDIST, PANEL | 19.B2
XT0334:1 | SC | 0V | WHT | 14 | 29.C2 | XT0104:5 | POWERDIST, PANEL | 19.C2
XT0460:1 | SC | FU0460 | WHT | 14 | 40.C3 | FU0460:LD | POWERDIST, PANEL | 40.C2
XT0460:6 | SC | 0V | WHT | 14 | 40.D5 | XT0104:6 | POWERDIST, PANEL | 19.C2
AU0120:L1 | WC0020 | AU0200L2 | ENET | CABLE | 2.C2 | AU0200:L2 | TCP, SMT130 | 2.C5
SolarTools ver. 24.0.84.24712 (Jul 31, 2025)
Report date: 2/3/2026 11:55 AM

## MCC PNL,SMT130
MCC PNL,SMT130
Project # | 4L321
Project Name | Enterprise SMT130 M4 WTX
Revision | 0.1
Controls DE
Phone:
Controls ME
Phone:
From | [5 empty] | To
Device ID | Cable (W) Conductor (SC) Jumper Clip (JC) | Wire No. | Wire ID | Gauge/Size | Page/Zone | Device ID | Location | Page/Zone
XT0290:1 | JC | 0V | CLIP | --- | 41.B1 | XT0290:2 | MCC PNL,SMT130 | 41.B1
XT0290:2 | JC | 0V | CLIP | --- | 41.B1 | XT0290:3 | MCC PNL,SMT130 | 41.C1
XT2920:6 | SC | JW29205 | VIO | 20 | 135.B5 | XT2920:5 | MCC PNL,SMT130 | 135.B5
XT2920:8 | SC | JW2920 | VIO | 20 | 135.B5 | XT2920:7 | MCC PNL,SMT130 | 135.B5
AF0291:01 | SC | KA2970A1 | WHT | 20 | 92.B7 | KA2970:A1 | MCC PNL,SMT130 | 92.B6
AF0291:03 | SC | KA2960A1 | WHT | 20 | 104.B6 | KA2960:A1 | MCC PNL,SMT130 | 104.B6
AF0291:07 | SC | SH04715 | WHT | 20 | 44.A7 | XT0292:8 | MCC PNL,SMT130 | 44.A5
AF0291:08 | SC | SH04705 | WHT | 20 | 44.B7 | XT0292:14 | MCC PNL,SMT130 | 44.B5
AF0291:09 | SC | SH04755 | WHT | 20 | 43.A6 | XT0292:26 | MCC PNL,SMT130 | 43.A5
AF0291:10 | SC | HL0409BA | WHT | 20 | 44.C7 | XT0292:18 | MCC PNL,SMT130 | 44.C5
AF0291:11 | SC | HL0411BA | WHT | 20 | 44.D7 | XT0292:20 | MCC PNL,SMT130 | 44.D5
AF0291:17 | SC | KA2970A2 | WHT | 20 | 92.B7 | KA2970:A2 | MCC PNL,SMT130 | 92.B6
AF0291:19 | SC | KA2960A2 | WHT | 20 | 104.B6 | KA2960:A2 | MCC PNL,SMT130 | 104.B6
AF0291:23 | SC | SH04716 | WHT | 20 | 44.A7 | XT0292:9 | MCC PNL,SMT130 | 44.A5
AF0291:24 | SC | SH04706 | WHT | 20 | 44.B7 | XT0292:15 | MCC PNL,SMT130 | 44.C5
AF0291:25 | SC | SH04756 | WHT | 20 | 43.A6 | XT0292:27 | MCC PNL,SMT130 | 43.A5
AF0291:26 | SC | HL0409BB | WHT | 20 | 44.C7 | XT0292:19 | MCC PNL,SMT130 | 44.D5
AF0291:27 | SC | HL0411BB | WHT | 20 | 44.D7 | XT0292:21 | MCC PNL,SMT130 | 44.D5
AF0291:COM | SC | 0V | WHT | 16 | 41.B2 | XT0290:2 | MCC PNL,SMT130 | 41.B1
AF0291:V+ | SC | FU0291 | WHT | 16 | 41.B2 | FU0291:LD | MCC PNL,SMT130 | 41.B1
AF0292:COM | SC | AF0292N | WHT | 16 | 41.B3 | AF0293:COM | MCC PNL,SMT130 | 41.B3
AF0292:COM | SC | 0V | WHT | 16 | 41.B3 | XT0290:3 | MCC PNL,SMT130 | 41.C1
AF0292:V+ | SC | AF0292P | WHT | 16 | 41.B3 | AF0293:V+ | MCC PNL,SMT130 | 41.B3
AF0292:V+ | SC | FU0294 | WHT | 16 | 41.B3 | FU0294:LD | MCC PNL,SMT130 | 41.C1
AF0293:01 | SC | 0V | WHT | 20 | 18.A7 | XT0290:2 | MCC PNL,SMT130 | 41.B1
AF0293:03 | SC | 0V | WHT | 20 | 18.A7 | XT0290:3 | MCC PNL,SMT130 | 41.C1
AF0293:COM | SC | AF0293N | WHT | 16 | 41.B3 | AF0294:COM | MCC PNL,SMT130 | 41.A4
AF0293:SH | SC | AF0294G | GRN | 14 | 41.B3 | AF0294:SH | MCC PNL,SMT130 | 41.A4
AF0293:SH | SC | AU0290G | GRN | 14 | 41.B3 | AU0290:GND | MCC PNL,SMT130 | 41.A2
AF0293:V+ | SC | AF0293P | WHT | 16 | 41.B3 | AF0294:V+ | MCC PNL,SMT130 | 41.A4
AF0294:COM | SC | AF0294N | WHT | 16 | 41.A4 | AF0295:COM | MCC PNL,SMT130 | 41.A5
AF0294:SH | SC | AF0295G | GRN | 14 | 41.A4 | AF0295:SH | MCC PNL,SMT130 | 41.A5
AF0294:V+ | SC | AF0294P | WHT | 16 | 41.A4 | AF0295:V+ | MCC PNL,SMT130 | 41.A5
AF0295:COM | SC | AF0295N | WHT | 16 | 41.A5 | AF0296:COM | MCC PNL,SMT130 | 41.B5
AF0295:V+ | SC | AF0295P | WHT | 16 | 41.A5 | AF0296:V+ | MCC PNL,SMT130 | 41.B5
AF0296:00 | SC | SH04714 | WHT | 20 | 44.A7 | XT0292:5 | MCC PNL,SMT130 | 44.A5
AF0296:01 | SC | SH04702 | WHT | 20 | 44.B7 | XT0292:11 | MCC PNL,SMT130 | 44.B5
AF0296:02 | SC | SB047112 | WHT | 20 | 44.C7 | XT0292:17 | MCC PNL,SMT130 | 44.C5
AF0296:03 | SC | SH04754 | WHT | 20 | 43.A6 | XT0292:23 | MCC PNL,SMT130 | 43.A5
AF0296:06 | SC | SB0402BNO | WHT | 20 | 43.B6 | XT0292:29 | MCC PNL,SMT130 | 43.B5
AF0296:07 | SC | SB0403BNO | WHT | 20 | 43.B6 | XT0292:31 | MCC PNL,SMT130 | 43.B5
AF0296:09 | SC | SA047524 | WHT | 20 | 45.B6 | XT0290:11 | MCC PNL,SMT130 | 45.B6
AF0296:10 | SC | SA047512 | WHT | 20 | 45.B6 | XT0290:13 | MCC PNL,SMT130 | 45.B6
AF0296:32 | SC | SH04713 | WHT | 20 | 44.A7 | XT0292:4 | MCC PNL,SMT130 | 44.A5
AF0296:33 | SC | SH04701 | WHT | 20 | 44.B7 | XT0292:10 | MCC PNL,SMT130 | 44.B5
AF0296:34 | SC | SB047111 | WHT | 20 | 44.C7 | XT0292:16 | MCC PNL,SMT130 | 44.C5
AF0296:35 | SC | SH04753 | WHT | 20 | 43.A6 | XT0292:22 | MCC PNL,SMT130 | 43.A5
AF0296:38 | SC | SB0402BC | WHT | 20 | 43.B6 | XT0292:28 | MCC PNL,SMT130 | 43.B5
AF0296:39 | SC | SB0403BC | WHT | 20 | 43.B6 | XT0292:30 | MCC PNL,SMT130 | 43.B5
AF0296:41 | SC | SA047523 | WHT | 20 | 45.B6 | XT0290:10 | MCC PNL,SMT130 | 45.B6
AF0296:42 | SC | SA047511 | WHT | 20 | 45.B6 | XT0290:12 | MCC PNL,SMT130 | 45.B6
AF0296:COM | SC | AF0296N | WHT | 16 | 41.B5 | AF0297:COM | MCC PNL,SMT130 | 41.A6
AF0296:V+ | SC | AF0296P | WHT | 16 | 41.B5 | AF0297:V+ | MCC PNL,SMT130 | 41.A6
AF0297:01 | SC | SB851212 | WHT | 20 | 135.A7 | XT2920:2 | MCC PNL,SMT130 | 135.A5
AF0297:02 | SC | SB951212 | WHT | 20 | 135.B7 | XT2920:6 | MCC PNL,SMT130 | 135.B5
AF0297:03 | SC | SB047222 | WHT | 20 | 45.A6 | XT0290:7 | MCC PNL,SMT130 | 45.A6
AF0297:33 | SC | SB851211 | WHT | 20 | 135.A7 | XT2920:1 | MCC PNL,SMT130 | 135.A5
AF0297:34 | SC | SB951211 | WHT | 20 | 135.B7 | XT2920:5 | MCC PNL,SMT130 | 135.B5
AF0297:35 | SC | SB047221 | WHT | 20 | 45.A6 | XT0290:6 | MCC PNL,SMT130 | 45.A6
AU0290:COM | SC | 0V | WHT | 16 | 41.A2 | XT0290:1 | MCC PNL,SMT130 | 41.B1
AU0290:V+ | SC | FU0290 | WHT | 16 | 41.A2 | FU0290:LD | MCC PNL,SMT130 | 41.B1
FU0290:LI | SC | FU0560 | WHT | 14 | 41.B1 | FU0291:LI | MCC PNL,SMT130 | 41.B1
FU0290:LI | SC | FU0560 | WHT | 14 | 41.B1 | XT0295:1 | MCC PNL,SMT130 | 41.A3
FU0291:LI | SC | FU0560 | WHT | 14 | 41.B1 | FU0294:LI | MCC PNL,SMT130 | 41.C1
GR0291: | SC | GR0291 | GRN/YEL | 14 | 17.A4 | FRAME | MCC PNL,SMT130 | 17.A4
KA2960:11 | SC | CCATS29601 | WHT | 16 | 104.B5 | XT0292:37 | MCC PNL,SMT130 | 104.B5
KA2960:14 | SC | CCATS29602 | WHT | 16 | 104.B5 | XT0292:38 | MCC PNL,SMT130 | 104.B5
KA2970:11 | SC | KA297011 | WHT | 16 | 92.C5 | XT0290:4 | MCC PNL,SMT130 | 92.B5
KA2970:14 | SC | KA297014 | WHT | 16 | 92.C5 | XT0290:5 | MCC PNL,SMT130 | 92.C5
RR2921: -3.01K OHM | SC | FU0181 | LEAD | --- | 18.C6 | XT0292:1 | MCC PNL,SMT130 | 18.C6
RR2921: -3.01K OHM | SC | 018209 | LEAD | --- | 18.C6 | XT0292:2 | MCC PNL,SMT130 | 18.C6
RR2922: -1.0K OHM | SC | 0V | LEAD | --- | 18.C6 | XT0292:3 | MCC PNL,SMT130 | 18.C6
RR2922: -1.0K OHM | SC | 018209 | LEAD | --- | 18.C6 | XT0292:2 | MCC PNL,SMT130 | 18.C6
XT0292:35 | SC | FU0560 | WHT | 16 | 147.A6 | XT0295:1 | MCC PNL,SMT130 | 41.A3
XT0292:36 | SC | 0V | WHT | 16 | 147.A6 | XT0295:2 | MCC PNL,SMT130 | 41.A3
XT0295:2 | SC | 0V | WHT | 14 | 41.A3 | XT0290:1 | MCC PNL,SMT130 | 41.B1
XT2920:7 | SC | SB047211 | WHT | 16 | 135.B5 | XT0290:9 | MCC PNL,SMT130 | 45.A6
AF0293:25 | WC7890 | TE7100A1 | RED-TR1 | 18 | 110.A6 | XT7100:1 | JB7100 | 110.A2
AF0293:09 | WC7890 | TE7100A2 | WHT-TR1 | 18 | 110.A6 | XT7100:2 | JB7100 | 110.A2
AF0293:08 | WC7890 | TE7100A3 | BLK-TR1 | 18 | 110.A6 | XT7100:3 | JB7100 | 110.A2
AF0293:56 | WC7890 | TE7100AS | SH-TR1 | 18 | 110.A6 | FW1:1 | JB7100 | 110.A2
AF0293:27 | WC7890 | TE7100B1 | RED-TR2 | 18 | 110.A6 | XT7100:4 | JB7100 | 110.A2
AF0293:11 | WC7890 | TE7100B2 | WHT-TR2 | 18 | 110.A6 | XT7100:5 | JB7100 | 110.A2
AF0293:10 | WC7890 | TE7100B3 | BLK-TR2 | 18 | 110.A6 | XT7100:6 | JB7100 | 110.B2
AF0293:58 | WC7890 | TE7100BS | SH-TR2 | 18 | 110.A6 | FW2:1 | JB7100 | 110.B2
AF0293:29 | WC7890 | TE7100C1 | RED-TR3 | 18 | 110.B6 | XT7100:7 | JB7100 | 110.B2
AF0293:13 | WC7890 | TE7100C2 | WHT-TR3 | 18 | 110.B6 | XT7100:8 | JB7100 | 110.B2
AF0293:12 | WC7890 | TE7100C3 | BLK-TR3 | 18 | 110.B6 | XT7100:9 | JB7100 | 110.B2
AF0293:60 | WC7890 | TE7100CS | SH-TR3 | 18 | 110.B6 | FW3:1 | JB7100 | 110.B2
AF0291:00 | SC | KA3420A1 | WHT | 20 | 101.B7 | KA3420:A1 | GEN CMPNT | 101.B5
AF0291:04 | SC | 029104 | WHT | 20 | 91.B7 | KA2320:A1 | GEN CMPNT | 91.C6
AF0291:05 | SC | KA3103A1 | WHT | 20 | 80.A6 | KA3103:A1 | GEN CMPNT | 80.A5
AF0291:16 | SC | KA3420A2 | WHT | 20 | 101.B7 | KA3420:A2 | GEN CMPNT | 101.B5
AF0291:20 | SC | 029120 | WHT | 20 | 91.B7 | KA2320:A2 | GEN CMPNT | 91.C6
AF0291:21 | SC | KA3103A2 | WHT | 20 | 80.A6 | KA3103:A2 | GEN CMPNT | 80.A5
PEG2240:14 | SC | PEG224014 | GRN/YEL | 8 | 17.B2 | PEG0140:0 | GEN CMPNT | 17.B2
XT0292:1 | SC | FU0181 | WHT | 16 | 18.C6 | FU0181:LD | GEN CMPNT | 32.D1
XT0292:2 | SC | 018209 | WHT | 16 | 18.C6 | AF0182:09 | GEN CMPNT | 18.C7
XT0292:3 | SC | 0V | WHT | 16 | 18.C6 | XT0180:2 | GEN CMPNT | 32.D1
XT0292:3 | SC | 0V | WHT | 16 | 18.C6 | AF0182:25 | GEN CMPNT | 18.C7
XT2920:13 | SC | ESTOP | WHT | 16 | 29.C2 | XT0336:1 | GEN CMPNT | 29.C4
AF0293:38 | WC7622 | 029338 | RED | 20 | 129.C7 | XT0337:4 | GEN CMPNT | 129.C5
AF0293:06 | WC7622 | 029306 | BLK | 20 | 129.C7 | XT0337:5 | GEN CMPNT | 129.C5
AF0293:54 | WC7622 | 029354 | SH | 20 | 129.C7 | XT0337:6 | GEN CMPNT | 129.C5
AU0290:L1 | WC0603 | AP0603L2 | ENET | CABLE | 2.C5 | AP0603:L2 | PLC, PANEL | 2.C4
AF0292:00 | SC | UJ0131OK2 | WHT | 20 | 18.B7 | UJ0131:OK2 | POWERDIST, PANEL | 18.B4
AF0292:32 | SC | UJ0131OK1 | WHT | 20 | 18.B7 | UJ0131:OK1 | POWERDIST, PANEL | 18.B4
AF0293:00 | SC | UJ0131VIN | WHT | 20 | 18.A7 | UJ0131:VIN | POWERDIST, PANEL | 18.B4
AF0293:02 | SC | UJ0131IOUT | WHT | 20 | 18.A7 | UJ0131:IOUT | POWERDIST, PANEL | 18.B4
AF0295:SH | SC | IEG22403 | GRN | 14 | 41.A5 | IEG2240:3 | POWERDIST, PANEL | 41.B6
GR0290: | SC | GR0290 | GRN | 14 | 17.A4 | IEG2240:1 | POWERDIST, PANEL | 17.A4
PEG2240:1 | SC | 0V | GRN/YEL | 8 | 19.C1 | XT0104:7 | POWERDIST, PANEL | 19.C2
XT0290:8 | SC | SB047212 | WHT | 20 | 45.A6 | XT0563:2 | PWR DST,DR,SMT130 | 37.D6
XT0295:1 | SC | FU0560 | WHT | 14 | 41.A3 | XT0561:2 | PWR DST,DR,SMT130 | 35.B3
XT0295:2 | SC | 0V | WHT | 20 | 41.A3 | XT0562:3 | PWR DST,DR,SMT130 | 35.B2
XT2920:4 | SC | SB851222 | WHT | 20 | 135.A5 | XT0563:1 | PWR DST,DR,SMT130 | 37.D6
AF0297:04 | SC | SB0400B212 | WHT | 20 | 38.A3 | SB0400:B2-12 | TCP, SMT130 | 38.A1
AF0297:36 | SC | SB0400B211 | WHT | 20 | 38.A3 | SB0400:B2-11 | TCP, SMT130 | 38.A1
AU0290:L2 | WC0029 | AU0290L2 | ENET | CABLE | 2.C5 | AU0200:L1 | TCP, SMT130 | 2.C5
SolarTools ver. 24.0.84.24712 (Jul 31, 2025)
Report date: 2/3/2026 11:55 AM

## PLC, PANEL
PLC, PANEL
Project # | 4L321
Project Name | Enterprise SMT130 M4 WTX
Revision | 0.1
Controls DE
Phone:
Controls ME
Phone:
From | [5 empty] | To
Device ID | Cable (W) Conductor (SC) Jumper Clip (JC) | Wire No. | Wire ID | Gauge/Size | Page/Zone | Device ID | Location | Page/Zone
AR0600:IE1 | SC | UV0600G | GRN | 14 | 4.A1 | UV0600:GND | PLC, PANEL | 4.B2
AP0602:L2 | WC0602 | AP0602L2 | ENET | CABLE | 2.C3 | AP0603:L1 | PLC, PANEL | 2.C4
AP0606:L1 | WC0606 | AP0606L1 | ENET | CABLE | 4.C3 | LSENET1:1 | JB774 | 4.C2
AP0606:L2 | WC0607 | AP0606L2 | ENET | CABLE | 4.C3 | LSENET2:1 | JB774 | 4.C2
AP0609:L1 | WC0609 | AP0609L1 | ENET | CABLE | 4.D3 | CCAP0609:1 | JB774 | 4.D2
AP0602:L1 | WC0017 | AT0170L2 | ENET | CABLE | 2.C3 | AT0170:L2 | FG&E CTRL,SMT130 | 2.C2
AR0600:IE2 | SC | IEG01407 | GRN | 12 | 4.A1 | IEG0140:7 | GEN CMPNT | 4.B6
AP0603:L2 | WC0603 | AP0603L2 | ENET | CABLE | 2.C4 | AU0290:L1 | MCC PNL,SMT130 | 2.C5
UV0600:(-) | SC | 0V | WHT | 14 | 4.B2 | XT0104:3 | POWERDIST, PANEL | 19.C2
UV0600:(+) | SC | FU0010 | WHT | 14 | 4.B2 | FU0010:LD | POWERDIST, PANEL | 19.B2
AP0607:L2 | WC7028 | BA0701ENET | ENET | CABLE | 4.A5 | BA0701:ENET | POWERDIST, PANEL | 5.B5
AP0607:L1 | WC7071 | AP0607L1 | ENET | CABLE | 4.A5 | BA0700:2 | POWERDIST, PANEL | 5.A3
SolarTools ver. 24.0.84.24712 (Jul 31, 2025)
Report date: 2/3/2026 11:55 AM

## PNL A,SMT130
PNL A,SMT130
Project # | 4L321
Project Name | Enterprise SMT130 M4 WTX
Revision | 0.1
Controls DE
Phone:
Controls ME
Phone:
From | [5 empty] | To
Device ID | Cable (W) Conductor (SC) Jumper Clip (JC) | Wire No. | Wire ID | Gauge/Size | Page/Zone | Device ID | Location | Page/Zone
XT0080:1 | JC | 0V | CLIP | --- | 20.D1 | XT0080:2 | PNL A,SMT130 | 20.D1
XT0080:2 | JC | 0V | CLIP | --- | 20.D1 | XT0080:3 | PNL A,SMT130 | 20.D1
XT0090:1 | JC | 0V | CLIP | --- | 20.B1 | XT0090:2 | PNL A,SMT130 | 20.B1
XT0134:1 | JC | 0V | CLIP | --- | 19.B4 | XT0134:2 | PNL A,SMT130 | 19.C4
XT0134:2 | JC | 0V | CLIP | --- | 19.C4 | XT0134:3 | PNL A,SMT130 | 19.C4
XT0134:3 | JC | 0V | CLIP | --- | 19.C4 | XT0134:4 | PNL A,SMT130 | 19.C4
XT0135:1 | JC | 0V | CLIP | --- | 19.B5 | XT0135:2 | PNL A,SMT130 | 19.C5
XT0135:2 | JC | 0V | CLIP | --- | 19.C5 | XT0135:3 | PNL A,SMT130 | 19.C5
XT0136:1 | JC | FU0139 | CLIP | --- | 23.A2 | XT0136:2 | PNL A,SMT130 | 23.A2
XT0138:1 | JC | FU0136 | CLIP | --- | 19.A4 | XT0138:2 | PNL A,SMT130 | 19.A4
XT0138:2 | JC | FU0136 | CLIP | --- | 19.A4 | XT0138:3 | PNL A,SMT130 | 19.A4
XT0138:3 | JC | FU0136 | CLIP | --- | 19.A4 | XT0138:4 | PNL A,SMT130 | 19.B4
XT0139:1 | JC | FU0137 | CLIP | --- | 19.A5 | XT0139:2 | PNL A,SMT130 | 19.A5
XT0139:2 | JC | FU0137 | CLIP | --- | 19.A5 | XT0139:3 | PNL A,SMT130 | 19.B5
AF0081:04 | SC | 008104 | WHT | 20 | 65.B7 | KA0221:14 | PNL A,SMT130 | 65.B6
AF0081:COM | SC | 0V | WHT | 16 | 20.D2 | XT0080:2 | PNL A,SMT130 | 20.D1
AF0081:J | SC | * |  |  | 20.D2 | AF0082:P | PNL A,SMT130 | 20.D3
AF0081:V+ | SC | FU0081 | WHT | 16 | 20.D2 | FU0081:LD | PNL A,SMT130 | 20.D1
AF0082:COM | SC | AF0082N | WHT | 16 | 20.D3 | AF0083:COM | PNL A,SMT130 | 20.D3
AF0082:COM | SC | 0V | WHT | 16 | 20.D3 | XT0080:3 | PNL A,SMT130 | 20.D1
AF0082:V+ | SC | AF0082P | WHT | 16 | 20.D3 | AF0083:V+ | PNL A,SMT130 | 20.D3
AF0082:V+ | SC | FU0082 | WHT | 16 | 20.D3 | FU0082:LD | PNL A,SMT130 | 20.D1
AF0083:COM | SC | AF0083N | WHT | 16 | 20.D3 | AF0084:COM | PNL A,SMT130 | 20.D4
AF0083:J | SC | * |  |  | 20.D3 | AF0084:P | PNL A,SMT130 | 20.D4
AF0083:SH | SC | AF0083G | GRN | 14 | 20.D3 | AF0084:SH | PNL A,SMT130 | 20.D4
AF0083:SH | SC | AU0080G | GRN | 14 | 20.D3 | AU0080:GND | PNL A,SMT130 | 20.C2
AF0083:V+ | SC | AF0083P | WHT | 16 | 20.D3 | AF0084:V+ | PNL A,SMT130 | 20.D4
AF0084:COM | SC | AF0084N | WHT | 16 | 20.D4 | AF0085:COM | PNL A,SMT130 | 20.D5
AF0084:J | SC | * |  |  | 20.D4 | AF0085:P | PNL A,SMT130 | 20.D5
AF0084:SH | SC | AF0084G | GRN | 14 | 20.D4 | AF0085:SH | PNL A,SMT130 | 20.D5
AF0084:V+ | SC | AF0084P | WHT | 16 | 20.D4 | AF0085:V+ | PNL A,SMT130 | 20.D5
AF0085:COM | SC | AF0085N | WHT | 16 | 20.D5 | AF0086:COM | PNL A,SMT130 | 20.D5
AF0085:J | SC | * |  |  | 20.D5 | AF0086:P | PNL A,SMT130 | 20.D5
AF0085:SH | SC | AF0085G | GRN | 14 | 20.D5 | AF0086:SH | PNL A,SMT130 | 20.D5
AF0085:V+ | SC | AF0085P | WHT | 16 | 20.D5 | AF0086:V+ | PNL A,SMT130 | 20.D5
AF0091:03 | SC | KA014114 | WHT | 20 | 23.C2 | KA0141:14 | PNL A,SMT130 | 23.C2
AF0091:04 | SC | KA013624 | WHT | 20 | 23.B4 | KA0136:24 | PNL A,SMT130 | 23.B3
AF0091:07 | SC | KA0134A1 | WHT | 20 | 89.D7 | KA0134:A1 | PNL A,SMT130 | 23.C6
AF0091:35 | SC | KA014111 | WHT | 20 | 23.C2 | KA0141:11 | PNL A,SMT130 | 23.C2
AF0091:36 | SC | KA013621 | WHT | 20 | 23.B4 | KA0136:21 | PNL A,SMT130 | 23.B3
AF0091:COM | SC | AU0090N | WHT | 16 | 20.B2 | AU0090:COM | PNL A,SMT130 | 20.A2
AF0091:V+ | SC | AU0090P | WHT | 16 | 20.B2 | AU0090:V+ | PNL A,SMT130 | 20.A2
AF0092:00 | SC | 009200 | WHT | 20 | 144.A7 | XT0137:6 | PNL A,SMT130 | 144.A6
AF0092:01 | SC | 009201 | WHT | 20 | 145.A7 | XT0137:8 | PNL A,SMT130 | 145.A6
AF0092:02 | SC | KA0133A1 | WHT | 14 | 88.A7 | KA0133:A1 | PNL A,SMT130 | 23.C6
AF0092:04 | SC | 009204 | WHT | 20 | 142.B7 | XT0137:2 | PNL A,SMT130 | 142.B6
AF0092:06 | SC | KA013114 | WHT | 20 | 88.A7 | KA0131:14 | PNL A,SMT130 | 23.D4
AF0092:07 | SC | 009207 | WHT | 20 | 25.D6 | PC0470:INP_A | PNL A,SMT130 | 25.D5
AF0092:08 | SC | 009208 | WHT | 20 | 28.A6 | KA0875:A1 | PNL A,SMT130 | 28.A5
AF0092:13 | SC | 009213 | WHT | 20 | 143.A7 | XT0137:4 | PNL A,SMT130 | 143.A6
AF0092:16 | SC | 009216 | WHT | 20 | 144.A7 | KA6221:A2 | PNL A,SMT130 | 144.A6
AF0092:17 | SC | 009217 | WHT | 20 | 145.A7 | KA6222:A2 | PNL A,SMT130 | 145.A6
AF0092:20 | SC | 009220 | WHT | 20 | 142.B7 | KA6211:A2 | PNL A,SMT130 | 142.B6
AF0092:23 | SC | 009223 | WHT | 20 | 25.D6 | PC0470:-PWR | PNL A,SMT130 | 25.D5
AF0092:24 | SC | 009224 | WHT | 20 | 28.A6 | KA0875:A2 | PNL A,SMT130 | 28.A5
AF0092:29 | SC | 009229 | WHT | 20 | 143.A7 | KA6212:A2 | PNL A,SMT130 | 143.A6
AF0092:32 | SC | 009232 | WHT | 20 | 144.A7 | KA0176:24 | PNL A,SMT130 | 144.A6
AF0092:33 | SC | 009233 | WHT | 20 | 145.A7 | KA0177:24 | PNL A,SMT130 | 145.A6
AF0092:36 | SC | 009236 | WHT | 20 | 142.B7 | KA0176:14 | PNL A,SMT130 | 142.B6
AF0092:39 | SC | 009239 | WHT | 20 | 25.D6 | PC0470:+PWR | PNL A,SMT130 | 25.D5
AF0092:45 | SC | 009245 | WHT | 20 | 143.A7 | KA0177:14 | PNL A,SMT130 | 143.A6
AF0092:COM | SC | 0V | WHT | 16 | 20.B3 | XT0090:2 | PNL A,SMT130 | 20.B1
AF0092:J | SC | * |  |  | 20.B3 | AF0093:P | PNL A,SMT130 | 20.A3
AF0092:V+ | SC | FU0091 | WHT | 16 | 20.B3 | FU0091:LD | PNL A,SMT130 | 20.B1
AF0093:06 | SC | 009306 | WHT | 20 | 27.C7 | KA0130:14 | PNL A,SMT130 | 27.D6
AF0093:38 | SC | 009338 | WHT | 20 | 27.C7 | KA0130:A1 | PNL A,SMT130 | 27.C5
AF0093:COM | SC | 0V | WHT | 16 | 20.A3 | XT0090:2 | PNL A,SMT130 | 20.B1
AF0093:V+ | SC | FU0092 | WHT | 16 | 20.A3 | FU0092:LD | PNL A,SMT130 | 20.B1
AU0080:COM | SC | 0V | WHT | 16 | 20.C2 | XT0080:1 | PNL A,SMT130 | 20.D1
AU0080:V+ | SC | FU0080 | WHT | 16 | 20.C2 | FU0080:LD | PNL A,SMT130 | 20.D1
AU0090:COM | SC | 0V | WHT | 16 | 20.A2 | XT0090:1 | PNL A,SMT130 | 20.B1
AU0090:V+ | SC | FU0090 | WHT | 16 | 20.A2 | FU0090:LD | PNL A,SMT130 | 20.B1
FU0080:LI | SC | FU0137 | WHT | 14 | 20.D1 | FU0081:LI | PNL A,SMT130 | 20.D1
FU0080:LI | SC | FU0137 | WHT | 14 | 20.D1 | XT0139:1 | PNL A,SMT130 | 19.A5
FU0081:LI | SC | FU0137 | WHT | 14 | 20.D1 | FU0082:LI | PNL A,SMT130 | 20.D1
FU0090:LI | SC | FU0137 | WHT | 14 | 20.B1 | FU0091:LI | PNL A,SMT130 | 20.B1
FU0090:LI | SC | FU0137 | WHT | 14 | 20.B1 | XT0139:2 | PNL A,SMT130 | 19.A5
FU0091:LI | SC | FU0137 | WHT | 14 | 20.B1 | FU0092:LI | PNL A,SMT130 | 20.B1
FU0092:LI | SC | FU0137 | WHT | 14 | 20.B1 | FU0093:LI | PNL A,SMT130 | 20.B1
FU0137:LD | SC | FU0137 | WHT | 12 | 19.A5 | XT0139:1 | PNL A,SMT130 | 19.A5
FU0137:LI | SC | FU0136 | WHT | 12 | 19.A5 | XT0138:1 | PNL A,SMT130 | 19.A4
FU0139:LD | SC | FU0139 | WHT | 14 | 19.A6 | XT0136:1 | PNL A,SMT130 | 23.A2
FU0140:LI | SC | FU0137 | WHT | 14 | 19.A6 | FU0139:LI | PNL A,SMT130 | 19.A6
FU0140:LI | SC | FU0137 | WHT | 14 | 19.A6 | XT0139:1 | PNL A,SMT130 | 19.A5
FU2100:LI | SC | FU0137 | WHT | 14 | 19.B6 | XT0139:2 | PNL A,SMT130 | 19.A5
GR0131: | SC | GR0131 | GRN/YEL | 14 | 22.A4 | FRAME | PNL A,SMT130 | 22.A4
GR0132: | SC | GR0132 | GRN/YEL | 14 | 22.A4 | FRAME | PNL A,SMT130 | 22.A4
KA0130:A1 | SC | 009338 | WHT | 20 | 27.C5 | KA0130:11 | PNL A,SMT130 | 27.D6
KA0131:11 | SC | KA0135A1 | WHT | 20 | 23.D4 | KA0135:A1 | PNL A,SMT130 | 23.D6
KA0131:12 | SC | KA013724 | WHT | 20 | 23.D4 | KA0137:24 | PNL A,SMT130 | 23.D3
KA0131:A1 | SC | KA0231A1 | WHT | 20 | 23.B6 | KA0132:A1 | PNL A,SMT130 | 23.C6
KA0131:A1 | SC | KA0231A1 | WHT | 20 | 23.B6 | XT0136:12 | PNL A,SMT130 | 23.B5
KA0131:A2 | SC | 0V | WHT | 20 | 23.B6 | KA0132:A2 | PNL A,SMT130 | 23.C6
KA0131:A2 | SC | 0V | WHT | 20 | 23.B6 | KT0145:A2 | PNL A,SMT130 | 23.B6
KA0132:11 | SC | FU0139 | WHT | 20 | 23.A3 | KA0133:11 | PNL A,SMT130 | 23.B3
KA0132:11 | SC | FU0139 | WHT | 20 | 23.A3 | KT0145:15 | PNL A,SMT130 | 23.D2
KA0132:12 | SC | KT0141A1 | WHT | 20 | 23.A3 | KT0142:A1 | PNL A,SMT130 | 23.A6
KA0132:12 | SC | KT0141A1 | WHT | 20 | 23.A3 | KA0133:12 | PNL A,SMT130 | 23.B3
KA0132:21 | SC | KA0138A1 | WHT | 20 | 23.D4 | KA0138:A1 | PNL A,SMT130 | 23.D6
KA0132:22 | SC | KA013222 | WHT | 20 | 23.D4 | KA0137:14 | PNL A,SMT130 | 23.D3
KA0132:22 | SC | KA013222 | WHT | 20 | 23.D4 | KT0141:18 | PNL A,SMT130 | 23.D2
KA0132:24 | SC | KA013224 | WHT | 20 | 23.D4 | KA0134:14 | PNL A,SMT130 | 23.D3
KA0132:A1 | SC | KA0231A1 | WHT | 20 | 23.C6 | KA0141:A1 | PNL A,SMT130 | 23.C6
KA0132:A2 | SC | 0V | WHT | 20 | 23.C6 | KA0141:A2 | PNL A,SMT130 | 23.C6
KA0133:11 | SC | FU0139 | WHT | 20 | 23.B3 | KA0134:11 | PNL A,SMT130 | 23.D3
KA0133:A2 | SC | 0V | WHT | 20 | 23.C6 | KA0134:A2 | PNL A,SMT130 | 23.C6
KA0133:A2 | SC | 0V | WHT | 20 | 23.C6 | KA0141:A2 | PNL A,SMT130 | 23.C6
KA0134:11 | SC | FU0139 | WHT | 20 | 23.D3 | KA0136:11 | PNL A,SMT130 | 23.B4
KA0134:A1 | SC | KA0134A1 | WHT | 20 | 23.C6 | AF0081:08 | PNL A,SMT130 | 89.C7
KA0134:A2 | SC | 0V | WHT | 20 | 23.C6 | KA0135:A2 | PNL A,SMT130 | 23.D6
KA0135:11 | SC | KM3150EN | RED | 16 | 88.B7 | XT1135:2 | PNL A,SMT130 | 88.B6
KA0135:12 | SC | KM3150EP | RED | 16 | 88.B7 | XT1135:1 | PNL A,SMT130 | 88.B6
KA0135:21 | SC | KA013521 | WHT | 20 | 142.A6 | KA0176:A1 | PNL A,SMT130 | 142.A5
KA0135:A2 | SC | 0V | WHT | 20 | 23.D6 | KA0136:A2 | PNL A,SMT130 | 23.D6
KA0136:11 | SC | FU0139 | WHT | 20 | 23.B4 | KA0137:21 | PNL A,SMT130 | 23.D3
KA0136:14 | SC | KA013821 | WHT | 20 | 23.B4 | KA0138:21 | PNL A,SMT130 | 23.B5
KA0136:A1 | SC | PS32002 | WHT | 20 | 23.D6 | XT0136:5 | PNL A,SMT130 | 86.D5
KA0136:A2 | SC | 0V | WHT | 20 | 23.D6 | KA0137:A2 | PNL A,SMT130 | 23.D6
KA0137:11 | SC | FU0139 | WHT | 20 | 23.D3 | KA0137:21 | PNL A,SMT130 | 23.D3
KA0137:24 | SC | KA013724 | WHT | 20 | 23.D3 | AF0091:05 | PNL A,SMT130 | 23.C4
KA0137:A1 | SC | KA0137A1 | WHT | 20 | 23.D6 | KT0142:18 | PNL A,SMT130 | 23.D2
KA0137:A2 | SC | 0V | WHT | 20 | 23.D6 | KA0138:A2 | PNL A,SMT130 | 23.D6
KA0138:11 | SC | KM31701 | WHT | 20 | 89.C6 | XT0136:9 | PNL A,SMT130 | 89.C6
KA0138:14 | SC | FU0139 | WHT | 14 | 89.C6 | XT0136:11 | PNL A,SMT130 | 89.C7
KA0138:24 | SC | KT0144B1 | WHT | 20 | 23.B5 | KT0144:B1 | PNL A,SMT130 | 23.B6
KA0138:A1 | SC | KA0138A1 | WHT | 20 | 23.D6 | KA0142:A1 | PNL A,SMT130 | 23.D6
KA0138:A2 | SC | 0V | WHT | 20 | 23.D6 | KA0142:A2 | PNL A,SMT130 | 23.D6
KA0141:21 | SC | KT0146A1 | WHT | 20 | 23.B2 | KT0146:A1 | PNL A,SMT130 | 23.C2
KA0141:24 | SC | FU0139 | WHT | 20 | 23.B2 | XT0136:2 | PNL A,SMT130 | 23.A2
KA0176:11 | SC | KA024611 | WHT | 20 | 142.B6 | XT0137:1 | PNL A,SMT130 | 142.B5
KA0176:21 | SC | KA024621 | WHT | 20 | 144.A6 | XT0137:5 | PNL A,SMT130 | 144.A5
KA0176:A1 | SC | KA013521 | WHT | 20 | 142.A5 | KA0177:A1 | PNL A,SMT130 | 142.A5
KA0176:A2 | SC | 0V | WHT | 20 | 142.A5 | XT0135:3 | PNL A,SMT130 | 19.C5
KA0176:A2 | SC | 0V | WHT | 20 | 142.A5 | KA0177:A2 | PNL A,SMT130 | 142.A5
KA0177:11 | SC | KA024711 | WHT | 20 | 143.A6 | XT0137:3 | PNL A,SMT130 | 143.A5
KA0177:21 | SC | KA024721 | WHT | 20 | 145.A6 | XT0137:7 | PNL A,SMT130 | 145.A5
KA0875:11 | SC | HA0472BLK-2 | WHT | 20 | 28.A6 | KA0178:11 | PNL A,SMT130 | 28.A5
KA6211:11 | SC | KM6211EN | RED | 16 | 142.B6 | XT1135:4 | PNL A,SMT130 | 142.B6
KA6211:14 | SC | KM6211EP | RED | 16 | 142.B6 | XT1135:3 | PNL A,SMT130 | 142.A6
KA6212:11 | SC | KA6212EN | RED | 16 | 143.B6 | XT1135:6 | PNL A,SMT130 | 143.B5
KA6212:14 | SC | KM6212EP | RED | 16 | 143.B6 | XT1135:5 | PNL A,SMT130 | 143.A5
KT0140:15 | SC | FU0139 | WHT | 20 | 23.D1 | KT0142:15 | PNL A,SMT130 | 23.D2
KT0140:15 | SC | FU0139 | WHT | 20 | 23.B2 | XT0136:2 | PNL A,SMT130 | 23.A2
KT0140:16 | SC | KT014115 | WHT | 20 | 23.D1 | KT0141:15 | PNL A,SMT130 | 23.D2
KT0140:18 | SC | KT0143A1 | WHT | 20 | 23.B2 | KT0143:A1 | PNL A,SMT130 | 23.B6
KT0140:A1 | SC | KT0140A1 | WHT | 20 | 23.A6 | KT0143:16 | PNL A,SMT130 | 23.A5
KT0140:A2 | SC | 0V | WHT | 20 | 23.A6 | KT0141:A2 | PNL A,SMT130 | 23.A6
KT0140:A2 | SC | 0V | WHT | 20 | 23.A6 | XT0136:3 | PNL A,SMT130 | 23.A2
KT0141:18 | SC | KA013222 | WHT | 20 | 23.D2 | KT0144:18 | PNL A,SMT130 | 23.D2
KT0141:A1 | SC | KT0141A1 | WHT | 20 | 23.A6 | KT0143:15 | PNL A,SMT130 | 23.A5
KT0141:A1 | SC | KT0141A1 | WHT | 20 | 23.A6 | KT0142:A1 | PNL A,SMT130 | 23.A6
KT0141:A2 | SC | 0V | WHT | 20 | 23.A6 | KT0142:A2 | PNL A,SMT130 | 23.A6
KT0142:15 | SC | FU0139 | WHT | 20 | 23.D2 | KT0144:A1 | PNL A,SMT130 | 23.B6
KT0142:18 | SC | KA0137A1 | WHT | 20 | 23.D2 | KT0145:18 | PNL A,SMT130 | 23.D2
KT0142:A2 | SC | 0V | WHT | 20 | 23.A6 | KT0143:A2 | PNL A,SMT130 | 23.B6
KT0143:A2 | SC | 0V | WHT | 20 | 23.B6 | KT0144:A2 | PNL A,SMT130 | 23.B6
KT0144:15 | SC | FU0139 | WHT | 20 | 23.D2 | KT0145:15 | PNL A,SMT130 | 23.D2
KT0144:15 | SC | FU0139 | WHT | 20 | 23.D2 | KT0144:A1 | PNL A,SMT130 | 23.B6
KT0144:A2 | SC | 0V | WHT | 20 | 23.B6 | KT0145:A2 | PNL A,SMT130 | 23.B6
PC0470:INP_A | SC | 009207 | WHT | 20 | 25.D5 | PC0470:INP_B | PNL A,SMT130 | 25.D5
VD6211:--1N4007 | SC | KA024611 | LEAD | --- | 142.B5 | XT0137:1 | PNL A,SMT130 | 142.B5
VD6211:+-1N4007 | SC | 009204 | LEAD | --- | 142.B5 | XT0137:2 | PNL A,SMT130 | 142.B6
VD6212:--1N4007 | SC | KA024711 | LEAD | --- | 143.A5 | XT0137:3 | PNL A,SMT130 | 143.A5
VD6212:+-1N4007 | SC | 009213 | LEAD | --- | 143.A5 | XT0137:4 | PNL A,SMT130 | 143.A6
VD6221:--1N4007 | SC | KA024621 | LEAD | --- | 144.A5 | XT0137:5 | PNL A,SMT130 | 144.A5
VD6221:+-1N4007 | SC | 009200 | LEAD | --- | 144.A5 | XT0137:6 | PNL A,SMT130 | 144.A6
VD6222:--1N4007 | SC | KA024721 | LEAD | --- | 145.A5 | XT0137:7 | PNL A,SMT130 | 145.A5
VD6222:+-1N4007 | SC | 009201 | LEAD | --- | 145.A5 | XT0137:8 | PNL A,SMT130 | 145.A6
XT0080:1 | SC | 0V | WHT | 14 | 20.D1 | XT0135:1 | PNL A,SMT130 | 19.B5
XT0134:1 | SC | 0V | WHT | 12 | 19.B4 | XT0135:1 | PNL A,SMT130 | 19.B5
XT0135:1 | SC | 0V | WHT | 14 | 19.B5 | XT0136:3 | PNL A,SMT130 | 23.A2
XT0135:2 | SC | 0V | WHT | 14 | 19.C5 | XT0090:1 | PNL A,SMT130 | 20.B1
XT0136:1 | SC | FU0139 | WHT | 14 | 23.A2 | XT0136:11 | PNL A,SMT130 | 89.C7
XT0136:10 | SC | 0V | WHT | 16 | 89.C6 | XT0136:3 | PNL A,SMT130 | 23.A2
XT0136:4 | SC | FU0139 | WHT | 14 | 86.D5 | XT0136:1 | PNL A,SMT130 | 23.A2
AU0080:L1 | WC0009 | AU0090L2 | ENET | CABLE | 2.A3 | AU0090:L2 | PNL A,SMT130 | 2.A2
AF0081:20 | SC | SV21202 | WHT | 16 | 65.B7 | XT0060:4 | PNL B,SMT130 | 65.B5
AF0086:SH | SC | IEG02304 | GRN | 14 | 20.D5 | IEG0230:4 | PNL B,SMT130 | 20.D6
AF0091:15 | SC | SB6200C | WHT | 20 | 47.B6 | XT0240:27 | PNL B,SMT130 | 47.B5
AF0091:47 | SC | SB6200NO | WHT | 20 | 47.B6 | XT0240:26 | PNL B,SMT130 | 47.B5
AF0092:15 | SC | HL62002 | WHT | 20 | 47.B6 | XT0240:24 | PNL B,SMT130 | 47.B5
AF0092:31 | SC | HL62001 | WHT | 20 | 47.B6 | XT0240:25 | PNL B,SMT130 | 47.B5
AF0093:00 | SC | UA1200J21 | WHT | 20 | 24.A7 | KA0241:11 | PNL B,SMT130 | 24.A5
AF0093:02 | SC | KA024314 | WHT | 20 | 24.B7 | KA0243:14 | PNL B,SMT130 | 24.B6
AF0093:03 | SC | KA024524 | WHT | 20 | 24.B7 | KA0245:24 | PNL B,SMT130 | 24.B6
AF0093:05 | SC | KA026014 | WHT | 20 | 24.C7 | KA0260:14 | PNL B,SMT130 | 24.C6
AF0093:07 | SC | KA023924 | WHT | 20 | 24.A7 | KA0239:24 | PNL B,SMT130 | 24.B6
AF0093:10 | SC | SB047312 | WHT | 20 | 47.A6 | XT0240:19 | PNL B,SMT130 | 47.A5
AF0093:11 | SC | SB751212 | WHT | 16 | 134.A7 | XT0240:15 | PNL B,SMT130 | 134.A5
AF0093:12 | SC | KA024214 | WHT | 20 | 24.C7 | KA0242:14 | PNL B,SMT130 | 24.C6
AF0093:22 | SC | UA1200J27 | WHT | 20 | 27.C7 | UA1200:J2-7 | PNL B,SMT130 | 27.B1
AF0093:34 | SC | KA024311 | WHT | 20 | 24.B7 | KA0243:11 | PNL B,SMT130 | 24.B6
AF0093:35 | SC | KA024521 | WHT | 20 | 24.B7 | KA0245:21 | PNL B,SMT130 | 24.B6
AF0093:37 | SC | KA026011 | WHT | 20 | 24.C7 | KA0260:11 | PNL B,SMT130 | 24.C6
AF0093:39 | SC | KA023921 | WHT | 20 | 24.A7 | KA0239:21 | PNL B,SMT130 | 24.B6
AF0093:42 | SC | SB047311 | WHT | 20 | 47.A6 | XT0240:18 | PNL B,SMT130 | 47.A5
AF0093:43 | SC | SB751211 | WHT | 16 | 134.A7 | XT0240:14 | PNL B,SMT130 | 134.A5
AU0090:GND | SC | IEG02305 | GRN | 14 | 20.A2 | IEG0230:5 | PNL B,SMT130 | 20.B1
GR0111: | SC | IEG02303 | GRN | 14 | 22.A4 | IEG0230:3 | PNL B,SMT130 | 22.A4
GR0134: | SC | IEG02307 | GRN | 14 | 22.A4 | IEG0230:7 | PNL B,SMT130 | 22.A4
KA0130:A2 | SC | UA1200J26 | WHT | 20 | 27.C5 | UA1200:J2-6 | PNL B,SMT130 | 27.B1
KA0135:21 | SC | KA013521 | WHT | 20 | 142.A6 | KA0249:11 | PNL B,SMT130 | 142.A6
KA0135:22 | SC | KA013522 | WHT | 20 | 142.A6 | KA0232:21 | PNL B,SMT130 | 142.A6
KA0141:21 | SC | KT0146A1 | WHT | 20 | 23.B2 | KA0241:21 | PNL B,SMT130 | 23.B2
KA0141:24 | SC | FU0139 | WHT | 20 | 23.B2 | KA0241:24 | PNL B,SMT130 | 23.B2
KA0178:14 | SC | KA017814 | WHT | 20 | 28.A5 | KA0232:11 | PNL B,SMT130 | 28.A6
KA0178:A1 | SC | KA0178A1 | WHT | 20 | 28.D3 | XT0240:22 | PNL B,SMT130 | 28.D4
KA0178:A2 | SC | 017824 | WHT | 20 | 28.D3 | XT0240:23 | PNL B,SMT130 | 28.D4
KA0221:11 | SC | KA023814 | WHT | 20 | 65.B6 | KA0238:14 | PNL B,SMT130 | 65.B5
KA0221:A1 | SC | KA0221A1 | WHT | 20 | 65.B6 | AF0075:03 | PNL B,SMT130 | 65.B7
KA0221:A2 | SC | KA0221A2 | WHT | 20 | 65.B6 | AF0075:19 | PNL B,SMT130 | 65.B7
KA0222:11 | SC | KA023824 | WHT | 20 | 65.C6 | KA0238:24 | PNL B,SMT130 | 65.C5
KA0222:14 | SC | 006306 | WHT | 20 | 65.C6 | AF0063:06 | PNL B,SMT130 | 65.C7
KA0222:A1 | SC | KA0222A1 | WHT | 20 | 65.C6 | AF0075:04 | PNL B,SMT130 | 65.C7
KA0222:A2 | SC | KA0222A2 | WHT | 20 | 65.C6 | AF0075:20 | PNL B,SMT130 | 65.C7
KA0875:11 | SC | HA0472BLK-2 | WHT | 20 | 28.A6 | XT0235:5 | PNL B,SMT130 | 28.A5
KA0875:14 | SC | FU0136 | WHT | 20 | 28.A6 | XT0235:7 | PNL B,SMT130 | 28.A6
KA0875:14 | SC | FU0136 | WHT | 20 | 28.A6 | KA0232:12 | PNL B,SMT130 | 28.A6
KA6211:A1 | SC | KA6211A1 | WHT | 20 | 142.B6 | KA0246:14 | PNL B,SMT130 | 142.B5
KA6212:A1 | SC | KA6212A1 | WHT | 20 | 143.A6 | KA0247:14 | PNL B,SMT130 | 143.A5
KA6221:A1 | SC | KA6221A1 | WHT | 20 | 144.A6 | KA0246:24 | PNL B,SMT130 | 144.A5
KA6222:A1 | SC | KA6222A1 | WHT | 20 | 145.A6 | KA0247:24 | PNL B,SMT130 | 145.A5
KT0145:A1 | SC | KA024412 | WHT | 14 | 23.B6 | KA0244:12 | PNL B,SMT130 | 24.D4
KT0146:15 | SC | KT014615 | WHT | 20 | 24.D6 | AF0075:08 | PNL B,SMT130 | 24.D7
KT0146:18 | SC | KA024214 | WHT | 20 | 24.D6 | KA0231:14 | PNL B,SMT130 | 24.C6
KT0146:A2 | SC | KT0146A2 | WHT | 20 | 23.C2 | AF0075:25 | PNL B,SMT130 | 23.C2
KT0146:B1 | SC | KT0146B1 | WHT | 20 | 23.C2 | AF0075:09 | PNL B,SMT130 | 23.C2
XT0134:2 | SC | 0V | WHT | 14 | 19.C4 | XT0235:8 | PNL B,SMT130 | 28.A6
XT0134:4 | SC | 0V | WHT | 14 | 19.C4 | XT0235:1 | PNL B,SMT130 | 19.D5
XT0136:1 | SC | FU0139 | WHT | 14 | 23.A2 | XT0240:12 | PNL B,SMT130 | 24.C4
XT0136:12 | SC | KA0231A1 | WHT | 20 | 23.B5 | KA0242:11 | PNL B,SMT130 | 24.C6
XT0136:3 | SC | 0V | WHT | 20 | 23.A2 | XT0240:10 | PNL B,SMT130 | 24.D3
XT0136:6 | SC | PS32004 | WHT | 20 | 86.D5 | KA0240:11 | PNL B,SMT130 | 86.D5
XT0136:7 | SC | UF1300P | WHT | 20 | 86.D6 | KA0240:14 | PNL B,SMT130 | 86.D5
XT0137:1 | SC | KA024611 | WHT | 20 | 142.B5 | KA0246:11 | PNL B,SMT130 | 142.B5
XT0137:3 | SC | KA024711 | WHT | 20 | 143.A5 | KA0247:11 | PNL B,SMT130 | 143.A5
XT0137:5 | SC | KA024621 | WHT | 20 | 144.A5 | KA0246:21 | PNL B,SMT130 | 144.A5
XT0137:7 | SC | KA024721 | WHT | 20 | 145.A5 | KA0247:21 | PNL B,SMT130 | 145.A5
XT0138:2 | SC | FU0136 | WHT | 14 | 19.A4 | XT0235:7 | PNL B,SMT130 | 28.A6
XT0138:4 | SC | FU0136 | WHT | 12 | 19.B4 | FU0210:LI | PNL B,SMT130 | 19.C5
XT0138:4 | SC | FU0136 | WHT | 14 | 19.B4 | KA0232:22 | PNL B,SMT130 | 142.A6
AU0080:L2 | WC0008 | AU0080L2 | ENET | CABLE | 2.A3 | AU0070:L1 | PNL B,SMT130 | 2.A4
SolarTools ver. 24.0.84.24712 (Jul 31, 2025)
Report date: 2/3/2026 11:55 AM

## PNL B,SMT130
PNL B,SMT130
Project # | 4L321
Project Name | Enterprise SMT130 M4 WTX
Revision | 0.1
Controls DE
Phone:
Controls ME
Phone:
From | [5 empty] | To
Device ID | Cable (W) Conductor (SC) Jumper Clip (JC) | Wire No. | Wire ID | Gauge/Size | Page/Zone | Device ID | Location | Page/Zone
XT0060:1 | JC | 0V | CLIP | --- | 21.D1 | XT0060:2 | PNL B,SMT130 | 21.D1
XT0110:1 | JC | FU0110 | CLIP | --- | 26.A4 | XT0110:2 | PNL B,SMT130 | 26.A4
XT0110:4 | JC | 0V | CLIP | --- | 26.A4 | XT0110:3 | PNL B,SMT130 | 26.A4
XT0233:1 | JC | FU0210 | CLIP | --- | 19.C5 | XT0233:2 | PNL B,SMT130 | 19.C5
XT0233:2 | JC | FU0210 | CLIP | --- | 19.C5 | XT0233:3 | PNL B,SMT130 | 19.D5
XT0235:1 | JC | 0V | CLIP | --- | 19.D5 | XT0235:2 | PNL B,SMT130 | 19.D5
XT0235:2 | JC | 0V | CLIP | --- | 19.D5 | XT0235:3 | PNL B,SMT130 | 19.D5
XT0240:11 | JC | FU0139 | CLIP | --- | 24.C4 | XT0240:12 | PNL B,SMT130 | 24.C4
XT0240:9 | JC | 0V | CLIP | --- | 24.D3 | XT0240:10 | PNL B,SMT130 | 24.D3
AF0061:02 | SC | 006102 | WHT | 20 | 58.B7 | KA0233:14 | PNL B,SMT130 | 58.B5
AF0061:14 | SC | 006114 | WHT | 20 | 56.B7 | KA0234:14 | PNL B,SMT130 | 56.B5
AF0061:COM | SC | 0V | WHT | 16 | 21.C2 | XT0060:1 | PNL B,SMT130 | 21.D1
AF0061:V+ | SC | FU0061 | WHT | 16 | 21.C2 | FU0061:LD | PNL B,SMT130 | 21.D1
AF0062:COM | SC | 0V | WHT | 16 | 21.C3 | XT0060:2 | PNL B,SMT130 | 21.D1
AF0062:V+ | SC | FU0062 | WHT | 16 | 21.C3 | FU0062:LD | PNL B,SMT130 | 21.D1
AF0063:22 | SC | SV21242 | WHT | 16 | 65.C7 | XT0060:5 | PNL B,SMT130 | 65.C5
AF0063:COM | SC | 0V | WHT | 16 | 21.C3 | XT0060:2 | PNL B,SMT130 | 21.D1
AF0063:V+ | SC | FU0063 | WHT | 16 | 21.C3 | FU0063:LD | PNL B,SMT130 | 21.D1
AF0064:COM | SC | AF0064N | WHT | 16 | 21.C4 | AF0065:COM | PNL B,SMT130 | 21.C5
AF0064:COM | SC | 0V | WHT | 16 | 21.C4 | XT0060:2 | PNL B,SMT130 | 21.D1
AF0064:V+ | SC | AF0064P | WHT | 16 | 21.C4 | AF0065:V+ | PNL B,SMT130 | 21.C5
AF0064:V+ | SC | FU0064 | WHT | 16 | 21.C4 | FU0064:LD | PNL B,SMT130 | 21.D1
AF0065:COM | SC | AF0065N | WHT | 16 | 21.C5 | AF0066:COM | PNL B,SMT130 | 21.C5
AF0065:J | SC | * |  |  | 21.C5 | AF0066:P | PNL B,SMT130 | 21.C5
AF0065:SH | SC | AF0065G | GRN | 14 | 21.C5 | AF0066:SH | PNL B,SMT130 | 21.C5
AF0065:SH | SC | AU0060G | GRN | 14 | 21.C5 | AU0060:GND | PNL B,SMT130 | 21.C2
AF0065:V+ | SC | AF0065P | WHT | 16 | 21.C5 | AF0066:V+ | PNL B,SMT130 | 21.C5
AF0066:COM | SC | AF0066N | WHT | 16 | 21.C5 | AF0067:COM | PNL B,SMT130 | 21.C6
AF0066:J | SC | * |  |  | 21.C5 | AF0067:P | PNL B,SMT130 | 21.C6
AF0066:SH | SC | AF0066G | GRN | 14 | 21.C5 | AF0067:SH | PNL B,SMT130 | 21.C6
AF0066:V+ | SC | AF0066P | WHT | 16 | 21.C5 | AF0067:V+ | PNL B,SMT130 | 21.C6
AF0067:COM | SC | AF0067N | WHT | 16 | 21.C6 | AF0068:COM | PNL B,SMT130 | 21.C6
AF0067:J | SC | * |  |  | 21.C6 | AF0068:P | PNL B,SMT130 | 21.C6
AF0067:SH | SC | AF0067G | GRN | 14 | 21.C6 | AF0068:SH | PNL B,SMT130 | 21.C6
AF0067:V+ | SC | AF0067P | WHT | 16 | 21.C6 | AF0068:V+ | PNL B,SMT130 | 21.C6
AF0068:SH | SC | IEG02302 | GRN | 14 | 21.C6 | IEG0230:2 | PNL B,SMT130 | 21.D6
AF0071:COM | SC | AF0071N | WHT | 16 | 21.B2 | AF0072:COM | PNL B,SMT130 | 21.B3
AF0071:COM | SC | AU0070N | WHT | 16 | 21.B2 | AU0070:COM | PNL B,SMT130 | 21.A2
AF0071:J | SC | * |  |  | 21.B2 | AF0072:P | PNL B,SMT130 | 21.B3
AF0071:SH | SC | AF0071G | GRN | 14 | 21.B2 | AF0072:SH | PNL B,SMT130 | 21.B3
AF0071:SH | SC | AU0070G | GRN | 14 | 21.B2 | AU0070:GND | PNL B,SMT130 | 21.A2
AF0071:V+ | SC | AF0071P | WHT | 16 | 21.B2 | AF0072:V+ | PNL B,SMT130 | 21.B3
AF0071:V+ | SC | AU0070P | WHT | 16 | 21.B2 | AU0070:V+ | PNL B,SMT130 | 21.A2
AF0072:COM | SC | AF0072N | WHT | 16 | 21.B3 | AF0073:COM | PNL B,SMT130 | 21.A3
AF0072:J | SC | * |  |  | 21.B3 | AF0073:P | PNL B,SMT130 | 21.A3
AF0072:SH | SC | AF0072G | GRN | 14 | 21.B3 | AF0073:SH | PNL B,SMT130 | 21.A3
AF0072:V+ | SC | AF0072P | WHT | 16 | 21.B3 | AF0073:V+ | PNL B,SMT130 | 21.A3
AF0073:COM | SC | AF0073N | WHT | 16 | 21.A3 | AF0074:COM | PNL B,SMT130 | 21.B4
AF0073:J | SC | * |  |  | 21.A3 | AF0074:P | PNL B,SMT130 | 21.B4
AF0073:SH | SC | AF0073G | GRN | 14 | 21.A3 | AF0074:SH | PNL B,SMT130 | 21.B4
AF0073:V+ | SC | AF0073P | WHT | 16 | 21.A3 | AF0074:V+ | PNL B,SMT130 | 21.B4
AF0074:J | SC | * |  |  | 21.B4 | AF0075:P | PNL B,SMT130 | 21.A5
AF0074:SH | SC | IEG02301 | GRN | 14 | 21.B4 | IEG0230:1 | PNL B,SMT130 | 21.B5
AF0075:00 | SC | KA023624 | WHT | 16 | 69.B7 | KA0236:24 | PNL B,SMT130 | 69.B5
AF0075:01 | SC | KA023714 | WHT | 16 | 70.B7 | KA0237:14 | PNL B,SMT130 | 70.B5
AF0075:07 | SC | 007507 | WHT | 20 | 25.C6 | KA1020:A1 | PNL B,SMT130 | 25.C5
AF0075:10 | SC | UA1200J14 | WHT | 20 | 27.C7 | UA1200:J1-4 | PNL B,SMT130 | 27.B1
AF0075:11 | SC | 007511 | WHT | 20 | 27.C7 | XT0237:1 B2 | PNL B,SMT130 | 27.C5
AF0075:23 | SC | 007523 | WHT | 20 | 25.C6 | KA1020:A2 | PNL B,SMT130 | 25.C5
AF0075:24 | SC | KA0231A2 | WHT | 20 | 24.D7 | KA0231:A2 | PNL B,SMT130 | 24.D6
AF0075:COM | SC | 0V | WHT | 16 | 21.A5 | XT0070:2 | PNL B,SMT130 | 21.B1
AF0075:V+ | SC | FU0071 | WHT | 16 | 21.A5 | FU0071:LD | PNL B,SMT130 | 21.B1
AF0400:12 | SC | XT04001 | GRN | 16 | 26.B6 | XT0400:1 | PNL B,SMT130 | 26.C5
AF0410:32 | SC | XT04001 | GRN | 16 | 26.B5 | XT0400:1 | PNL B,SMT130 | 26.C5
AF0410:53 | SC | 0V | WHT | 16 | 26.B5 | XT0110:3 | PNL B,SMT130 | 26.A4
AF0410:54 | SC | 0V | WHT | 16 | 26.B5 | AF0420:53 | PNL B,SMT130 | 26.B4
AF0410:55 | SC | FU0113 | WHT | 16 | 26.B5 | FU0113:LD | PNL B,SMT130 | 26.A4
AF0410:56 | SC | FU0113 | WHT | 16 | 26.B5 | AF0420:55 | PNL B,SMT130 | 26.B4
AF0420:32 | SC | XT04001 | GRN | 16 | 26.B4 | XT0400:1 | PNL B,SMT130 | 26.C5
AF0420:54 | SC | 0V | WHT | 16 | 26.B4 | AF0450:53 | PNL B,SMT130 | 26.B3
AF0420:56 | SC | FU0113 | WHT | 16 | 26.B4 | AF0450:55 | PNL B,SMT130 | 26.B3
AF0450:32 | SC | AF045032 | GRN | 16 | 26.B3 | XT0400:2 | PNL B,SMT130 | 26.C3
AU0060:COM | SC | 0V | WHT | 16 | 21.C2 | XT0060:1 | PNL B,SMT130 | 21.D1
AU0060:V+ | SC | FU0060 | WHT | 16 | 21.C2 | FU0060:LD | PNL B,SMT130 | 21.C1
AU0070:COM | SC | 0V | WHT | 16 | 21.A2 | XT0070:1 | PNL B,SMT130 | 21.B1
AU0070:V+ | SC | FU0070 | WHT | 16 | 21.A2 | FU0070:LD | PNL B,SMT130 | 21.B1
FU0060:LI | SC | FU0210 | WHT | 14 | 21.C1 | FU0061:LI | PNL B,SMT130 | 21.D1
FU0060:LI | SC | FU0210 | WHT | 14 | 21.C1 | XT0233:2 | PNL B,SMT130 | 19.C5
FU0061:LI | SC | FU0210 | WHT | 14 | 21.D1 | FU0062:LI | PNL B,SMT130 | 21.D1
FU0062:LI | SC | FU0210 | WHT | 14 | 21.D1 | FU0063:LI | PNL B,SMT130 | 21.D1
FU0063:LI | SC | FU0210 | WHT | 14 | 21.D1 | FU0064:LI | PNL B,SMT130 | 21.D1
FU0070:LI | SC | FU0210 | WHT | 14 | 21.B1 | XT0233:2 | PNL B,SMT130 | 19.C5
FU0070:LI | SC | FU0210 | WHT | 14 | 21.B1 | FU0071:LI | PNL B,SMT130 | 21.B1
FU0110:LD | SC | FU0110 | WHT | 14 | 26.A5 | XT0110:1 | PNL B,SMT130 | 26.A4
FU0110:LI | SC | FU0210 | WHT | 14 | 26.A5 | XT0233:1 | PNL B,SMT130 | 19.C5
FU0113:LI | SC | FU0110 | WHT | 14 | 26.A4 | XT0110:1 | PNL B,SMT130 | 26.A4
FU0210:LD | SC | FU0210 | WHT | 12 | 19.C5 | XT0233:1 | PNL B,SMT130 | 19.C5
FU0211:LD | SC | FU0211 | WHT | 16 | 19.D6 | KA1020:14 | PNL B,SMT130 | 62.A5
FU0211:LI | SC | FU0210 | WHT | 12 | 19.D6 | XT0233:3 | PNL B,SMT130 | 19.D5
FU0212:LD | SC | FU0212 | WHT | 16 | 19.C6 | KA0248:21 | PNL B,SMT130 | 27.C6
FU0212:LI | SC | FU0210 | WHT | 14 | 19.C6 | XT0233:1 | PNL B,SMT130 | 19.C5
FU0213:LD | SC | FU0213 | WHT | 20 | 19.D6 | XT0233:4 | PNL B,SMT130 | 27.D5
FU0213:LI | SC | FU0210 | WHT | 14 | 19.D6 | XT0233:3 | PNL B,SMT130 | 19.D5
GR0233: | SC | GR0233 | GRN/YEL | 14 | 22.B4 | FRAME | PNL B,SMT130 | 22.B4
GR0244: | SC | IEG023011 | GRN | 14 | 22.A4 | IEG0230:11 | PNL B,SMT130 | 22.A4
GR0251: | SC | IEG02306 | GRN | 14 | 22.B4 | IEG0230:6 | PNL B,SMT130 | 22.B4
IEG0230:8 | SC | IEG02308 | GRN | 16 | 27.D2 | UA1200:J3-4 | PNL B,SMT130 | 27.B1
IEG0230:9 | SC | IEG02309 | GRN | 14 | 26.C6 | XT0400:3 | PNL B,SMT130 | 26.C6
KA0231:11 | SC | KA0231A1 | WHT | 20 | 24.C6 | KA0231:A1 | PNL B,SMT130 | 24.D6
KA0231:11 | SC | KA0231A1 | WHT | 20 | 24.C6 | KA0242:11 | PNL B,SMT130 | 24.C6
KA0231:14 | SC | KA024214 | WHT | 20 | 24.C6 | KA0242:14 | PNL B,SMT130 | 24.C6
KA0231:21 | SC | KA023121 | WHT | 20 | 24.A5 | KA0260:24 | PNL B,SMT130 | 24.A4
KA0231:A1 | SC | KA0231A1 | WHT | 20 | 24.D6 | KA0232:A1 | PNL B,SMT130 | 24.D6
KA0231:A2 | SC | KA0231A2 | WHT | 20 | 24.D6 | KA0232:A2 | PNL B,SMT130 | 24.D6
KA0232:21 | SC | KA013522 | WHT | 20 | 142.A6 | KA0249:12 | PNL B,SMT130 | 142.A6
KA0232:A1 | SC | KA0231A1 | WHT | 20 | 24.D6 | KA0233:A1 | PNL B,SMT130 | 24.D6
KA0232:A2 | SC | KA0231A2 | WHT | 20 | 24.D6 | KA0233:A2 | PNL B,SMT130 | 24.D6
KA0233:A1 | SC | KA0231A1 | WHT | 20 | 24.D6 | KA0234:A1 | PNL B,SMT130 | 24.D6
KA0233:A2 | SC | KA0231A2 | WHT | 20 | 24.D6 | KA0234:A2 | PNL B,SMT130 | 24.D6
KA0235:11 | SC | UA1200J21 | WHT | 20 | 24.A5 | XT0060:3 | PNL B,SMT130 | 27.D5
KA0235:11 | SC | UA1200J21 | WHT | 20 | 24.A5 | KA0241:11 | PNL B,SMT130 | 24.A5
KA0235:14 | SC | KA024114 | WHT | 20 | 24.A5 | KA0241:14 | PNL B,SMT130 | 24.A5
KA0235:A1 | SC | ESTOP | WHT | 20 | 24.A2 | KA0236:A1 | PNL B,SMT130 | 24.B2
KA0235:A1 | SC | ESTOP | WHT | 20 | 24.A2 | XT0240:4 | PNL B,SMT130 | 24.A3
KA0236:11 | SC | FU0139 | WHT | 20 | 24.D4 | KA0244:11 | PNL B,SMT130 | 24.D4
KA0236:11 | SC | FU0139 | WHT | 20 | 24.D4 | XT0240:12 | PNL B,SMT130 | 24.C4
KA0236:12 | SC | KA023612 | WHT | 20 | 24.D4 | XT0240:13 | PNL B,SMT130 | 24.D4
KA0236:A1 | SC | ESTOP | WHT | 20 | 24.B2 | KA0237:A1 | PNL B,SMT130 | 24.B2
KA0236:A2 | SC | 0V | WHT | 20 | 24.B2 | KA0235:A2 | PNL B,SMT130 | 24.A2
KA0236:A2 | SC | 0V | WHT | 20 | 24.B2 | KA0237:A2 | PNL B,SMT130 | 24.B2
KA0237:A1 | SC | ESTOP | WHT | 20 | 24.B2 | KA0238:A1 | PNL B,SMT130 | 24.B2
KA0237:A2 | SC | 0V | WHT | 20 | 24.B2 | KA0238:A2 | PNL B,SMT130 | 24.B2
KA0238:A1 | SC | ESTOP | WHT | 20 | 24.B2 | KA0239:A1 | PNL B,SMT130 | 24.B2
KA0238:A2 | SC | 0V | WHT | 20 | 24.B2 | KA0239:A2 | PNL B,SMT130 | 24.B2
KA0239:A1 | SC | ESTOP | WHT | 20 | 24.B2 | KA0240:A1 | PNL B,SMT130 | 24.B2
KA0239:A2 | SC | 0V | WHT | 20 | 24.B2 | KA0240:A2 | PNL B,SMT130 | 24.B2
KA0240:A1 | SC | ESTOP | WHT | 20 | 24.B2 | KA0248:A1 | PNL B,SMT130 | 24.C2
KA0240:A2 | SC | 0V | WHT | 20 | 24.B2 | KA0248:A2 | PNL B,SMT130 | 24.C2
KA0241:14 | SC | KA024114 | WHT | 20 | 24.A5 | KA0231:24 | PNL B,SMT130 | 24.A5
KA0241:A1 | SC | KA0241A1 | WHT | 20 | 24.C2 | KA0242:A1 | PNL B,SMT130 | 24.C2
KA0241:A1 | SC | KA0241A1 | WHT | 20 | 24.C2 | XT0240:6 | PNL B,SMT130 | 24.C3
KA0241:A2 | SC | 0V | WHT | 20 | 24.C2 | KA0242:A2 | PNL B,SMT130 | 24.C2
KA0241:A2 | SC | 0V | WHT | 20 | 24.C2 | KA0250:A2 | PNL B,SMT130 | 24.C2
KA0242:21 | SC | 024221 | WHT | 20 | 27.C6 | XT0237:1 T2 | PNL B,SMT130 | 27.C5
KA0242:24 | SC | 024822 | WHT | 20 | 27.C6 | KA0248:22 | PNL B,SMT130 | 27.C6
KA0242:A2 | SC | 0V | WHT | 20 | 24.C2 | KA0243:A2 | PNL B,SMT130 | 24.C2
KA0243:21 | SC | SB751221 | WHT | 20 | 24.A3 | XT0240:1 | PNL B,SMT130 | 24.A3
KA0243:24 | SC | KA024511 | WHT | 20 | 24.A3 | KA0245:11 | PNL B,SMT130 | 24.A4
KA0243:A1 | SC | KA0243A1 | WHT | 20 | 24.C2 | KA0244:A1 | PNL B,SMT130 | 24.D2
KA0243:A1 | SC | KA0243A1 | WHT | 20 | 24.C2 | XT0240:7 | PNL B,SMT130 | 24.C3
KA0243:A2 | SC | 0V | WHT | 20 | 24.C2 | KA0244:A2 | PNL B,SMT130 | 24.D2
KA0244:A1 | SC | KA0243A1 | WHT | 20 | 24.D2 | KA0246:A1 | PNL B,SMT130 | 24.D2
KA0244:A2 | SC | 0V | WHT | 20 | 24.D2 | KA0246:A2 | PNL B,SMT130 | 24.D2
KA0245:14 | SC | KA026021 | WHT | 20 | 24.A4 | KA0260:21 | PNL B,SMT130 | 24.A4
KA0245:A1 | SC | KA0245A1 | WHT | 20 | 24.D2 | KA0249:A1 | PNL B,SMT130 | 24.D2
KA0245:A1 | SC | KA0245A1 | WHT | 20 | 24.D2 | XT0240:8 | PNL B,SMT130 | 24.D3
KA0245:A2 | SC | 0V | WHT | 20 | 24.D2 | KA0249:A2 | PNL B,SMT130 | 24.D2
KA0245:A2 | SC | 0V | WHT | 20 | 24.D2 | KA0247:A2 | PNL B,SMT130 | 24.D2
KA0246:A1 | SC | KA0243A1 | WHT | 20 | 24.D2 | KA0247:A1 | PNL B,SMT130 | 24.D2
KA0246:A2 | SC | 0V | WHT | 20 | 24.D2 | KA0247:A2 | PNL B,SMT130 | 24.D2
KA0248:A1 | SC | ESTOP | WHT | 20 | 24.C2 | KA0250:A1 | PNL B,SMT130 | 24.C2
KA0248:A2 | SC | 0V | WHT | 20 | 24.C2 | KA0250:A2 | PNL B,SMT130 | 24.C2
KA0249:A2 | SC | 0V | WHT | 20 | 24.D2 | XT0240:10 | PNL B,SMT130 | 24.D3
KA0260:A1 | SC | KA0260A1 | WHT | 20 | 24.B4 | XT0240:37 | PNL B,SMT130 | 24.B4
KA0260:A2 | SC | 0V | WHT | 14 | 24.B4 | XT0240:9 | PNL B,SMT130 | 24.D3
KA1020:24 | SC | 0V | WHT | 20 | 62.A5 | XT0235:3 | PNL B,SMT130 | 19.D5
UA1200:J1-10 | SC | FU0213 | WHT | 20 | 27.B1 | XT0233:4 | PNL B,SMT130 | 27.D5
UA1200:J1-5 | SC | UA1200J15 | WHT | 20 | 27.B1 | XT0237:1 B1 | PNL B,SMT130 | 27.C5
UA1200:J1-8 | SC | UA1200J | WHT | 20 | 55.B6 | UA1200:J3-5 | PNL B,SMT130 | 55.B6
UA1200:J1-9 | SC | 0V | WHT | 20 | 27.B1 | XT0235:4 | PNL B,SMT130 | 27.D5
UA1200:J2-1 | SC | UA1200J21 | WHT | 20 | 27.B1 | XT0060:3 | PNL B,SMT130 | 27.D5
UA1200:J2-2 | SC | FU0213 | WHT | 20 | 27.B1 | XT0233:4 | PNL B,SMT130 | 27.D5
XT0060:1 | SC | 0V | WHT | 14 | 21.D1 | XT0235:1 | PNL B,SMT130 | 19.D5
XT0070:1 | SC | 0V | WHT | 14 | 21.B1 | XT0070:2 | PNL B,SMT130 | 21.B1
XT0110:3 | SC | 0V | WHT | 16 | 26.A4 | XT0235:2 | PNL B,SMT130 | 19.D5
XT0235:1 | SC | 0V | WHT | 14 | 19.D5 | XT0070:1 | PNL B,SMT130 | 21.B1
XT0235:2 | SC | 0V | WHT | 16 | 19.D5 | XT0235:4 | PNL B,SMT130 | 27.D5
XT0235:6 | SC | 0V | WHT | 20 | 28.A5 | XT0235:8 | PNL B,SMT130 | 28.A6
XT0240:16 | SC | SB751221 | WHT | 20 | 134.A5 | XT0240:1 | PNL B,SMT130 | 24.A3
XT0240:17 | SC | SB851221 | WHT | 20 | 134.A5 | XT0240:2 | PNL B,SMT130 | 24.A3
XT0240:20 | SC | SB951222 | WHT | 20 | 47.A5 | XT0240:3 | PNL B,SMT130 | 24.A3
XT0240:21 | SC | ESTOP | WHT | 20 | 47.A5 | XT0240:5 | PNL B,SMT130 | 24.B3
XT0240:31 | SC | LON0A | WHT | 20 | 127.A5 | XT0240:28 | PNL B,SMT130 | 126.D6
XT0240:32 | SC | LON0B | WHT | 20 | 127.A5 | XT0240:29 | PNL B,SMT130 | 126.D6
XT0240:33 | SC | LON0S1 | WHT | 20 | 127.A5 | XT0240:30 | PNL B,SMT130 | 126.D6
XT0240:5 | SC | ESTOP | WHT | 20 | 24.B3 | XT0240:4 | PNL B,SMT130 | 24.A3
AF0410:L1 | WC0006 | AU0060L2 | ENET | CABLE | 2.A2 | AU0060:L2 | PNL B,SMT130 | 2.A5
AU0060:L1 | WC0007 | AU0070L2 | ENET | CABLE | 2.A5 | AU0070:L2 | PNL B,SMT130 | 2.A4
AF0410:L2 | WC0041 | AF0410L2 | ENET | CABLE | 2.A2 | AF0420:L1 | PNL B,SMT130 | 2.A3
AF0420:L2 | WC0042 | AF0420L2 | ENET | CABLE | 2.A3 | AF0450:L1 | PNL B,SMT130 | 2.A4
AF0067:12 | WC4524 | UA1200J13 | RED | 20 | 27.B7 | UA1200:J1-3 | PNL B,SMT130 | 27.B1
AF0067:28 | WC4524 | UA1200J11 | BLK | 20 | 27.B7 | UA1200:J1-1 | PNL B,SMT130 | 27.B1
AF0067:60 | WC4524 | UA1200S | SH | 20 | 27.B7 | FLOATING | PNL B,SMT130 | 27.B2
AF0400:LBUS | WC8040 | AF0410RBUS | BUS | CABLE | 26.B6 | AF0410:RBUS | PNL B,SMT130 | 26.B5
AF0410:LBUS | WC8041 | AF0420RBUS | BUS | CABLE | 26.B5 | AF0420:RBUS | PNL B,SMT130 | 26.B4
AF0420:LBUS | WC8042 | AF0420LBUS | BUS | CABLE | 26.B4 | AF0450:RBUS | PNL B,SMT130 | 26.B3
AF0063:06 | SC | 006306 | WHT | 20 | 65.C7 | KA0222:14 | PNL A,SMT130 | 65.C6
AF0075:03 | SC | KA0221A1 | WHT | 20 | 65.B7 | KA0221:A1 | PNL A,SMT130 | 65.B6
AF0075:04 | SC | KA0222A1 | WHT | 20 | 65.C7 | KA0222:A1 | PNL A,SMT130 | 65.C6
AF0075:08 | SC | KT014615 | WHT | 20 | 24.D7 | KT0146:15 | PNL A,SMT130 | 24.D6
AF0075:09 | SC | KT0146B1 | WHT | 20 | 23.C2 | KT0146:B1 | PNL A,SMT130 | 23.C2
AF0075:19 | SC | KA0221A2 | WHT | 20 | 65.B7 | KA0221:A2 | PNL A,SMT130 | 65.B6
AF0075:20 | SC | KA0222A2 | WHT | 20 | 65.C7 | KA0222:A2 | PNL A,SMT130 | 65.C6
AF0075:25 | SC | KT0146A2 | WHT | 20 | 23.C2 | KT0146:A2 | PNL A,SMT130 | 23.C2
FU0210:LI | SC | FU0136 | WHT | 12 | 19.C5 | XT0138:4 | PNL A,SMT130 | 19.B4
IEG0230:3 | SC | IEG02303 | GRN | 14 | 22.A4 | GR0111: | PNL A,SMT130 | 22.A4
IEG0230:4 | SC | IEG02304 | GRN | 14 | 20.D6 | AF0086:SH | PNL A,SMT130 | 20.D5
IEG0230:5 | SC | IEG02305 | GRN | 14 | 20.B1 | AU0090:GND | PNL A,SMT130 | 20.A2
IEG0230:7 | SC | IEG02307 | GRN | 14 | 22.A4 | GR0134: | PNL A,SMT130 | 22.A4
KA0231:14 | SC | KA024214 | WHT | 20 | 24.C6 | KT0146:18 | PNL A,SMT130 | 24.D6
KA0232:11 | SC | KA017814 | WHT | 20 | 28.A6 | KA0178:14 | PNL A,SMT130 | 28.A5
KA0232:12 | SC | FU0136 | WHT | 20 | 28.A6 | KA0875:14 | PNL A,SMT130 | 28.A6
KA0232:21 | SC | KA013522 | WHT | 20 | 142.A6 | KA0135:22 | PNL A,SMT130 | 142.A6
KA0232:22 | SC | FU0136 | WHT | 14 | 142.A6 | XT0138:4 | PNL A,SMT130 | 19.B4
KA0238:14 | SC | KA023814 | WHT | 20 | 65.B5 | KA0221:11 | PNL A,SMT130 | 65.B6
KA0238:24 | SC | KA023824 | WHT | 20 | 65.C5 | KA0222:11 | PNL A,SMT130 | 65.C6
KA0239:21 | SC | KA023921 | WHT | 20 | 24.B6 | AF0093:39 | PNL A,SMT130 | 24.A7
KA0239:24 | SC | KA023924 | WHT | 20 | 24.B6 | AF0093:07 | PNL A,SMT130 | 24.A7
KA0240:11 | SC | PS32004 | WHT | 20 | 86.D5 | XT0136:6 | PNL A,SMT130 | 86.D5
KA0240:14 | SC | UF1300P | WHT | 20 | 86.D5 | XT0136:7 | PNL A,SMT130 | 86.D6
KA0241:11 | SC | UA1200J21 | WHT | 20 | 24.A5 | AF0093:00 | PNL A,SMT130 | 24.A7
KA0241:21 | SC | KT0146A1 | WHT | 20 | 23.B2 | KA0141:21 | PNL A,SMT130 | 23.B2
KA0241:24 | SC | FU0139 | WHT | 20 | 23.B2 | KA0141:24 | PNL A,SMT130 | 23.B2
KA0242:11 | SC | KA0231A1 | WHT | 20 | 24.C6 | XT0136:12 | PNL A,SMT130 | 23.B5
KA0242:14 | SC | KA024214 | WHT | 20 | 24.C6 | AF0093:12 | PNL A,SMT130 | 24.C7
KA0243:11 | SC | KA024311 | WHT | 20 | 24.B6 | AF0093:34 | PNL A,SMT130 | 24.B7
KA0243:14 | SC | KA024314 | WHT | 20 | 24.B6 | AF0093:02 | PNL A,SMT130 | 24.B7
KA0244:12 | SC | KA024412 | WHT | 14 | 24.D4 | KT0145:A1 | PNL A,SMT130 | 23.B6
KA0245:21 | SC | KA024521 | WHT | 20 | 24.B6 | AF0093:35 | PNL A,SMT130 | 24.B7
KA0245:24 | SC | KA024524 | WHT | 20 | 24.B6 | AF0093:03 | PNL A,SMT130 | 24.B7
KA0246:11 | SC | KA024611 | WHT | 20 | 142.B5 | XT0137:1 | PNL A,SMT130 | 142.B5
KA0246:14 | SC | KA6211A1 | WHT | 20 | 142.B5 | KA6211:A1 | PNL A,SMT130 | 142.B6
KA0246:21 | SC | KA024621 | WHT | 20 | 144.A5 | XT0137:5 | PNL A,SMT130 | 144.A5
KA0246:24 | SC | KA6221A1 | WHT | 20 | 144.A5 | KA6221:A1 | PNL A,SMT130 | 144.A6
KA0247:11 | SC | KA024711 | WHT | 20 | 143.A5 | XT0137:3 | PNL A,SMT130 | 143.A5
KA0247:14 | SC | KA6212A1 | WHT | 20 | 143.A5 | KA6212:A1 | PNL A,SMT130 | 143.A6
KA0247:21 | SC | KA024721 | WHT | 20 | 145.A5 | XT0137:7 | PNL A,SMT130 | 145.A5
KA0247:24 | SC | KA6222A1 | WHT | 20 | 145.A5 | KA6222:A1 | PNL A,SMT130 | 145.A6
KA0249:11 | SC | KA013521 | WHT | 20 | 142.A6 | KA0135:21 | PNL A,SMT130 | 142.A6
KA0260:11 | SC | KA026011 | WHT | 20 | 24.C6 | AF0093:37 | PNL A,SMT130 | 24.C7
KA0260:14 | SC | KA026014 | WHT | 20 | 24.C6 | AF0093:05 | PNL A,SMT130 | 24.C7
UA1200:J2-6 | SC | UA1200J26 | WHT | 20 | 27.B1 | KA0130:A2 | PNL A,SMT130 | 27.C5
UA1200:J2-7 | SC | UA1200J27 | WHT | 20 | 27.B1 | AF0093:22 | PNL A,SMT130 | 27.C7
XT0060:4 | SC | SV21202 | WHT | 16 | 65.B5 | AF0081:20 | PNL A,SMT130 | 65.B7
XT0235:1 | SC | 0V | WHT | 14 | 19.D5 | XT0134:4 | PNL A,SMT130 | 19.C4
XT0235:5 | SC | HA0472BLK-2 | WHT | 20 | 28.A5 | KA0875:11 | PNL A,SMT130 | 28.A6
XT0235:7 | SC | FU0136 | WHT | 14 | 28.A6 | XT0138:2 | PNL A,SMT130 | 19.A4
XT0235:7 | SC | FU0136 | WHT | 20 | 28.A6 | KA0875:14 | PNL A,SMT130 | 28.A6
XT0235:8 | SC | 0V | WHT | 14 | 28.A6 | XT0134:2 | PNL A,SMT130 | 19.C4
XT0240:10 | SC | 0V | WHT | 20 | 24.D3 | XT0136:3 | PNL A,SMT130 | 23.A2
XT0240:12 | SC | FU0139 | WHT | 14 | 24.C4 | XT0136:1 | PNL A,SMT130 | 23.A2
XT0240:14 | SC | SB751211 | WHT | 16 | 134.A5 | AF0093:43 | PNL A,SMT130 | 134.A7
XT0240:15 | SC | SB751212 | WHT | 16 | 134.A5 | AF0093:11 | PNL A,SMT130 | 134.A7
XT0240:18 | SC | SB047311 | WHT | 20 | 47.A5 | AF0093:42 | PNL A,SMT130 | 47.A6
XT0240:19 | SC | SB047312 | WHT | 20 | 47.A5 | AF0093:10 | PNL A,SMT130 | 47.A6
XT0240:22 | SC | KA0178A1 | WHT | 20 | 28.D4 | KA0178:A1 | PNL A,SMT130 | 28.D3
XT0240:23 | SC | 017824 | WHT | 20 | 28.D4 | KA0178:A2 | PNL A,SMT130 | 28.D3
XT0240:24 | SC | HL62002 | WHT | 20 | 47.B5 | AF0092:15 | PNL A,SMT130 | 47.B6
XT0240:25 | SC | HL62001 | WHT | 20 | 47.B5 | AF0092:31 | PNL A,SMT130 | 47.B6
XT0240:26 | SC | SB6200NO | WHT | 20 | 47.B5 | AF0091:47 | PNL A,SMT130 | 47.B6
XT0240:27 | SC | SB6200C | WHT | 20 | 47.B5 | AF0091:15 | PNL A,SMT130 | 47.B6
AU0070:L1 | WC0008 | AU0080L2 | ENET | CABLE | 2.A4 | AU0080:L2 | PNL A,SMT130 | 2.A3
XT0235:5 | WC5072 | HA0472BLK-2 | BLK | 16 | 28.A5 | HA0472:BLK-2 | TURBINE CONTROL^JB70 | 28.A1
XT0235:6 | WC5072 | 0V | WHT | 16 | 28.A5 | HA0472:BLK-1 | TURBINE CONTROL^JB70 | 28.A1
SolarTools ver. 24.0.84.24712 (Jul 31, 2025)
Report date: 2/3/2026 11:55 AM

## PNL,DOOR,2-BAY
PNL,DOOR,2-BAY
Project # | 4L321
Project Name | Enterprise SMT130 M4 WTX
Revision | 0.1
Controls DE
Phone:
Controls ME
Phone:
From | [5 empty] | To
Device ID | Cable (W) Conductor (SC) Jumper Clip (JC) | Wire No. | Wire ID | Gauge/Size | Page/Zone | Device ID | Location | Page/Zone
AT0190:GND | SC | AT0190G | GRN/YEL | 14 | 35.C4 | FRAME | PNL,DOOR,2-BAY | 35.C3
AT0190:USB | SC | AT0190K | CABLE | USB | 35.C4 | AT0190K:KI | PNL,DOOR,2-BAY | 35.C5
KA0461:11 | SC | KA046111 | WHT | 20 | 40.D3 | XT0460:8 | GEN CMPNT | 40.D5
KA0461:13 | SC | KA046113 | WHT | 20 | 40.D3 | XT0460:7 | GEN CMPNT | 40.D5
KA0461:14 | SC | FU0460 | WHT | 14 | 40.D3 | XT0460:2 | GEN CMPNT | 40.C3
KA0461:16 | SC | KA0333A1 | WHT | 20 | 40.D3 | XT0460:5 | GEN CMPNT | 40.D3
KA0461:16 | SC | KA0333A1 | WHT | 20 | 40.D3 | XT0337:12 | GEN CMPNT | 130.B3
KA0461:B | SC | 0V | WHT | 14 | 40.D3 | XT0460:6 | GEN CMPNT | 40.D5
KA0461:G | SC | KA046032 | WHT | 14 | 40.D3 | XT0460:4 | GEN CMPNT | 40.C3
AT0190:ENET2 | WC0019 | AT0190ENET2 | ENET | CABLE | 35.C4 | BA0703:LAN | POWERDIST, PANEL | 35.C6
AT0190:ENET1 | WC7024 | AT0190ENET1 | ENET | CABLE | 35.C4 | BA0700:1 | POWERDIST, PANEL | 5.A3
AT0190:NEG | SC | 0V | WHT | 14 | 35.C4 | XT0562:4 | PWR DST,DR,SMT130 | 35.C2
AT0190:POS | SC | FU0190 | WHT | 14 | 35.C4 | FU0190:LD | PWR DST,DR,SMT130 | 35.C3
SB6500:11 | SC | FU0560 | WHT | 16 | 39.A2 | XT2930:1 | PWR DST,DR,SMT130 | 39.A6
SB6500:12 | SC | SB650012 | WHT | 16 | 39.A2 | XT2930:2 | PWR DST,DR,SMT130 | 39.A6
HA0273:(+) | WC5540 | HA0273P | BLK | 16 | 37.D4 | AF0202:23 | TCP, SMT130 | 37.D6
HA0273:(-) | WC5540 | HA0273N | WHT | 16 | 37.D4 | AF0202:55 | TCP, SMT130 | 37.D6
SolarTools ver. 24.0.84.24712 (Jul 31, 2025)
Report date: 2/3/2026 11:55 AM

## POWERDIST, PANEL
POWERDIST, PANEL
Project # | 4L321
Project Name | Enterprise SMT130 M4 WTX
Revision | 0.1
Controls DE
Phone:
Controls ME
Phone:
From | [5 empty] | To
Device ID | Cable (W) Conductor (SC) Jumper Clip (JC) | Wire No. | Wire ID | Gauge/Size | Page/Zone | Device ID | Location | Page/Zone
XT0102:1 | JC | FU0136 | CLIP | --- | 19.A2 | XT0102:2 | POWERDIST, PANEL | 19.A2
XT0102:2 | JC | FU0136 | CLIP | --- | 19.A2 | XT0102:3 | POWERDIST, PANEL | 19.B2
XT0102:3 | JC | FU0136 | CLIP | --- | 19.B2 | XT0102:4 | POWERDIST, PANEL | 19.B2
XT0102:4 | JC | FU0136 | CLIP | --- | 19.B2 | XT0102:5 | POWERDIST, PANEL | 19.B2
XT0102:5 | JC | FU0136 | CLIP | --- | 19.B2 | XT0102:6 | POWERDIST, PANEL | 19.B2
XT0104:1 | JC | 0V | CLIP | --- | 19.B2 | XT0104:2 | POWERDIST, PANEL | 19.C2
XT0104:2 | JC | 0V | CLIP | --- | 19.C2 | XT0104:3 | POWERDIST, PANEL | 19.C2
XT0104:3 | JC | 0V | CLIP | --- | 19.C2 | XT0104:4 | POWERDIST, PANEL | 19.C2
XT0104:4 | JC | 0V | CLIP | --- | 19.C2 | XT0104:5 | POWERDIST, PANEL | 19.C2
XT0104:5 | JC | 0V | CLIP | --- | 19.C2 | XT0104:6 | POWERDIST, PANEL | 19.C2
XT0104:6 | JC | 0V | CLIP | --- | 19.C2 | XT0104:7 | POWERDIST, PANEL | 19.C2
BA0700:V1(-) | SC | 0V | WHT | 16 | 5.A3 | XT0027:1 | POWERDIST, PANEL | 5.A4
BA0700:V1(+) | SC | FU2700 | WHT | 16 | 5.A3 | FU2700:LD | POWERDIST, PANEL | 5.A4
BA0701:0V | SC | 0V | WHT | 16 | 5.B5 | XT0027:2 | POWERDIST, PANEL | 5.B5
BA0701:24V | SC | FU2701 | WHT | 16 | 5.B5 | FU2701:LD | POWERDIST, PANEL | 5.B5
BA0703:V1- | SC | 0V | WHT | 16 | 35.C6 | XT0027:3 | POWERDIST, PANEL | 35.C5
BA0703:V1+ | SC | FU2703 | WHT | 16 | 35.C6 | FU2703:LD | POWERDIST, PANEL | 35.C5
FU0010:LI | SC | FU0136 | WHT | 14 | 19.B2 | XT0102:3 | POWERDIST, PANEL | 19.B2
FU0011:LD | SC | UJ0131P | WHT | 12 | 18.B3 | UJ0131:+ | POWERDIST, PANEL | 18.B4
FU0136:LD | SC | FU0136 | WHT | 10 | 19.A1 | XT0102:1 | POWERDIST, PANEL | 19.A2
FU0136:LI | SC | 24V | WHT | 10 | 19.A1 | UJ0131:OUT(+) | POWERDIST, PANEL | 18.B4
FU0460:LI | SC | FU0136 | WHT | 14 | 40.C2 | XT0102:6 | POWERDIST, PANEL | 19.B2
FU0500:LI | SC | FU0136 | WHT | 14 | 19.A2 | XT0102:2 | POWERDIST, PANEL | 19.A2
FU2700:LI | SC | FU0136 | WHT | 14 | 5.A4 | XT0102:6 | POWERDIST, PANEL | 19.B2
FU2701:LI | SC | FU0136 | WHT | 14 | 5.B5 | XT0102:5 | POWERDIST, PANEL | 19.B2
FU2703:LI | SC | FU0136 | WHT | 14 | 35.C5 | XT0102:3 | POWERDIST, PANEL | 19.B2
GR0144: | SC | GR0144 | GRN/YEL | 14 | 17.A4 | FRAME | POWERDIST, PANEL | 17.A4
GR0145: | SC | GR0145 | GRN/YEL | 14 | 17.A4 | FRAME | POWERDIST, PANEL | 17.A4
GR0146: | SC | GR0146 | GRN | 14 | 17.A4 | IEG2240:2 | POWERDIST, PANEL | 17.A4
UJ0131:- | SC | 521NEG | WHT | 12 | 18.B4 | XT0011:1 | POWERDIST, PANEL | 18.B3
UJ0131:G | SC | UJ0131G | GRN/YEL | 12 | 18.B4 | FRAME | POWERDIST, PANEL | 18.B4
UJ0131:OUT(-) | SC | 0V | WHT | 10 | 18.B4 | XT0104:1 | POWERDIST, PANEL | 19.B2
XT0104:3 | SC | 0V | WHT | 14 | 19.C2 | XT0027:3 | POWERDIST, PANEL | 35.C5
XT0104:4 | SC | 0V | WHT | 14 | 19.C2 | XT0027:1 | POWERDIST, PANEL | 5.A4
XT0104:7 | SC | 0V | WHT | 14 | 19.C2 | XT0027:2 | POWERDIST, PANEL | 5.B5
BA0700:7 | WC0701 | BA07007 | ENET | CABLE | 5.A3 | CCENET1:1 | JB774 | 5.C7
BA0700:8 | WC0702 | BA07008 | ENET | CABLE | 5.A3 | CCENET2:1 | JB774 | 5.D7
BA0700:6 | WC0703 | BA07006 | ENET | CABLE | 5.A3 | CCENET3:1 | JB774 | 5.D7
XT0104:6 | SC | 0V | WHT | 14 | 19.C2 | KA0460:63 | BECKWITH RELAY,SMT130 | 40.A3
FU0500:LD | SC | FU0500 | WHT | 14 | 19.A2 | XT0510:1 | FG&E CTRL,SMT130 | 33.A5
IEG2240:13 | SC | IEG224013 | GRN | 8 | 17.C2 | IEG0356:0 | FG&E CTRL,SMT130 | 17.C2
XT0102:5 | SC | FU0136 | WHT | 14 | 19.B2 | FU0170:LI | FG&E CTRL,SMT130 | 34.A2
XT0104:2 | SC | 0V | WHT | 14 | 19.C2 | XT0510:3 | FG&E CTRL,SMT130 | 33.A5
XT0104:4 | SC | 0V | WHT | 14 | 19.C2 | XT0170:3 | FG&E CTRL,SMT130 | 34.A2
FU0460:LD | SC | FU0460 | WHT | 14 | 40.C2 | XT0460:1 | GEN CMPNT | 40.C3
IEG2240:14 | SC | IEG224014 | GRN | 8 | 17.B2 | IEG0140:0 | GEN CMPNT | 17.B2
XT0102:4 | SC | FU0136 | WHT | 14 | 19.B2 | XT0332:1 | GEN CMPNT | 29.B2
XT0104:5 | SC | 0V | WHT | 14 | 19.C2 | XT0334:1 | GEN CMPNT | 29.C2
XT0104:6 | SC | 0V | WHT | 14 | 19.C2 | XT0460:6 | GEN CMPNT | 40.D5
IEG2240:1 | SC | GR0290 | GRN | 14 | 17.A4 | GR0290: | MCC PNL,SMT130 | 17.A4
IEG2240:3 | SC | IEG22403 | GRN | 14 | 41.B6 | AF0295:SH | MCC PNL,SMT130 | 41.A5
UJ0131:IOUT | SC | UJ0131IOUT | WHT | 20 | 18.B4 | AF0293:02 | MCC PNL,SMT130 | 18.A7
UJ0131:OK1 | SC | UJ0131OK1 | WHT | 20 | 18.B4 | AF0292:32 | MCC PNL,SMT130 | 18.B7
UJ0131:OK2 | SC | UJ0131OK2 | WHT | 20 | 18.B4 | AF0292:00 | MCC PNL,SMT130 | 18.B7
UJ0131:VIN | SC | UJ0131VIN | WHT | 20 | 18.B4 | AF0293:00 | MCC PNL,SMT130 | 18.A7
XT0104:7 | SC | 0V | GRN/YEL | 8 | 19.C2 | PEG2240:1 | MCC PNL,SMT130 | 19.C1
FU0010:LD | SC | FU0010 | WHT | 14 | 19.B2 | UV0600:(+) | PLC, PANEL | 4.B2
XT0104:3 | SC | 0V | WHT | 14 | 19.C2 | UV0600:(-) | PLC, PANEL | 4.B2
BA0701:ENET | WC7028 | BA0701ENET | ENET | CABLE | 5.B5 | AP0607:L2 | PLC, PANEL | 4.A5
BA0700:2 | WC7071 | AP0607L1 | ENET | CABLE | 5.A3 | AP0607:L1 | PLC, PANEL | 4.A5
BA0703:LAN | WC0019 | AT0190ENET2 | ENET | CABLE | 35.C6 | AT0190:ENET2 | PNL,DOOR,2-BAY | 35.C4
BA0700:1 | WC7024 | AT0190ENET1 | ENET | CABLE | 5.A3 | AT0190:ENET1 | PNL,DOOR,2-BAY | 35.C4
XT0102:4 | SC | FU0136 | WHT | 12 | 19.B2 | FU0560:LI | PWR DST,DR,SMT130 | 35.A2
XT0104:5 | SC | 0V | WHT | 14 | 19.C2 | XT0562:1 | PWR DST,DR,SMT130 | 35.B2
IEG2240:4 | SC | IEG22404 | GRN | 14 | 35.A3 | GR0200: | TCP, SMT130 | 35.A3
IEG2240:5 | SC | AU0200G | GRN | 14 | 35.B5 | AU0200:GND | TCP, SMT130 | 35.A4
SolarTools ver. 24.0.84.24712 (Jul 31, 2025)
Report date: 2/3/2026 11:55 AM

## PROX,TURB
PROX,TURB
Project # | 4L321
Project Name | Enterprise SMT130 M4 WTX
Revision | 0.1
Controls DE
Phone:
Controls ME
Phone:
From | [5 empty] | To
Device ID | Cable (W) Conductor (SC) Jumper Clip (JC) | Wire No. | Wire ID | Gauge/Size | Page/Zone | Device ID | Location | Page/Zone
GR1210: | SC | GR1210 | GRN/YEL | 14 | 22.A6 | FRAME | PROX,TURB | 22.A6
GR1211: | SC | GR1211 | GRN/YEL | 14 | 22.A6 | FRAME | PROX,TURB | 22.A6
SolarTools ver. 24.0.84.24712 (Jul 31, 2025)
Report date: 2/3/2026 11:55 AM

## PWR DST,DR,SMT130
PWR DST,DR,SMT130
Project # | 4L321
Project Name | Enterprise SMT130 M4 WTX
Revision | 0.1
Controls DE
Phone:
Controls ME
Phone:
From | [5 empty] | To
Device ID | Cable (W) Conductor (SC) Jumper Clip (JC) | Wire No. | Wire ID | Gauge/Size | Page/Zone | Device ID | Location | Page/Zone
XT0561:1 | JC | FU0560 | CLIP | --- | 35.A3 | XT0561:2 | PWR DST,DR,SMT130 | 35.B3
XT0562:2 | JC | 0V | CLIP | --- | 35.B2 | XT0562:3 | PWR DST,DR,SMT130 | 35.B2
XT0562:3 | JC | 0V | CLIP | --- | 35.B2 | XT0562:4 | PWR DST,DR,SMT130 | 35.C2
XT2930:3 | JC | SB650012 | CLIP | --- | 111.B5 | XT2930:4 | PWR DST,DR,SMT130 | 111.B5
XT2930:5 | JC | 0V | CLIP | --- | 111.C5 | XT2930:6 | PWR DST,DR,SMT130 | 111.C5
FU0190:LI | SC | FU0560 | WHT | 14 | 35.C3 | FU0701:LI | PWR DST,DR,SMT130 | 35.D3
FU0190:LI | SC | FU0560 | WHT | 14 | 35.C3 | FU0273:LI | PWR DST,DR,SMT130 | 35.B3
FU0200:LI | SC | FU0560 | WHT | 14 | 35.A3 | XT0561:1 | PWR DST,DR,SMT130 | 35.A3
FU0201:LI | SC | FU0560 | WHT | 14 | 35.B3 | FU0273:LI | PWR DST,DR,SMT130 | 35.B3
FU0201:LI | SC | FU0560 | WHT | 14 | 35.B3 | XT0561:1 | PWR DST,DR,SMT130 | 35.A3
FU0560:LD | SC | FU0560 | WHT | 14 | 35.A2 | XT0561:1 | PWR DST,DR,SMT130 | 35.A3
FU2610:LI | SC | SB650012 | WHT | 16 | 111.B4 | XT2930:3 | PWR DST,DR,SMT130 | 111.B5
FU2620:LI | SC | SB650012 | WHT | 16 | 111.B4 | XT2930:4 | PWR DST,DR,SMT130 | 111.B5
XT0562:1 | SC | 0V | WHT | 20 | 35.B2 | XT0562:2 | PWR DST,DR,SMT130 | 35.B2
XT2930:1 | SC | FU0560 | WHT | 14 | 39.A6 | XT0561:2 | PWR DST,DR,SMT130 | 35.B3
XT2930:3 | SC | SB650012 | WHT | 14 | 111.B5 | XT2930:2 | PWR DST,DR,SMT130 | 39.A6
XT2930:5 | SC | 0V | WHT | 14 | 111.C5 | XT0562:3 | PWR DST,DR,SMT130 | 35.B2
FU0273:LD | SC | FU0273 | WHT | 16 | 35.B3 | EL0273:SW+ | CONTROL,2-BAY | 35.B4
XT0562:2 | SC | 0V | WHT | 16 | 35.B2 | EL0273:SW- | CONTROL,2-BAY | 35.B4
XT0561:2 | SC | FU0560 | WHT | 14 | 35.B3 | XT0295:1 | MCC PNL,SMT130 | 41.A3
XT0562:3 | SC | 0V | WHT | 20 | 35.B2 | XT0295:2 | MCC PNL,SMT130 | 41.A3
XT0563:1 | SC | SB851222 | WHT | 20 | 37.D6 | XT2920:4 | MCC PNL,SMT130 | 135.A5
XT0563:2 | SC | SB047212 | WHT | 20 | 37.D6 | XT0290:8 | MCC PNL,SMT130 | 45.A6
FU0190:LD | SC | FU0190 | WHT | 14 | 35.C3 | AT0190:POS | PNL,DOOR,2-BAY | 35.C4
XT0562:4 | SC | 0V | WHT | 14 | 35.C2 | AT0190:NEG | PNL,DOOR,2-BAY | 35.C4
XT2930:1 | SC | FU0560 | WHT | 16 | 39.A6 | SB6500:11 | PNL,DOOR,2-BAY | 39.A2
XT2930:2 | SC | SB650012 | WHT | 16 | 39.A6 | SB6500:12 | PNL,DOOR,2-BAY | 39.A2
FU0560:LI | SC | FU0136 | WHT | 12 | 35.A2 | XT0102:4 | POWERDIST, PANEL | 19.B2
XT0562:1 | SC | 0V | WHT | 14 | 35.B2 | XT0104:5 | POWERDIST, PANEL | 19.C2
FU0200:LD | SC | FU0200 | WHT | 16 | 35.A3 | AU0200:V+ | TCP, SMT130 | 35.A4
FU0201:LD | SC | FU0201 | WHT | 16 | 35.B3 | AF0202:V+ | TCP, SMT130 | 35.A6
XT0562:2 | SC | 0V | WHT | 16 | 35.B2 | AU0200:COM | TCP, SMT130 | 35.A4
XT0562:3 | SC | 0V | WHT | 16 | 35.B2 | AF0202:COM | TCP, SMT130 | 35.A6
XT0562:4 | SC | 0V | WHT | 20 | 35.C2 | SH0400:B | TCP, SMT130 | 37.B5
XT0563:1 | SC | SB851222 | WHT | 20 | 37.D6 | SB0400:B1-11 | TCP, SMT130 | 37.D5
XT0563:2 | SC | SB047212 | WHT | 20 | 37.D6 | SB0400:B1-12 | TCP, SMT130 | 37.D5
XT0563:3 | SC | KA023612 | WHT | 20 | 37.B6 | XT0564:1 B2 | TCP, SMT130 | 37.B5
XT0563:4 | SC | 0V | WHT | 20 | 37.B6 | HL0410:A | TCP, SMT130 | 37.B5
XT0563:5 | SC | KA0241A1 | WHT | 20 | 37.C6 | SA0401:1 | TCP, SMT130 | 37.C5
XT0563:6 | SC | FU0139 | WHT | 20 | 37.C6 | SA0401:2 | TCP, SMT130 | 37.C5
SolarTools ver. 24.0.84.24712 (Jul 31, 2025)
Report date: 2/3/2026 11:55 AM

## TCP, SMT130
TCP, SMT130
Project # | 4L321
Project Name | Enterprise SMT130 M4 WTX
Revision | 0.1
Controls DE
Phone:
Controls ME
Phone:
From | [5 empty] | To
Device ID | Cable (W) Conductor (SC) Jumper Clip (JC) | Wire No. | Wire ID | Gauge/Size | Page/Zone | Device ID | Location | Page/Zone
AF0201:00 | SC | TCP13NO | WHT | 20 | 37.A3 | SH0400:NO | TCP, SMT130 | 37.A1
AF0201:01 | SC | TCP14NO | WHT | 20 | 37.A3 | SH0401:NO | TCP, SMT130 | 37.A1
AF0201:02 | SC | TCP15NO | WHT | 20 | 37.B3 | SH0409:NO | TCP, SMT130 | 37.B1
AF0201:03 | SC | TCP16NO | WHT | 20 | 37.B3 | SH0410:NO | TCP, SMT130 | 37.B1
AF0201:04 | SC | TCP17A2 | WHT | 20 | 37.C3 | SA0400:B2-14 | TCP, SMT130 | 37.C1
AF0201:05 | SC | TCP17B2 | WHT | 20 | 37.C3 | SA0400:B1-12 | TCP, SMT130 | 37.C1
AF0201:08 | SC | TCP23NC | WHT | 20 | 37.D3 | SB0401:NC | TCP, SMT130 | 37.D1
AF0201:09 | SC | TCP24NO | WHT | 20 | 37.D3 | SB0402:NO | TCP, SMT130 | 37.D1
AF0201:10 | SC | TCP25NO | WHT | 20 | 37.A7 | SB0403:NO | TCP, SMT130 | 37.A5
AF0201:11 | SC | TCP26NO | WHT | 20 | 37.A7 | SB0404:NO | TCP, SMT130 | 37.A5
AF0201:12 | SC | TCP29NO | WHT | 20 | 38.C3 | SB0405:NO | TCP, SMT130 | 38.C1
AF0201:13 | SC | TCP28NC | WHT | 20 | 38.D3 | SB0406:NC | TCP, SMT130 | 38.D1
AF0201:14 | SC | TCP31NO | WHT | 20 | 38.A6 | SB0407:NO | TCP, SMT130 | 38.A5
AF0201:15 | SC | TCP32NO | WHT | 20 | 38.A6 | SB0408:NO | TCP, SMT130 | 38.A5
AF0201:16 | SC | TCP30NO | WHT | 20 | 38.D3 | SH0408:NO | TCP, SMT130 | 38.D1
AF0201:17 | SC | TCP19NO | WHT | 20 | 38.A3 | SH0404:NO | TCP, SMT130 | 38.A1
AF0201:18 | SC | TCP20NO | WHT | 20 | 38.B3 | SH0405:NO | TCP, SMT130 | 38.B1
AF0201:19 | SC | TCP21NO | WHT | 20 | 38.B3 | SH0411:NO | TCP, SMT130 | 38.B1
AF0201:20 | SC | TCP22NO | WHT | 20 | 38.C3 | SH0412:NO | TCP, SMT130 | 38.C1
AF0201:32 | SC | TCP13C | WHT | 20 | 37.A3 | SH0400:C | TCP, SMT130 | 37.A1
AF0201:33 | SC | TCP14C | WHT | 20 | 37.A3 | SH0401:C | TCP, SMT130 | 37.A1
AF0201:34 | SC | TCP15C | WHT | 20 | 37.B3 | SH0409:C | TCP, SMT130 | 37.B1
AF0201:35 | SC | TCP16C | WHT | 20 | 37.B3 | SH0410:C | TCP, SMT130 | 37.B1
AF0201:36 | SC | TCP17A1 | WHT | 20 | 37.C3 | SA0400:B2-13 | TCP, SMT130 | 37.C1
AF0201:37 | SC | TCP17B1 | WHT | 20 | 37.C3 | SA0400:B1-11 | TCP, SMT130 | 37.C1
AF0201:40 | SC | TCP23C | WHT | 20 | 37.D3 | SB0401:C | TCP, SMT130 | 37.D1
AF0201:41 | SC | TCP24C | WHT | 20 | 37.D3 | SB0402:C | TCP, SMT130 | 37.D1
AF0201:42 | SC | TCP25C | WHT | 20 | 37.A7 | SB0403:C | TCP, SMT130 | 37.A5
AF0201:43 | SC | TCP26C | WHT | 20 | 37.A7 | SB0404:C | TCP, SMT130 | 37.A5
AF0201:44 | SC | TCP29C | WHT | 20 | 38.C3 | SB0405:C | TCP, SMT130 | 38.C1
AF0201:45 | SC | TCP28C | WHT | 20 | 38.D3 | SB0406:C | TCP, SMT130 | 38.D1
AF0201:46 | SC | TCP31C | WHT | 20 | 38.A6 | SB0407:C | TCP, SMT130 | 38.A5
AF0201:47 | SC | TCP32C | WHT | 20 | 38.A6 | SB0408:C | TCP, SMT130 | 38.A5
AF0201:48 | SC | TCP30C | WHT | 20 | 38.D3 | SH0408:C | TCP, SMT130 | 38.D1
AF0201:49 | SC | TCP19C | WHT | 20 | 38.A3 | SH0404:C | TCP, SMT130 | 38.A1
AF0201:50 | SC | TCP20C | WHT | 20 | 38.B3 | SH0405:C | TCP, SMT130 | 38.B1
AF0201:51 | SC | TCP21C | WHT | 20 | 38.B3 | SH0411:C | TCP, SMT130 | 38.B1
AF0201:52 | SC | TCP22C | WHT | 20 | 38.C3 | SH0412:C | TCP, SMT130 | 38.C1
AF0201:COM | SC | AU0200N | WHT | 16 | 35.A5 | AU0200:COM | TCP, SMT130 | 35.A4
AF0201:J | SC | * |  |  | 35.A5 | AF0202:P | TCP, SMT130 | 35.A6
AF0201:SHLD | SC | AF0201V+ | WHT | 16 | 35.D6 | AF0201:V+ | TCP, SMT130 | 35.D6
AF0201:V+ | SC | AU0200P | WHT | 16 | 35.A5 | AU0200:V+ | TCP, SMT130 | 35.A4
AF0202:00 | SC | TCP01AP | WHT | 20 | 36.A3 | HL0400:A+ | TCP, SMT130 | 36.A1
AF0202:01 | SC | TCP02AP | WHT | 20 | 36.A3 | HL0401:A+ | TCP, SMT130 | 36.A1
AF0202:02 | SC | TCP03AP | WHT | 20 | 36.B3 | HL0402:A+ | TCP, SMT130 | 36.B1
AF0202:03 | SC | TCP04AP | WHT | 20 | 36.B3 | HL0403:A+ | TCP, SMT130 | 36.B1
AF0202:04 | SC | TCP05AP | WHT | 20 | 36.C3 | HL0404:A+ | TCP, SMT130 | 36.C1
AF0202:05 | SC | TCP06AP | WHT | 20 | 36.C3 | HL0405:A+ | TCP, SMT130 | 36.C1
AF0202:06 | SC | TCP06BP | WHT | 20 | 36.D3 | HL0405:B+ | TCP, SMT130 | 36.D1
AF0202:08 | SC | TCP07AP | WHT | 20 | 36.D3 | HL0406:A+ | TCP, SMT130 | 36.D1
AF0202:09 | SC | TCP08AP | WHT | 20 | 36.A7 | HL0407:A+ | TCP, SMT130 | 36.A5
AF0202:10 | SC | TCP09AP | WHT | 20 | 36.A7 | HL0408:A+ | TCP, SMT130 | 36.A5
AF0202:11 | SC | TCP10AP | WHT | 20 | 36.B7 | HL0409:A+ | TCP, SMT130 | 36.B5
AF0202:12 | SC | TCP11AP | WHT | 20 | 36.B7 | HL0411:A+ | TCP, SMT130 | 36.B5
AF0202:13 | SC | TCP15AP | WHT | 20 | 36.C7 | SH0409:A+ | TCP, SMT130 | 36.C5
AF0202:14 | SC | TCP15BP | WHT | 20 | 36.C7 | SH0409:B+ | TCP, SMT130 | 36.C5
AF0202:15 | SC | TCP16AP | WHT | 20 | 36.D7 | SH0410:A+ | TCP, SMT130 | 36.D5
AF0202:16 | SC | TCP16BP | WHT | 20 | 36.D7 | SH0410:B+ | TCP, SMT130 | 36.D5
AF0202:17 | SC | TCP19AP | WHT | 20 | 38.B6 | SH0404:A+ | TCP, SMT130 | 38.B5
AF0202:18 | SC | TCP20AP | WHT | 20 | 38.B6 | SH0405:A+ | TCP, SMT130 | 38.B5
AF0202:19 | SC | TCP21AP | WHT | 20 | 38.C6 | SH0411:A+ | TCP, SMT130 | 38.C5
AF0202:20 | SC | TCP22AP | WHT | 20 | 38.C6 | SH0412:A+ | TCP, SMT130 | 38.C5
AF0202:21 | SC | TCP30AP | WHT | 20 | 38.D6 | SH0408:A+ | TCP, SMT130 | 38.D5
AF0202:22 | SC | TCP30BP | WHT | 20 | 38.D6 | SH0408:B+ | TCP, SMT130 | 38.D5
AF0202:32 | SC | TCP01A | WHT | 20 | 36.A3 | HL0400:A | TCP, SMT130 | 36.A1
AF0202:33 | SC | TCP02A | WHT | 20 | 36.A3 | HL0401:A | TCP, SMT130 | 36.A1
AF0202:34 | SC | TCP03A | WHT | 20 | 36.B3 | HL0402:A | TCP, SMT130 | 36.B1
AF0202:35 | SC | TCP04A | WHT | 20 | 36.B3 | HL0403:A | TCP, SMT130 | 36.B1
AF0202:36 | SC | TCP05A | WHT | 20 | 36.C3 | HL0404:A | TCP, SMT130 | 36.C1
AF0202:37 | SC | TCP06A | WHT | 20 | 36.C3 | HL0405:A | TCP, SMT130 | 36.C1
AF0202:38 | SC | TCP06B | WHT | 20 | 36.D3 | HL0405:B | TCP, SMT130 | 36.D1
AF0202:40 | SC | TCP07A | WHT | 20 | 36.D3 | HL0406:A | TCP, SMT130 | 36.D1
AF0202:41 | SC | TCP08A | WHT | 20 | 36.A7 | HL0407:A | TCP, SMT130 | 36.A5
AF0202:42 | SC | TCP09A | WHT | 20 | 36.A7 | HL0408:A | TCP, SMT130 | 36.A5
AF0202:43 | SC | TCP10A | WHT | 20 | 36.B7 | HL0409:A | TCP, SMT130 | 36.B5
AF0202:44 | SC | TCP11A | WHT | 20 | 36.B7 | HL0411:A | TCP, SMT130 | 36.B5
AF0202:45 | SC | TCP15A | WHT | 20 | 36.C7 | SH0409:A | TCP, SMT130 | 36.C5
AF0202:46 | SC | TCP15B | WHT | 20 | 36.C7 | SH0409:B | TCP, SMT130 | 36.C5
AF0202:47 | SC | TCP16A | WHT | 20 | 36.D7 | SH0410:A | TCP, SMT130 | 36.D5
AF0202:48 | SC | TCP16B | WHT | 20 | 36.D7 | SH0410:B | TCP, SMT130 | 36.D5
AF0202:49 | SC | TCP19A | WHT | 20 | 38.B6 | SH0404:A | TCP, SMT130 | 38.B5
AF0202:50 | SC | TCP20A | WHT | 20 | 38.B6 | SH0405:A | TCP, SMT130 | 38.B5
AF0202:51 | SC | TCP21A | WHT | 20 | 38.C6 | SH0411:A | TCP, SMT130 | 38.C5
AF0202:52 | SC | TCP22A | WHT | 20 | 38.C6 | SH0412:A | TCP, SMT130 | 38.C5
AF0202:53 | SC | TCP30A | WHT | 20 | 38.D6 | SH0408:A | TCP, SMT130 | 38.D5
AF0202:54 | SC | TCP30B | WHT | 20 | 38.D6 | SH0408:B | TCP, SMT130 | 38.D5
AF0202:COM | SC | AF0202COM | WHT | 16 | 35.D7 | AF0202:SHLD | TCP, SMT130 | 35.D7
HL0400:A | SC | TCP01A | WHT | 20 | 36.A1 | HL0400:B | TCP, SMT130 | 36.A1
HL0400:A+ | SC | TCP01AP | WHT | 20 | 36.A1 | HL0400:B+ | TCP, SMT130 | 36.A1
HL0401:A | SC | TCP02A | WHT | 20 | 36.A1 | HL0401:B | TCP, SMT130 | 36.A1
HL0401:A+ | SC | TCP02AP | WHT | 20 | 36.A1 | HL0401:B+ | TCP, SMT130 | 36.A1
HL0402:A | SC | TCP03A | WHT | 20 | 36.B1 | HL0402:B | TCP, SMT130 | 36.B1
HL0402:A+ | SC | TCP03AP | WHT | 20 | 36.B1 | HL0402:B+ | TCP, SMT130 | 36.B1
HL0403:A | SC | TCP04A | WHT | 20 | 36.B1 | HL0403:B | TCP, SMT130 | 36.B1
HL0403:A+ | SC | TCP04AP | WHT | 20 | 36.B1 | HL0403:B+ | TCP, SMT130 | 36.B1
HL0404:A | SC | TCP05A | WHT | 20 | 36.C1 | HL0404:B | TCP, SMT130 | 36.C1
HL0404:A+ | SC | TCP05AP | WHT | 20 | 36.C1 | HL0404:B+ | TCP, SMT130 | 36.C1
HL0406:A | SC | TCP07A | WHT | 20 | 36.D1 | HL0406:B | TCP, SMT130 | 36.D1
HL0406:A+ | SC | TCP07AP | WHT | 20 | 36.D1 | HL0406:B+ | TCP, SMT130 | 36.D1
HL0407:A | SC | TCP08A | WHT | 20 | 36.A5 | HL0407:B | TCP, SMT130 | 36.A5
HL0407:A+ | SC | TCP08AP | WHT | 20 | 36.A5 | HL0407:B+ | TCP, SMT130 | 36.A5
HL0408:A | SC | TCP09A | WHT | 20 | 36.A5 | HL0408:B | TCP, SMT130 | 36.A5
HL0408:A+ | SC | TCP09AP | WHT | 20 | 36.A5 | HL0408:B+ | TCP, SMT130 | 36.A5
HL0409:A | SC | TCP10A | WHT | 20 | 36.B5 | HL0409:B | TCP, SMT130 | 36.B5
HL0409:A+ | SC | TCP10AP | WHT | 20 | 36.B5 | HL0409:B+ | TCP, SMT130 | 36.B5
HL0410:A | SC | 0V | WHT | 20 | 37.B5 | HL0410:B | TCP, SMT130 | 37.B5
HL0410:A+ | SC | TCP12AP | WHT | 20 | 37.B5 | XT0564:1 B1 | TCP, SMT130 | 37.B5
HL0410:A+ | SC | TCP12AP | WHT | 20 | 37.B5 | HL0410:B+ | TCP, SMT130 | 37.B5
HL0411:A | SC | TCP11A | WHT | 20 | 36.B5 | HL0411:B | TCP, SMT130 | 36.B5
HL0411:A+ | SC | TCP11AP | WHT | 20 | 36.B5 | HL0411:B+ | TCP, SMT130 | 36.B5
SB0404:NO | SC | TCP26NO | WHT | 20 | 37.A5 | XT0564:1 T1 | TCP, SMT130 | 37.B5
SH0400:A | SC | 0V | WHT | 20 | 37.B5 | SH0401:A | TCP, SMT130 | 37.C5
SH0400:A | SC | 0V | WHT | 20 | 37.B5 | SH0400:B | TCP, SMT130 | 37.B5
SH0400:A+ | SC | TCP13AP | WHT | 20 | 37.B5 | XT0564:2 B1 | TCP, SMT130 | 37.B5
SH0400:B+ | SC | TCP13BP | WHT | 20 | 37.B5 | XT0564:3 B1 | TCP, SMT130 | 37.B5
SH0401:A | SC | 0V | WHT | 20 | 37.C5 | SH0401:B | TCP, SMT130 | 37.C5
SH0401:A+ | SC | TCP14AP | WHT | 20 | 37.C5 | XT0564:5 B1 | TCP, SMT130 | 37.C5
SH0401:B+ | SC | TCP14BP | WHT | 20 | 37.C5 | XT0564:4 B1 | TCP, SMT130 | 37.C5
SH0404:A | SC | TCP19A | WHT | 20 | 38.B5 | SH0404:B | TCP, SMT130 | 38.B5
SH0404:A+ | SC | TCP19AP | WHT | 20 | 38.B5 | SH0404:B+ | TCP, SMT130 | 38.B5
SH0405:A | SC | TCP20A | WHT | 20 | 38.B5 | SH0405:B | TCP, SMT130 | 38.B5
SH0405:A+ | SC | TCP20AP | WHT | 20 | 38.B5 | SH0405:B+ | TCP, SMT130 | 38.B5
SH0411:A | SC | TCP21A | WHT | 20 | 38.C5 | SH0411:B | TCP, SMT130 | 38.C5
SH0411:A+ | SC | TCP21AP | WHT | 20 | 38.C5 | SH0411:B+ | TCP, SMT130 | 38.C5
SH0412:A | SC | TCP22A | WHT | 20 | 38.C5 | SH0412:B | TCP, SMT130 | 38.C5
SH0412:A+ | SC | TCP22AP | WHT | 20 | 38.C5 | SH0412:B+ | TCP, SMT130 | 38.C5
XT0564:1 T2 | SC | TCP26NO | WHT | 20 | 37.B5 | XT0564:2 T2 | TCP, SMT130 | 37.B5
XT0564:2 T1 | SC | TCP26NO | WHT | 20 | 37.B5 | XT0564:3 T1 | TCP, SMT130 | 37.B5
XT0564:3 T2 | SC | TCP26NO | WHT | 20 | 37.B5 | XT0564:4 T2 | TCP, SMT130 | 37.C5
XT0564:4 T1 | SC | TCP26NO | WHT | 20 | 37.C5 | XT0564:5 T1 | TCP, SMT130 | 37.C5
AU0200:L2 | WC0020 | AU0200L2 | ENET | CABLE | 2.C5 | AU0120:L1 | GEN CMPNT | 2.C2
SB0400:B2-11 | SC | SB0400B211 | WHT | 20 | 38.A1 | AF0297:36 | MCC PNL,SMT130 | 38.A3
SB0400:B2-12 | SC | SB0400B212 | WHT | 20 | 38.A1 | AF0297:04 | MCC PNL,SMT130 | 38.A3
AU0200:L1 | WC0029 | AU0290L2 | ENET | CABLE | 2.C5 | AU0290:L2 | MCC PNL,SMT130 | 2.C5
AF0202:23 | WC5540 | HA0273P | BLK | 16 | 37.D6 | HA0273:(+) | PNL,DOOR,2-BAY | 37.D4
AF0202:55 | WC5540 | HA0273N | WHT | 16 | 37.D6 | HA0273:(-) | PNL,DOOR,2-BAY | 37.D4
AU0200:GND | SC | AU0200G | GRN | 14 | 35.A4 | IEG2240:5 | POWERDIST, PANEL | 35.B5
GR0200: | SC | IEG22404 | GRN | 14 | 35.A3 | IEG2240:4 | POWERDIST, PANEL | 35.A3
AF0202:COM | SC | 0V | WHT | 16 | 35.A6 | XT0562:3 | PWR DST,DR,SMT130 | 35.B2
AF0202:V+ | SC | FU0201 | WHT | 16 | 35.A6 | FU0201:LD | PWR DST,DR,SMT130 | 35.B3
AU0200:COM | SC | 0V | WHT | 16 | 35.A4 | XT0562:2 | PWR DST,DR,SMT130 | 35.B2
AU0200:V+ | SC | FU0200 | WHT | 16 | 35.A4 | FU0200:LD | PWR DST,DR,SMT130 | 35.A3
HL0410:A | SC | 0V | WHT | 20 | 37.B5 | XT0563:4 | PWR DST,DR,SMT130 | 37.B6
SA0401:1 | SC | KA0241A1 | WHT | 20 | 37.C5 | XT0563:5 | PWR DST,DR,SMT130 | 37.C6
SA0401:2 | SC | FU0139 | WHT | 20 | 37.C5 | XT0563:6 | PWR DST,DR,SMT130 | 37.C6
SB0400:B1-11 | SC | SB851222 | WHT | 20 | 37.D5 | XT0563:1 | PWR DST,DR,SMT130 | 37.D6
SB0400:B1-12 | SC | SB047212 | WHT | 20 | 37.D5 | XT0563:2 | PWR DST,DR,SMT130 | 37.D6
SH0400:B | SC | 0V | WHT | 20 | 37.B5 | XT0562:4 | PWR DST,DR,SMT130 | 35.C2
XT0564:1 B2 | SC | KA023612 | WHT | 20 | 37.B5 | XT0563:3 | PWR DST,DR,SMT130 | 37.B6
SolarTools ver. 24.0.84.24712 (Jul 31, 2025)
Report date: 2/3/2026 11:55 AM

## TURBINE CONTROL^JB70
TURBINE CONTROL^JB70
Project # | 4L321
Project Name | Enterprise SMT130 M4 WTX
Revision | 0.1
Controls DE
Phone:
Controls ME
Phone:
From | [5 empty] | To
Device ID | Cable (W) Conductor (SC) Jumper Clip (JC) | Wire No. | Wire ID | Gauge/Size | Page/Zone | Device ID | Location | Page/Zone
GR1000: | SC | GR1000 | GRN/YEL | 14 | 22.B4 | FRAME | TURBINE CONTROL^JB70 | 22.B4
GR1100: | SC | GR1100 | GRN/YEL | 14 | 22.B4 | FRAME | TURBINE CONTROL^JB70 | 22.B4
HA0472:BLK-2 | WC5072 | HA0472BLK-2 | BLK | 16 | 28.A1 | XT0235:5 | PNL B,SMT130 | 28.A5
HA0472:BLK-1 | WC5072 | 0V | WHT | 16 | 28.A1 | XT0235:6 | PNL B,SMT130 | 28.A5
SolarTools ver. 24.0.84.24712 (Jul 31, 2025)
Report date: 2/3/2026 11:55 AM

## Panel Errors
Panel Errors
Project # | 4L321
Project Name | Enterprise SMT130 M4 WTX
Revision | 0.1
Controls DE
Phone:
Controls ME
Phone:
From | [6 empty] | To
Device ID | Location | Cable (W) Conductor (SC) Jumper Clip (JC) | Wire ID | Wire No. | Gauge/Size | Page/Zone | Device ID | Location | Page/Zone
Report date: 2/3/2026 11:55 AM |  |  |  | SolarTools ver. 24.0.84.24712 (Jul 31, 2025)

## Cable Part Numbers
Cable Part Numbers |  |  | SolarTools ver. 24.0.84.24712 (Jul 31, 2025)
Project # | 4L321
Report date: 2/3/2026 11:56 AM
Project Name | Enterprise SMT130 M4 WTX
Revision | 0.1
Controls DE
Phone:
Controls ME
Phone:
Device ID |  | Part Number |  | Description
WC0006 |  | 1302073-36 |  | CABLE, ETHERNET - 36 INCHES
WC0007 |  | 1302073-36 |  | CABLE, ETHERNET - 36 INCHES
WC0008 |  | 1302073-36 |  | CABLE, ETHERNET - 36 INCHES
WC0009 |  | 1302073-36 |  | CABLE, ETHERNET - 36 INCHES
WC0012 |  | 1302073-36 |  | CABLE, ETHERNET - 36 INCHES
WC0014 |  | 1302073-36 |  | CABLE, ETHERNET - 36 INCHES
WC0017 |  | 1302073-36 |  | CABLE, ETHERNET - 36 INCHES
WC0018 |  | 1302073-36 |  | CABLE, ETHERNET - 36 INCHES
WC0019 |  | 1302073-36 |  | CABLE, ETHERNET - 36 INCHES
WC0020 |  | 1302073-36 |  | CABLE, ETHERNET - 36 INCHES
WC0029 |  | 1302073-36 |  | CABLE, ETHERNET - 36 INCHES
WC0041 |  | 1302073-36 |  | CABLE, ETHERNET - 36 INCHES
WC0042 |  | 1302073-36 |  | CABLE, ETHERNET - 36 INCHES
WC0602 |  | 1302073-36 |  | CABLE, ETHERNET - 36 INCHES
WC0603 |  | 1302073-36 |  | CABLE, ETHERNET - 36 INCHES
WC1242 |  | 1022941-13 |  | TPE, 1 TRIAD TWISTED SHIELDED
WC1243 |  | 1022941-13 |  | TPE, 1 TRIAD TWISTED SHIELDED
WC1244 |  | 1022941-13 |  | TPE, 1 TRIAD TWISTED SHIELDED
WC1245 |  | 1022941-13 |  | TPE, 1 TRIAD TWISTED SHIELDED
WC1246 |  | 1022941-13 |  | TPE, 1 TRIAD TWISTED SHIELDED
WC4524 |  | 1022941-12 |  | TPE, 1 PAIR TWISTED SHIELDED
WC5072 |  | PART OF 1113568-200 |  | CABLE, 2 CONDUCTOR TRIMMED SHIELD PART OF HORN
WC5540 |  | PART OF 1113568-200 |  | CABLE, 2 CONDUCTOR TRIMMED SHIELD PART OF HORN
WC7024 |  | 1302073-36 |  | CABLE, ETHERNET - 36 INCHES
WC7028 |  | 1302073-36 |  | CABLE, ETHERNET - 36 INCHES
WC7071 |  | 1302073-36 |  | CABLE, ETHERNET - 36 INCHES
WC7622 |  | 1022941-12 |  | TPE, 1 PAIR TWISTED SHIELDED
WC8009 |  | 1022941-22 |  | TPE, 1 PAIR TWISTED SHIELDED
WC8040 |  | 1322418-90 |  | CABLE, DYNAMIX 1444 BUS
WC8041 |  | 1322418-90 |  | CABLE, DYNAMIX 1444 BUS
WC8042 |  | 1322418-90 |  | CABLE, DYNAMIX 1444 BUS
WC8050 |  | 1322418-90 |  | CABLE, DYNAMIX 1444 BUS
WC8066 |  | 1022941-22 |  | TPE, 1 PAIR TWISTED SHIELDED
WC8067 |  | 1022941-22 |  | TPE, 1 PAIR TWISTED SHIELDED
WC8069 |  | 1022941-22 |  | TPE, 1 PAIR TWISTED SHIELDED
WC8071 |  | 1022941-22 |  | TPE, 1 PAIR TWISTED SHIELDED
WC8101 |  | 1022941-33 |  | TPE, 1 TRIAD TWISTED SHIELDED
WC8102 |  | 1022941-32 |  | TPE, 1 PAIR TWISTED SHIELDED
WC8201 |  | 1022941-33 |  | TPE, 1 TRIAD TWISTED SHIELDED
WC8301 |  | 1022941-33 |  | TPE, 1 TRIAD TWISTED SHIELDED

## Part Number List
Part Number List |  | SolarTools ver. 24.0.84.24712 (Jul 31, 2025)
Project # | 4L321
Report date: 2/3/2026 11:56 AM
Project Name | Enterprise SMT130 M4 WTX
Revision | 0.1
Controls DE
Phone:
Controls ME
Phone:
Device ID | Part Number | Description | Location
KA0460 | 1062941-400 | RELAY, BECKWITH, M3425-A GENERATOR PROTECTION | BECKWITH RELAY,SMT130
EL0273 | 2403630-1 | LIGHT, LED, CONTROL BOX, WHITE | CONTROL,2-BAY
AF0500 | 1322418-31,1322418-40,1322418-72,1322418-73 | 1444-TSCX02-02RB, 2-CH TACHOMETER INPUT^DYNAMIX 1444 VIBRATION | FG&E CTRL,SMT130
AF0510 | 1322418-11,1322418-20,1322418-70,1322418-71 | 1444-DYN04-01RA, 4-CH VIBRATION INPUT^DYNAMIX 1444 VIBRATION | FG&E CTRL,SMT130
AT0170 | 1056244-29 | CONTROLLER, EAGLE QUANTUM PREMIER | FG&E CTRL,SMT130
AT0171 | 1056244-5 | 8 CHANNEL ED I/O, EAGLE QUANTUM PREMIER | FG&E CTRL,SMT130
AT0175 | 1056244-5 | 8 CHANNEL ED I/O, EAGLE QUANTUM PREMIER | FG&E CTRL,SMT130
AT0176 | 1056244-5 | 8 CHANNEL ED I/O, EAGLE QUANTUM PREMIER | FG&E CTRL,SMT130
AT0178 | 1056244-5 | 8 CHANNEL ED I/O, EAGLE QUANTUM PREMIER | FG&E CTRL,SMT130
FU0170 | 1043265-1,1043265-5 | FUSE, 10A | FG&E CTRL,SMT130
FU0171 | 1043265-1,1043265-5 | FUSE, 10A | FG&E CTRL,SMT130
FU0510 | 1043265-1,1043265-4 | FUSE, 5A | FG&E CTRL,SMT130
GR0170 | 903849C1 | RAIL GROUND, DIN RAIL GROUNDING | FG&E CTRL,SMT130
GR0172 | 903849C1 | RAIL GROUND, DIN RAIL GROUNDING | FG&E CTRL,SMT130
IEG0356 | 232941-200 | BUS BAR, FIRE SYSTEM PANEL - INSTRUMENTATION GROUNDING | FG&E CTRL,SMT130
KA0172 | 1061979-1 | RELAY, FIRE DETECTED (CUSTOMER) | FG&E CTRL,SMT130
KA0174 | 1061979-1 | RELAY, GAS DETECTED (CUSTOMER) | FG&E CTRL,SMT130
KA0179 | 1061979-1 | RELAY, MV FIRE (CUSTOMER) | FG&E CTRL,SMT130
KA6510 | 1061979-1 | RELAY, FIRE SYSTEM AUTO/INHIBIT | FG&E CTRL,SMT130
RR0178 | 912137C1 | RESISTOR, 10K OHM | FG&E CTRL,SMT130
RR1755 | 912137C1 | RESISTOR, 10K OHM | FG&E CTRL,SMT130
RR7610 | 912137C1 | RESISTOR, 10K OHM | FG&E CTRL,SMT130
RR7611 | 912137C1 | RESISTOR, 10K OHM | FG&E CTRL,SMT130
RR7613 | 912137C1 | RESISTOR, 10K OHM | FG&E CTRL,SMT130
RR7614 | CUSTOMER SUPPLIED | RESISTOR, 10K OHM | FG&E CTRL,SMT130
RR7615 | CUSTOMER SUPPLIED | RESISTOR, 10K OHM | FG&E CTRL,SMT130
RR7616 | CUSTOMER SUPPLIED | RESISTOR, 10K OHM | FG&E CTRL,SMT130
RR7617 | CUSTOMER SUPPLIED | RESISTOR, 10K OHM | FG&E CTRL,SMT130
UAI6611 | 1053038-28 | ISOLATOR, DISCRETE INPUT SIGNAL | FG&E CTRL,SMT130
UAI6621 | 1053038-28 | ISOLATOR, DISCRETE INPUT SIGNAL | FG&E CTRL,SMT130
UV0170 | 1056244-2 | POWER SUPPLY, EAGLE QUANTUM PREMIER | FG&E CTRL,SMT130
VD0178 | 960592C1 | DIODE, 15 pF | FG&E CTRL,SMT130
XT0170 | 1066730-7,1066730-8,1067996-11 | TERMINAL BLOCK, SPRING, 4 CONDUCTOR,30-12 AWG (0.05-3.31 MM2),NON-IS | FG&E CTRL,SMT130
XT0171 | 1066730-7,1066730-8,1067996-11 | TERMINAL BLOCK, SPRING, 4 CONDUCTOR,30-12 AWG (0.05-3.31 MM2),NON-IS | FG&E CTRL,SMT130
XT0172 | 1066730-7,1066730-8,1067996-11 | TERMINAL BLOCK, SPRING, 4 CONDUCTOR,30-12 AWG (0.05-3.31 MM2),NON-IS | FG&E CTRL,SMT130
XT0173 | 1066730-7,1066730-8,1067996-11 | TERMINAL BLOCK, SPRING, 4 CONDUCTOR,30-12 AWG (0.05-3.31 MM2),NON-IS | FG&E CTRL,SMT130
XT0500 | 1066730-7,1066730-8,1067996-11 | TERMINAL BLOCK, SPRING, 4 CONDUCTOR,30-12 AWG (0.05-3.31 MM2),NON-IS | FG&E CTRL,SMT130
XT0510 | 1066730-7,1066730-8,1067996-11 | TERMINAL BLOCK, SPRING, 4 CONDUCTOR,30-12 AWG (0.05-3.31 MM2),NON-IS | FG&E CTRL,SMT130
XT0550 | 1066730-7,1066730-8,1067996-11 | TERMINAL BLOCK, SPRING, 4 CONDUCTOR,30-12 AWG (0.05-3.31 MM2),NON-IS | FG&E CTRL,SMT130
AF0121 | 2684693-17,2684693-24 | 5094-OB16XT, 16 DISCRETE OUTPUT | GEN CMPNT
AF0122 | 2684693-17,2684693-23 | 5094-IB16XT, 16 DISCRETE INPUT | GEN CMPNT
AF0123 | 2684693-19,2684693-33 | 5094-IY8XT, 8 ANALOG INPUT, TC/RTD/ I&V | GEN CMPNT
AF0181 | 2684693-17,2684693-23 | 5094-IB16XT, 16 DISCRETE INPUT | GEN CMPNT
AF0182 | 2684693-18,2684693-56 | 5094-IF8IHXT, 8 ANALOG INPUT, ISOLATED | GEN CMPNT
AT0140 | 2769310-1,2769310-4 | MODULE, DESC-250 | GEN CMPNT
AU0120 | 2684693-22 | 5094-AENTRXT, FLEX 5000 I/O | GEN CMPNT
AU0180 | 2684693-22 | 5094-AENTRXT, FLEX 5000 I/O | GEN CMPNT
FU0120 | 1043265-1,1043265-5 | FUSE, 10A | GEN CMPNT
FU0121 | 1043265-5 | FUSE, 10A | GEN CMPNT
FU0180 | 1043265-5 | FUSE, 10A | GEN CMPNT
FU0181 | 1043265-5 | FUSE, 10A | GEN CMPNT
FU0313 | 1043265-1,1043265-7 | FUSE, 20A | GEN CMPNT
FU0314 | 1043265-1,1043265-7 | FUSE, 20A | GEN CMPNT
FU0315 | 1043265-1,1043265-7 | FUSE, 20A | GEN CMPNT
FU0332 | 1043265-7 | FUSE, 20A | GEN CMPNT
FU0333 | 1043265-4 | FUSE, 5A | GEN CMPNT
FU0334 | 1043265-4 | FUSE, 5A | GEN CMPNT
FU0335 | 1043265-4 | FUSE, 5A | GEN CMPNT
FU0336 | 1043265-3 | FUSE, 2A | GEN CMPNT
GR0139 | 903849C1 | RAIL GROUND, DIN RAIL GROUNDING | GEN CMPNT
GR0140 | 903849C1 | RAIL GROUND, DIN RAIL GROUNDING | GEN CMPNT
GR0141 | 903849C1 | RAIL GROUND, DIN RAIL GROUNDING | GEN CMPNT
IEG0140 | 232941-110 | BUS BAR, GENERATOR PANEL - INSTRUMENTATION GROUNDING | GEN CMPNT
KA0121 | 1061979-1 | RELAY, AUTOMATIC CLOSE CIRCUIT BREAKER | GEN CMPNT
KA0123 | 1061979-1 | RELAY, CGCM #1 ENABLED | GEN CMPNT
KA0128 | 1061979-1 | RELAY, GENERATOR TRIP SUMMARY CIRCUIT BREAKER | GEN CMPNT
KA0185 | 1061979-1 | RELAY, PERMISSIVE CLOSE CIRCUIT BREAKER | GEN CMPNT
KA0310 | 1061979-1 | RELAY, CGCM #1 FAULT | GEN CMPNT
KA0313 | 1076251-1,1076251-2 | RELAY, PMG INPUT #1 | GEN CMPNT
KA0314 | 1076251-1,1076251-2 | RELAY, PMG INPUT #1 | GEN CMPNT
KA0330 | 1061979-1 | RELAY, CLOSED CIRCUIT BREAKER | GEN CMPNT
KA0331 | 1061979-1 | RELAY, MAIN UTILITY BREAKER AUXILIARY CONTACT CLOSED | GEN CMPNT
KA0332 | 1061979-1 | RELAY, CLOSE CONTROL CIRCUIT BREAKER | GEN CMPNT
KA0333 | 1061979-1 | RELAY, TRIP CONTROL CIRCUIT BREAKER | GEN CMPNT
KA0335 | 1061979-1 | RELAY, NO EMERGENCY SHUTDOWN SUMMARY | GEN CMPNT
KA0336 | 1061979-1 | RELAY, CONTROLLER ACTIVE | GEN CMPNT
KA0340 | 1061979-1 | RELAY, BLACK START GEN REMOTE CONTROL | GEN CMPNT
KA2320 | 1061979-1 | RELAY, LUBE OIL COOLER^ENABLE | GEN CMPNT
KA2672 | 1061979-1 | RELAY, GENERATOR VOLT SELECTION | GEN CMPNT
KA2685 | 1061979-1 | RELAY, LBS AUX REMOTE OPEN | GEN CMPNT
KA3103 | 1061979-1 | RELAY, LUBE OIL TANK HEATER | GEN CMPNT
KA3420 | 1061979-1 | RELAY, GENERATOR JACKING OIL | GEN CMPNT
KA4100 | 1061979-1 | RELAY, GENERATOR HEATER ENABLED | GEN CMPNT
PEG0140 | 232941-110 | BUS BAR, GENERATOR PANEL - POWER EARTH GROUNDING | GEN CMPNT
XT0120 | 1066730-7,1066730-8,1067996-4 | TERMINAL BLOCK, SPRING, 4 CONDUCTOR,30-12 AWG (0.05-3.31 MM2),NON-IS | GEN CMPNT
XT0130 | 1066730-7,1066730-8,1067996-4 | TERMINAL BLOCK, SPRING, 4 CONDUCTOR,30-12 AWG (0.05-3.31 MM2),NON-IS | GEN CMPNT
XT0180 | 1066730-7,1066730-8,1067996-4 | TERMINAL BLOCK, SPRING, 4 CONDUCTOR,30-12 AWG (0.05-3.31 MM2),NON-IS | GEN CMPNT
XT0181 | 1066730-7,1066730-8,1067996-4 | TERMINAL BLOCK, SPRING, 4 CONDUCTOR,30-12 AWG (0.05-3.31 MM2),NON-IS | GEN CMPNT
XT0183 | 1066730-7,1066730-8,1067996-4 | TERMINAL BLOCK, SPRING, 4 CONDUCTOR,30-12 AWG (0.05-3.31 MM2),NON-IS | GEN CMPNT
XT0190 | 1066730-7,1066730-8,1067996-4 | TERMINAL BLOCK, SPRING, 4 CONDUCTOR,30-12 AWG (0.05-3.31 MM2),NON-IS | GEN CMPNT
XT0313 | 1066730-7,1066730-8,1067996-4 | TERMINAL BLOCK, SPRING, 4 CONDUCTOR,30-12 AWG (0.05-3.31 MM2),NON-IS | GEN CMPNT
XT0332 | 1066730-7 | TERMINAL BLOCK, SPRING, 4 CONDUCTOR,30-12 AWG (0.05-3.31 MM2),NON-IS | GEN CMPNT
XT0334 | 1066730-7 | TERMINAL BLOCK, SPRING, 4 CONDUCTOR,30-12 AWG (0.05-3.31 MM2),NON-IS | GEN CMPNT
XT0335 | 1066730-7 | TERMINAL BLOCK, SPRING, 4 CONDUCTOR,30-12 AWG (0.05-3.31 MM2),NON-IS | GEN CMPNT
XT0336 | 1066730-7 | TERMINAL BLOCK, SPRING, 4 CONDUCTOR,30-12 AWG (0.05-3.31 MM2),NON-IS | GEN CMPNT
XT0337 | 1066730-7 | TERMINAL BLOCK, SPRING, 4 CONDUCTOR,30-12 AWG (0.05-3.31 MM2),NON-IS | GEN CMPNT
XT0350 | 1066730-16,1066730-17,1066730-18 | TERMINAL STRIP, 2 CONDUCTOR | GEN CMPNT
XT0351 | 1066730-7,1066730-8,1067996-4 | TERMINAL BLOCK, SPRING, 4 CONDUCTOR,30-12 AWG (0.05-3.31 MM2),NON-IS | GEN CMPNT
XT0352 | 1066730-16,1066730-17,1066730-18 | TERMINAL STRIP, 2 CONDUCTOR | GEN CMPNT
XT0353 | 1066730-16,1066730-17,1066730-18 | TERMINAL STRIP, 2 CONDUCTOR | GEN CMPNT
XT0360 | 1066730-7,1066730-8,1067996-4 | TERMINAL BLOCK, SPRING, 4 CONDUCTOR,30-12 AWG (0.05-3.31 MM2),NON-IS | GEN CMPNT
XT0370 | 1066730-7 | TERMINAL BLOCK, SPRING, 4 CONDUCTOR,30-12 AWG (0.05-3.31 MM2),NON-IS | GEN CMPNT
XT0454 | 1066730-16,1066730-17,1066730-18 | TERMINAL STRIP, 2 CONDUCTOR | GEN CMPNT
XT0460 | 1066730-7,1066730-8,1067996-4 | TERMINAL BLOCK, SPRING, 4 CONDUCTOR,30-12 AWG (0.05-3.31 MM2),NON-IS | GEN CMPNT
XT2910 | 1066730-7,1066730-8,1067996-4 | TERMINAL BLOCK, SPRING, 4 CONDUCTOR,30-12 AWG (0.05-3.31 MM2),NON-IS | GEN CMPNT
XT7100 | PART OF J-BOX | TERMINAL BLOCK, JUNCTION BOX ASSEMBLY | JB7100
XT7701 | 1066730-22 | TERMINAL STRIP, 2 CONDUCTOR | JB770
XT7720 | PART OF J-BOX | TERMINAL BLOCK, JUNCTION BOX ASSEMBLY | JB772
CCAP0609 | PART OF ASSEMBLY | ETHERNET CONNECTION, SUPERVISORY PORT | JB774
CCENET1 | PART OF ASSEMBLY | CUSTOMER CONNECTION, ETHERNET PORT A | JB774
CCENET2 | PART OF ASSEMBLY | CUSTOMER CONNECTION, ETHERNET PORT B | JB774
CCENET3 | PART OF ASSEMBLY | CUSTOMER CONNECTION, ETHERNET PORT C | JB774
LSENET1 | PART OF ASSEMBLY | LOAD SHARE CONNECTION, LS PORT A | JB774
LSENET2 | PART OF ASSEMBLY | LOAD SHARE CONNECTION, LS PORT B | JB774
AF0291 | 2684693-17,2684693-24 | 5094-OB16XT, 16 DISCRETE OUTPUT | MCC PNL,SMT130
AF0292 | 2684693-17,2684693-23 | 5094-IB16XT, 16 DISCRETE INPUT | MCC PNL,SMT130
AF0293 | 2684693-19,2684693-33 | 5094-IY8XT, 8 ANALOG INPUT, TC/RTD/ I&V | MCC PNL,SMT130
AF0294 | 2684693-18,2684693-30 | 5094-IF4IHSXT, 4 ANALOG INPUT, S | MCC PNL,SMT130
AF0295 | 2684693-18,2684693-30 | 5094-IF4IHSXT, 4 ANALOG INPUT, S | MCC PNL,SMT130
AF0296 | 2684693-17,2684693-23 | 5094-IB16XT, 16 DISCRETE INPUT | MCC PNL,SMT130
AF0297 | 2684693-18,2684693-28 | 5094-IB16SXT, 16 DISCRETE INPUT, S | MCC PNL,SMT130
AU0290 | 2684693-22 | 5094-AENTRXT, FLEX 5000 I/O | MCC PNL,SMT130
FU0290 | 1043265-1,1043265-5 | FUSE, 10A | MCC PNL,SMT130
FU0291 | 1043265-1,1043265-5 | FUSE, 10A | MCC PNL,SMT130
FU0294 | 1043265-1,1043265-5 | FUSE, 10A | MCC PNL,SMT130
GR0290 | 903849C1 | RAIL GROUND, DIN RAIL GROUNDING | MCC PNL,SMT130
GR0291 | 903849C1 | RAIL GROUND, DIN RAIL GROUNDING | MCC PNL,SMT130
KA2960 | 1061979-1 | RELAY, ATS CB TRIP^SUMMARY | MCC PNL,SMT130
KA2970 | 1061979-1 | RELAY, LUBE OIL DEMISTER^ENABLE | MCC PNL,SMT130
PEG2240 | 232941-300 | BUS BAR, POWER DISTRIBUTION - POWER EARTH GROUNDING | MCC PNL,SMT130
RR2921 | 981090C1 | RESISTOR, 3.01K OHM | MCC PNL,SMT130
RR2922 | 981089C1 | RESISTOR, 1.0K OHM | MCC PNL,SMT130
XT0290 | 1066730-7,1066730-8,1067996-4 | TERMINAL BLOCK, SPRING, 4 CONDUCTOR,30-12 AWG (0.05-3.31 MM2),NON-IS | MCC PNL,SMT130
XT0292 | 1066730-7,1066730-8,1067996-4 | TERMINAL BLOCK, SPRING, 4 CONDUCTOR,30-12 AWG (0.05-3.31 MM2),NON-IS | MCC PNL,SMT130
XT0295 | 1066730-7,1066730-8,1067996-4 | TERMINAL BLOCK, SPRING, 4 CONDUCTOR,30-12 AWG (0.05-3.31 MM2),NON-IS | MCC PNL,SMT130
XT2920 | 1066730-7,1066730-8,1067996-4 | TERMINAL BLOCK, SPRING, 4 CONDUCTOR,30-12 AWG (0.05-3.31 MM2),NON-IS | MCC PNL,SMT130
AP0601 | 1089241-20 | MODULE, BLANK FILLER | PLC, PANEL
AP0602 | 1089241-40 | 1756-EN2TRXT, ETHERNET | PLC, PANEL
AP0603 | 1089241-40 | 1756-EN2TRXT, ETHERNET | PLC, PANEL
AP0604 | 1089241-20 | MODULE, BLANK FILLER | PLC, PANEL
AP0605 | 1089241-20 | MODULE, BLANK FILLER | PLC, PANEL
AP0606 | 1089241-40 | 1756-EN2TRXT, ETHERNET | PLC, PANEL
AP0607 | 1089241-40 | 1756-EN2TRXT, ETHERNET | PLC, PANEL
AP0608 | 1089241-36 | 1756-EN2TXT, ETHERNET | PLC, PANEL
AP0609 | 1089241-36 | 1756-EN2TXT, ETHERNET | PLC, PANEL
AR0600 | 1089241-42 | RACK CHASSIS, 1756-A10XT (10 SLOT) | PLC, PANEL
AT0600 | 1089241-43 | 1756-L83EXTS, CONTROLLER^GUARDLOGIX | PLC, PANEL
UV0600 | 1089241-28 | POWER SUPPLY, RSLOGIX CHASSIS | PLC, PANEL
AF0081 | 2684693-17,2684693-25 | 5094-OB8XT, 8 DISCRETE OUTPUT | PNL A,SMT130
AF0082 | 2684693-17,2684693-23 | 5094-IB16XT, 16 DISCRETE INPUT | PNL A,SMT130
AF0083 | 2684693-19,2684693-33 | 5094-IY8XT, 8 ANALOG INPUT, TC/RTD/ I&V | PNL A,SMT130
AF0084 | 2684693-18,2684693-56 | 5094-IF8IHXT, 8 ANALOG INPUT, ISOLATED | PNL A,SMT130
AF0085 | 2684693-18,2684693-56 | 5094-IF8IHXT, 8 ANALOG INPUT, ISOLATED | PNL A,SMT130
AF0086 | 2684693-19,2684693-33 | 5094-IY8XT, 8 ANALOG INPUT, TC/RTD/ I&V | PNL A,SMT130
AF0091 | 2684693-17,2684693-23 | 5094-IB16XT, 16 DISCRETE INPUT | PNL A,SMT130
AF0092 | 2684693-17,2684693-24 | 5094-OB16XT, 16 DISCRETE OUTPUT | PNL A,SMT130
AF0093 | 2684693-18,2684693-28 | 5094-IB16SXT, 16 DISCRETE INPUT, S | PNL A,SMT130
AU0080 | 2684693-22 | 5094-AENTRXT, FLEX 5000 I/O | PNL A,SMT130
AU0090 | 2684693-22 | 5094-AENTRXT, FLEX 5000 I/O | PNL A,SMT130
FU0080 | 1043265-5 | FUSE, 10A | PNL A,SMT130
FU0081 | 1043265-5 | FUSE, 10A | PNL A,SMT130
FU0082 | 1043265-5 | FUSE, 10A | PNL A,SMT130
FU0090 | 1043265-5 | FUSE, 10A | PNL A,SMT130
FU0091 | 1043265-5 | FUSE, 10A | PNL A,SMT130
FU0092 | 1043265-5 | FUSE, 10A | PNL A,SMT130
FU0093 | 1043265-1,1043265-5 | FUSE, 10A | PNL A,SMT130
FU0137 | 1043265-7 | FUSE, 20A | PNL A,SMT130
FU0139 | 1043265-4 | FUSE, 5A | PNL A,SMT130
FU0140 | 1043265-1,1043265-4 | FUSE, 5A | PNL A,SMT130
FU2100 | 1043265-1,1043265-4 | FUSE, 5A | PNL A,SMT130
GR0111 | 903849C1 | RAIL GROUND, DIN RAIL GROUNDING | PNL A,SMT130
GR0131 | 903849C1 | RAIL GROUND, DIN RAIL GROUNDING | PNL A,SMT130
GR0132 | 903849C1 | RAIL GROUND, DIN RAIL GROUNDING | PNL A,SMT130
GR0134 | 903849C1 | RAIL GROUND, DIN RAIL GROUNDING | PNL A,SMT130
KA0130 | 1061979-1 | RELAY, LOWSPEED/OPEN PROBE SETPOINT | PNL A,SMT130
KA0131 | 1061979-1 | RELAY, CONTROLLER ACTIVE | PNL A,SMT130
KA0132 | 1061979-1 | RELAY, CONTROLLER ACTIVE | PNL A,SMT130
KA0133 | 1061979-1 | RELAY, POST LUBE NOT REQUIRED | PNL A,SMT130
KA0134 | 1061979-1 | RELAY, BACKUP COMMAND OFF | PNL A,SMT130
KA0135 | 1061979-1 | RELAY, AC PRE/POST PUMP DRIVE | PNL A,SMT130
KA0136 | 1061979-1 | RELAY, LUBE OIL HEADER PRESSURE HIGH | PNL A,SMT130
KA0137 | 1061979-1 | RELAY, LUBE PUMP INHIBIT | PNL A,SMT130
KA0138 | 1061979-1 | RELAY, BACKUP LUBE OIL PUMP OFF | PNL A,SMT130
KA0141 | 1061979-1 | RELAY, CONTROLLER ACTIVE | PNL A,SMT130
KA0142 | 1061979-1 | RELAY, SPARE | PNL A,SMT130
KA0176 | 1061979-1 | RELAY, VENTILATION REQUIRED | PNL A,SMT130
KA0177 | 1061979-1 | RELAY, VENTILATION REQUIRED | PNL A,SMT130
KA0178 | 1061979-1 | RELAY, LOCAL HORN CONTROL (EQP) | PNL A,SMT130
KA0221 | 1061979-1 | RELAY | PNL A,SMT130
KA0222 | 1061979-1 | RELAY | PNL A,SMT130
KA0875 | 1061979-1 | RELAY, LOCAL HORN CONTROL (PLC) | PNL A,SMT130
KA6211 | 1061979-1 | RELAY, DRIVER ENCLOSURE^VENT FAN #1 | PNL A,SMT130
KA6212 | 1061979-1 | RELAY, DRIVER ENCLOSURE^VENT FAN #2 | PNL A,SMT130
KA6221 | 1061979-1 | RELAY, GENERATOR ENCLOSURE^VENT FAN #1 | PNL A,SMT130
KA6222 | 1061979-1 | RELAY, DRIVEN ENCLOSURE^VENT FAN #2 | PNL A,SMT130
KT0140 | 2651077-1 | TIMER RELAY, BACKUP PUMP POST LUBE OFF CYCLE | PNL A,SMT130
KT0141 | 2651077-1 | TIMER RELAY, BACKUP POST LUBE CONTINUOUS | PNL A,SMT130
KT0142 | 2651077-1 | TIMER RELAY, TOTAL POST LUBE | PNL A,SMT130
KT0143 | 2651077-1 | TIMER RELAY, BACKUP PUMP POST LUBE ON CYCLE | PNL A,SMT130
KT0144 | 2651077-1 | TIMER RELAY, HEADER PRESSURE HIGH BACKUP PUMP OFF | PNL A,SMT130
KT0145 | 2651077-1 | TIMER RELAY, FIRE DETECTED ROLLDOWN LUBE | PNL A,SMT130
KT0146 | 2651077-3 | TIMER RELAY, WATCHDOG | PNL A,SMT130
PC0470 | 2271605-1 | TIMER/COUNTER, ENGINE HOUR / START COUNTER | PNL A,SMT130
PEG0130 | 232941-300 | BUS BAR, PANEL A - POWER EARTH GROUNDING | PNL A,SMT130
VD6211 | 960592C1 | DIODE, 15 pF | PNL A,SMT130
VD6212 | 960592C1 | DIODE, 15 pF | PNL A,SMT130
VD6221 | 960592C1 | DIODE, 15 pF | PNL A,SMT130
VD6222 | 960592C1 | DIODE, 15 pF | PNL A,SMT130
XT0015 | 1066730-16,1066730-17,1066730-18 | TERMINAL STRIP, 2 CONDUCTOR | PNL A,SMT130
XT0016 | 1066730-16,1066730-17,1066730-18 | TERMINAL STRIP, 2 CONDUCTOR | PNL A,SMT130
XT0017 | 1066730-16,1066730-17,1066730-18 | TERMINAL STRIP, 2 CONDUCTOR | PNL A,SMT130
XT0080 | 1066730-7,1066730-8,1067996-4 | TERMINAL BLOCK, SPRING, 4 CONDUCTOR,30-12 AWG (0.05-3.31 MM2),NON-IS | PNL A,SMT130
XT0090 | 1066730-7,1066730-8,1067996-4 | TERMINAL BLOCK, SPRING, 4 CONDUCTOR,30-12 AWG (0.05-3.31 MM2),NON-IS | PNL A,SMT130
XT0134 | 1066730-16,1066730-17,1066730-18 | TERMINAL STRIP, 2 CONDUCTOR | PNL A,SMT130
XT0135 | 1066730-7,1066730-8,1067996-4 | TERMINAL BLOCK, SPRING, 4 CONDUCTOR,30-12 AWG (0.05-3.31 MM2),NON-IS | PNL A,SMT130
XT0136 | 1066730-7,1066730-8,1067996-3 | TERMINAL BLOCK, SPRING, 4 CONDUCTOR,30-12 AWG (0.05-3.31 MM2),NON-IS | PNL A,SMT130
XT0137 | 1066730-7,1066730-8,1067996-4 | TERMINAL BLOCK, SPRING, 4 CONDUCTOR,30-12 AWG (0.05-3.31 MM2),NON-IS | PNL A,SMT130
XT0138 | 1066730-16,1066730-17,1066730-18 | TERMINAL STRIP, 2 CONDUCTOR | PNL A,SMT130
XT0139 | 1066730-7,1066730-8,1067996-4 | TERMINAL BLOCK, SPRING, 4 CONDUCTOR,30-12 AWG (0.05-3.31 MM2),NON-IS | PNL A,SMT130
XT1135 | 1066730-7,1066730-8,1067996-4 | TERMINAL BLOCK, SPRING, 4 CONDUCTOR,30-12 AWG (0.05-3.31 MM2),NON-IS | PNL A,SMT130
AF0061 | 2684693-17,[2]2684693-25 | 5094-OB8XT, 8 DISCRETE OUTPUT | PNL B,SMT130
AF0062 | 2684693-17,2684693-25 | 5094-OB8XT, 8 DISCRETE OUTPUT | PNL B,SMT130
AF0063 | 2684693-17,2684693-25 | 5094-OB8XT, 8 DISCRETE OUTPUT | PNL B,SMT130
AF0064 | 2684693-17,2684693-23 | 5094-IB16XT, 16 DISCRETE INPUT | PNL B,SMT130
AF0065 | 2684693-18,2684693-30 | 5094-IF4IHSXT, 4 ANALOG INPUT, S | PNL B,SMT130
AF0066 | 2684693-21,2684693-36 | 5094-IRT8SXT, 8 RTD/TC ANALOG INPUT, S | PNL B,SMT130
AF0067 | 2684693-18,2684693-30 | 5094-IF4IHSXT, 4 ANALOG INPUT, S | PNL B,SMT130
AF0068 | 2684693-18,2684693-27 | 5094-OF8IHXT, 8 ANALOG OUTPUT, ISOLATED | PNL B,SMT130
AF0071 | 2684693-18,2684693-32 | 5094-IJ2ISXT, 2 FAST COUNTER INPUT, S | PNL B,SMT130
AF0072 | 2684693-18,2684693-56 | 5094-IF8IHXT, 8 ANALOG INPUT, ISOLATED | PNL B,SMT130
AF0073 | 2684693-18,2684693-30 | 5094-IF4IHSXT, 4 ANALOG INPUT, S | PNL B,SMT130
AF0074 | 2684693-21,2684693-36 | 5094-IRT8SXT, 8 RTD/TC ANALOG INPUT, S | PNL B,SMT130
AF0075 | 2684693-18,2684693-55 | 5094-OB16SXT, 16 DISCRETE OUTPUT, S | PNL B,SMT130
AF0400 | 1322418-31,1322418-40,1322418-72,1322418-73 | 1444-TSCX02-02RB, 2-CH TACHOMETER INPUT^DYNAMIX 1444 VIBRATION | PNL B,SMT130
AF0410 | 1322418-11,1322418-20,1322418-70,1322418-71 | 1444-DYN04-01RA, 4-CH VIBRATION INPUT^DYNAMIX 1444 VIBRATION | PNL B,SMT130
AF0420 | 1322418-11,1322418-20,1322418-70,1322418-71 | 1444-DYN04-01RA, 4-CH VIBRATION INPUT^DYNAMIX 1444 VIBRATION | PNL B,SMT130
AF0450 | 1322418-11,1322418-20,1322418-70,1322418-71 | 1444-DYN04-01RA, 4-CH VIBRATION INPUT^DYNAMIX 1444 VIBRATION | PNL B,SMT130
AU0060 | 2684693-22 | 5094-AENTRXT, FLEX 5000 I/O | PNL B,SMT130
AU0070 | 2684693-22 | 5094-AENTRXT, FLEX 5000 I/O | PNL B,SMT130
FU0060 | 1043265-5 | FUSE, 10A | PNL B,SMT130
FU0061 | 1043265-1,1043265-5 | FUSE, 10A | PNL B,SMT130
FU0062 | 1043265-5 | FUSE, 10A | PNL B,SMT130
FU0063 | 1043265-5 | FUSE, 10A | PNL B,SMT130
FU0064 | 1043265-5 | FUSE, 10A | PNL B,SMT130
FU0070 | 1043265-5 | FUSE, 10A | PNL B,SMT130
FU0071 | 1043265-1,1043265-5 | FUSE, 10A | PNL B,SMT130
FU0110 | 1043265-1,1043265-7 | FUSE, 20A | PNL B,SMT130
FU0113 | 1043265-1,1043265-4 | FUSE, 5A | PNL B,SMT130
FU0210 | 1043265-7 | FUSE, 20A | PNL B,SMT130
FU0211 | 1043265-1,1043265-4 | FUSE, 5A | PNL B,SMT130
FU0212 | 1043265-3 | FUSE, 2A | PNL B,SMT130
FU0213 | 1043265-4 | FUSE, 5A | PNL B,SMT130
GR0233 | 903849C1 | RAIL GROUND, DIN RAIL GROUNDING | PNL B,SMT130
GR0244 | 903849C1 | RAIL GROUND, DIN RAIL GROUNDING | PNL B,SMT130
GR0251 | 903849C1 | RAIL GROUND, DIN RAIL GROUNDING | PNL B,SMT130
IEG0230 | 232941-300 | BUS BAR, PANEL B - INSTRUMENT EARTH GROUNDING | PNL B,SMT130
KA0231 | 1061979-1 | RELAY, CONTROLLER ACTIVE | PNL B,SMT130
KA0232 | 1061979-1 | RELAY, CONTROLLER ACTIVE | PNL B,SMT130
KA0233 | 1061979-1 | RELAY, CONTROLLER ACTIVE | PNL B,SMT130
KA0234 | 1061979-1 | RELAY, CONTROLLER ACTIVE | PNL B,SMT130
KA0235 | 1061979-1 | RELAY, NO EMERGENCY SHUTDOWN SUMMARY | PNL B,SMT130
KA0236 | 1061979-1 | RELAY, NO EMERGENCY SHUTDOWN SUMMARY | PNL B,SMT130
KA0237 | 1061979-1 | RELAY, NO EMERGENCY SHUTDOWN SUMMARY | PNL B,SMT130
KA0238 | 1061979-1 | RELAY, NO EMERGENCY SHUTDOWN SUMMARY | PNL B,SMT130
KA0239 | 1061979-1 | RELAY, NO EMERGENCY SHUTDOWN SUMMARY | PNL B,SMT130
KA0240 | 1061979-1 | RELAY, NO EMERGENCY SHUTDOWN SUMMARY | PNL B,SMT130
KA0241 | 1061979-1 | RELAY, BACKUP SYSTEM RESET | PNL B,SMT130
KA0242 | 1061979-1 | RELAY, BACKUP SYSTEM RESET | PNL B,SMT130
KA0243 | 1061979-1 | RELAY, NO FIRE DETECTED | PNL B,SMT130
KA0244 | 1061979-1 | RELAY, NO FIRE DETECTED | PNL B,SMT130
KA0245 | 1061979-1 | RELAY, NO GAS DETECTED | PNL B,SMT130
KA0246 | 1061979-1 | RELAY, NO FIRE DETECTED | PNL B,SMT130
KA0247 | 1061979-1 | RELAY, NO FIRE DETECTED | PNL B,SMT130
KA0248 | 1061979-1 | RELAY, NO EMERGENCY SHUTDOWN SUMMARY | PNL B,SMT130
KA0249 | 1061979-1 | RELAY, NO GAS DETECTED | PNL B,SMT130
KA0250 | 1061979-1 | RELAY, NO EMERGENCY SHUTDOWN SUMMARY | PNL B,SMT130
KA0260 | 1061979-1 | RELAY, NO MV FIRE DETECTED | PNL B,SMT130
KA1020 | 1061979-1 | RELAY, IGNITION START | PNL B,SMT130
UA1200 | 1053834-11 | BUOS MODULE, BACKUP OVERSPEED | PNL B,SMT130
XT0060 | 1066730-7,1066730-8,1067996-4 | TERMINAL BLOCK, SPRING, 4 CONDUCTOR,30-12 AWG (0.05-3.31 MM2),NON-IS | PNL B,SMT130
XT0070 | 1066730-7,1066730-8,1067996-4 | TERMINAL BLOCK, SPRING, 4 CONDUCTOR,30-12 AWG (0.05-3.31 MM2),NON-IS | PNL B,SMT130
XT0110 | 1066730-7,1066730-8,1067996-4 | TERMINAL BLOCK, SPRING, 4 CONDUCTOR,30-12 AWG (0.05-3.31 MM2),NON-IS | PNL B,SMT130
XT0233 | 1066730-7,1066730-8,1067996-4 | TERMINAL BLOCK, SPRING, 4 CONDUCTOR,30-12 AWG (0.05-3.31 MM2),NON-IS | PNL B,SMT130
XT0235 | 1066730-7 | TERMINAL BLOCK, SPRING, 4 CONDUCTOR,30-12 AWG (0.05-3.31 MM2),NON-IS | PNL B,SMT130
XT0237 | 1066730-8,1066730-9,1067996-4 | DIODE TERMINAL STRIP, 4 CONDUCTOR | PNL B,SMT130
XT0240 | 1066730-7,1066730-8,1067996-4 | TERMINAL BLOCK, SPRING, 4 CONDUCTOR,30-12 AWG (0.05-3.31 MM2),NON-IS | PNL B,SMT130
XT0400 | 1066730-1,1066730-2,1067996-4 | TERMINAL STRIP, 4 CONDUCTOR | PNL B,SMT130
AT0190 | 1577354-5100 | WORKSTATION, PANEL COMPUTER, TT4000 | PNL,DOOR,2-BAY
AT0190K | 1068334 | KEYBOARD, TYPING INTERFACE | PNL,DOOR,2-BAY
HA0273 | 1113568-200 | HORN, AUDIBLE ALARM | PNL,DOOR,2-BAY
KA0461 | 1021502 | RELAY, LOCKOUT WITH MANUAL RESET | PNL,DOOR,2-BAY
SB6500 | 2380746-1 | PUSHBUTTON SWITCH, SMOKE DETECTOR RESET | PNL,DOOR,2-BAY
BA0700 | 2127397-1 | SWITCH, ETHERNET, MANAGED | POWERDIST, PANEL
BA0701 | 1901587-1 | MODULE, TIME SYNC | POWERDIST, PANEL
BA0703 | 2127397-2 | WIRELESS BRIDGE, HMI WIFI | POWERDIST, PANEL
FU0010 | 1043265-5 | FUSE, 10A | POWERDIST, PANEL
FU0011 | 1043265-7 | FUSE, 20A | POWERDIST, PANEL
FU0136 | 1043265-9 | FUSE, 30A | POWERDIST, PANEL
FU0460 | 1043265-5 | FUSE, 10A | POWERDIST, PANEL
FU0500 | 1043265-7 | FUSE, 20A | POWERDIST, PANEL
FU2700 | 1043265-4 | FUSE, 5A | POWERDIST, PANEL
FU2701 | 1043265-4 | FUSE, 5A | POWERDIST, PANEL
FU2703 | 1043265-4 | FUSE, 5A | POWERDIST, PANEL
GR0144 | 903849C1 | RAIL GROUND, DIN RAIL GROUNDING | POWERDIST, PANEL
GR0145 | 903849C1 | RAIL GROUND, DIN RAIL GROUNDING | POWERDIST, PANEL
GR0146 | 903849C1 | RAIL GROUND, DIN RAIL GROUNDING | POWERDIST, PANEL
IEG2240 | 232941-300 | BUS BAR, POWER DISTRIBUTION - INSTRUMENTATION GROUNDING | POWERDIST, PANEL
UJ0131 | 1286570-1 | POWER CONVERTER, AC/DC INPUT TO 28V DC OUTPUT | POWERDIST, PANEL
XT0011 | 1066730-16 | TERMINAL STRIP, 2 CONDUCTOR | POWERDIST, PANEL
XT0027 | 1066730-7 | TERMINAL BLOCK, SPRING, 4 CONDUCTOR,30-12 AWG (0.05-3.31 MM2),NON-IS | POWERDIST, PANEL
XT0102 | 1066730-16 | TERMINAL STRIP, 2 CONDUCTOR | POWERDIST, PANEL
XT0104 | 1066730-16 | TERMINAL STRIP, 2 CONDUCTOR | POWERDIST, PANEL
FU0190 | 1043265-5 | FUSE, 10A | PWR DST,DR,SMT130
FU0200 | 1043265-5 | FUSE, 10A | PWR DST,DR,SMT130
FU0201 | 1043265-5 | FUSE, 10A | PWR DST,DR,SMT130
FU0273 | 1043265-4 | FUSE, 5A | PWR DST,DR,SMT130
FU0560 | 1043265-7 | FUSE, 20A | PWR DST,DR,SMT130
FU0701 | 1043265-4 | FUSE, 5A | PWR DST,DR,SMT130
FU2610 | 1043265-1,1043265-3 | FUSE, 2A | PWR DST,DR,SMT130
FU2620 | 1043265-1,1043265-3 | FUSE, 2A | PWR DST,DR,SMT130
XT0561 | 1066730-7 | TERMINAL BLOCK, SPRING, 4 CONDUCTOR,30-12 AWG (0.05-3.31 MM2),NON-IS | PWR DST,DR,SMT130
XT0562 | 1066730-7 | TERMINAL BLOCK, SPRING, 4 CONDUCTOR,30-12 AWG (0.05-3.31 MM2),NON-IS | PWR DST,DR,SMT130
XT0563 | 1066730-7 | TERMINAL BLOCK, SPRING, 4 CONDUCTOR,30-12 AWG (0.05-3.31 MM2),NON-IS | PWR DST,DR,SMT130
XT2930 | 1066730-7 | TERMINAL BLOCK, SPRING, 4 CONDUCTOR,30-12 AWG (0.05-3.31 MM2),NON-IS | PWR DST,DR,SMT130
AF0201 | PARTOFTCPASSY | 5094-IB32XT, 32 DISCRETE INPUT | TCP, SMT130
AF0202 | PARTOFTCPASSY | 5094-OB32XT, 32 DISCRETE OUTPUT | TCP, SMT130
AU0200 | PARTOFTCPASSY | 5094-AENTRXT, FLEX 5000 I/O | TCP, SMT130
GR0200 | PARTOFTCPASSY | RAIL LUG, DIN RAIL GROUNDING | TCP, SMT130
HL0400 | PARTOFTCPASSY | LIGHT, READY, GREEN | TCP, SMT130
HL0401 | PARTOFTCPASSY | LIGHT, STARTING, WHITE | TCP, SMT130
HL0402 | PARTOFTCPASSY | LIGHT, READY TO LOAD, WHITE | TCP, SMT130
HL0403 | PARTOFTCPASSY | LIGHT, ON LOAD, WHITE | TCP, SMT130
HL0404 | PARTOFTCPASSY | LIGHT, SPARE, WHITE | TCP, SMT130
HL0405 | PARTOFTCPASSY | LIGHT, LOCAL/AUXILIARY SELECT, WHITE | TCP, SMT130
HL0406 | PARTOFTCPASSY | LIGHT, SPARE, WHITE | TCP, SMT130
HL0407 | PARTOFTCPASSY | LIGHT, COOLDOWN, WHITE | TCP, SMT130
HL0408 | PARTOFTCPASSY | LIGHT, STOPPING, WHITE | TCP, SMT130
HL0409 | PARTOFTCPASSY | LIGHT, ALARM SUMMARY, AMBER | TCP, SMT130
HL0410 | PARTOFTCPASSY | LIGHT, BACKUP ACTIVE, AMBER | TCP, SMT130
HL0411 | PARTOFTCPASSY | LIGHT, SHUTDOWN SUMMARY, RED | TCP, SMT130
SA0400 | PARTOFTCPASSY | SELECTOR SWITCH, OFF/LOCAL/AUXILIARY | TCP, SMT130
SA0401 | PARTOFTCPASSY | SELECTOR SWITCH, BACKUP SYSTEM RESET | TCP, SMT130
SB0400 | PARTOFTCPASSY | PUSHBUTTON SWITCH, EMERGENCY STOP | TCP, SMT130
SB0401 | PARTOFTCPASSY | PUSHBUTTON SWITCH, HORN SILENCE | TCP, SMT130
SB0402 | PARTOFTCPASSY | PUSHBUTTON SWITCH, ACKNOWLEDGE | TCP, SMT130
SB0403 | PARTOFTCPASSY | PUSHBUTTON SWITCH, RESET | TCP, SMT130
SB0404 | PARTOFTCPASSY | PUSHBUTTON SWITCH, LAMP TEST | TCP, SMT130
SB0405 | PARTOFTCPASSY | PUSHBUTTON SWITCH, START | TCP, SMT130
SB0406 | PARTOFTCPASSY | PUSHBUTTON SWITCH, NORMAL STOP | TCP, SMT130
SB0407 | PARTOFTCPASSY | PUSHBUTTON SWITCH, SPEED/LOAD DECREASE | TCP, SMT130
SB0408 | PARTOFTCPASSY | PUSHBUTTON SWITCH, SPEED/LOAD INCREASE | TCP, SMT130
SH0400 | PARTOFTCPASSY | LIGHTED SWITCH, SPARE, WHITE | TCP, SMT130
SH0401 | PARTOFTCPASSY | LIGHTED SWITCH, SPARE, WHITE | TCP, SMT130
SH0404 | PARTOFTCPASSY | LIGHTED SWITCH, SPARE, WHITE | TCP, SMT130
SH0405 | PARTOFTCPASSY | LIGHTED SWITCH, SPARE, WHITE | TCP, SMT130
SH0408 | PARTOFTCPASSY | LIGHTED SWITCH, SPARE, WHITE | TCP, SMT130
SH0409 | PARTOFTCPASSY | LIGHTED SWITCH, SPARE, WHITE | TCP, SMT130
SH0410 | PARTOFTCPASSY | LIGHTED SWITCH, SPARE, WHITE | TCP, SMT130
SH0411 | PARTOFTCPASSY | LIGHTED SWITCH, VOLTAGE DECREASE SELECT, WHITE | TCP, SMT130
SH0412 | PARTOFTCPASSY | LIGHTED SWITCH, VOLTAGE INCREASE SELECT, WHITE | TCP, SMT130
XT0564 | PARTOFTCPASSY | TERMINAL STRIP, SYSTEM FUNCTION (USE) | TCP, SMT130
GR1000 | 903849C1 | RAIL GROUND, DIN RAIL GROUNDING | TURBINE CONTROL^JB70
GR1100 | 903849C1 | RAIL GROUND, DIN RAIL GROUNDING | TURBINE CONTROL^JB70
HA0472 | 1103208-101 | HORN, START | TURBINE CONTROL^JB70