## Blue Labels
(SHT 1) CONTROL,JB70;TT6 | (SHT 10) JB72 GEN PANEL | (SHT 11) JB72 VIB PANEL | (SHT 12) JB5 PROX PANEL | (SHT 13) JB1123 FO PANEL | (SHT 14) MCC RAIL | (SHT 2) JB70 LEFT RAIL | (SHT 3) JB70 RIGHT RAIL | (SHT 4) JB70 PLC PANEL | (SHT 5) JB70 PANEL A | (SHT 6) JB70 PANEL B | (SHT 8) JB72 LEFT RAIL | (SHT 9) JB72 RIGHT RAIL
AT1100 | AT0140 | AF0510 | UA1263 | BA0005 | AU0110 | XTFGA | XT0111 | UV0600 | FU0080 | XT0060 | BA0120 | XTFGC
SB0471 | XT0339 | AF0500 | UA1211 | BA0006 | AF0111 | GR0431 | XTFGB | AT0600 | FU0081 | KA0235 | BA0121 | GR0141
SB0473 | KA0123 | FU0510 | UA1210 | GR1123 | AF0112 |  | GR0532 | AP0601 | FU0137 | KA0237 | XT0180
SB0474 | KA0310 | XT0501 | UA1262 | FU1123 | AF0113 |  |  | AP0602 | FU0090 | KA0221 | XT1207
SH0470 | XT0354 | XT0500 | UA1221 | FU1124 | AF0114 |  |  | AP0603 | XT0080 | KA0222 | FU0133
SH0471 | XT0370 |  | UA1220 | XT1123 | IEG0257 |  |  | AP0604 | AU0080 | FU0100 | FU0134
SH0472 | XT0336 |  | UA1231 | GR1125 | BA0110 |  |  | AP0607 | AF0081 | FU0210 | FU0180
SA0472 | XT0335 |  | UA1230 | IEG1123 | BA0111 |  |  | AP0608 | AF0082 | FU0070 | FU0181
SA0471 | FU0120 |  | GR1210 |  | BA0112 |  |  | AR0600 | AF0083 | FU0076 | FU0182
SA0473 | FU0121 |  | UA1520 |  | FU0110 |  |  | AP0605 | AU0090 | KA1020 | KA0180
HA0472 | FU0122 |  | XT1521 |  | FU0111 |  |  | AP0606 | AF0091 | KA0233 | KA0185
SB0472 | FU0332 |  | XTFGH |  | FU1110 |  |  | AP0609 | AF0092 | KA0234 | KA0181
| FU0334 |  | GR1211 |  | FU1111 |  |  | AT0680 | AF0093 | KA0251 | KA0182
| GR0145 |  |  |  | FU1112 |  |  | XT0680 | AF0094 | KA0224 | KA0183
| XT0350 |  |  |  | XT0100 |  |  | FU0680 | AF0095 | XT0224 | XT0181
| XT0351 |  |  |  | XT1124 |  |  | BA0001 | KA2160 | AU0070 | AF0185
| XT0352 |  |  |  | KA7000 |  |  | BA0002 | KA2161 | AF0071 | AF0184
| XT0353 |  |  |  | KA7001 |  |  | FU0010 | KA3330 | AF0072 | AF0183
| XT0355 |  |  |  | KA7002 |  |  | FU0021 | KA3331 | AF0073 | AF0182
| KA4100 |  |  |  | KA7003 |  |  | FU0022 | GR0133 | AF0074 | AF0181
| KA3420 |  |  |  | KA7004 |  |  | GR0234 | FU0139 | AF0075 | AU0180
| GR0144 |  |  |  | KA7005 |  |  |  | FU0387 | AF0076 | GR0241
| KA0335 |  |  |  | KA7006 |  |  |  | FU0388 | FU1100
| KA0336 |  |  |  | KA7007 |  |  |  | FU0389 | FU1101
| FU0333 |  |  |  | KA7008 |  |  |  | XT0089 | BA1100
| XT0338 |  |  |  | KA7009 |  |  |  | KT0140 | UV0291
| KA0121 |  |  |  | KA7010 |  |  |  | KT0141 | FU0291
| KA0128 |  |  |  | KA7011 |  |  |  | KT0142 | GR0233
| KA0330 |  |  |  | KA7012 |  |  |  | KT0143 | PC0470
| KA0331 |  |  |  | KA7013 |  |  |  | KT0144 | XT0062
| KA0332 |  |  |  | GR0257 |  |  |  | KT0145 | FU0212
| KA0333 |  |  |  | IEG0110 |  |  |  | KT0146 | FU0113
| XT0337 | [7 empty] | KA0130 | FU0114
| GR0143 | [7 empty] | KA0131 | FU0115
| IEG0140 | [7 empty] | KA0132 | FU0060
| XT0120 | [7 empty] | KA0133 | FU0061
| XT0525 | [7 empty] | KA0134 | FU0062
| KA7610 | [7 empty] | KA0136 | FU0063
| GR0142 | [7 empty] | KA0137 | FU0064
| KA0313 | [7 empty] | KA0138 | AF0068
| KA0314 | [7 empty] | KA0141 | AF0067
| AF0123 | [7 empty] | KA0231 | AF0066
| AF0122 | [7 empty] | KA0236 | AF0065
| AF0121 | [7 empty] | KA0239 | AF0064
| AU0120 | [7 empty] | KA0241 | AF0063
| PEG0140 | [7 empty] | KA0242 | AF0062
[9 empty] | KA0243 | AF0061
[9 empty] | KA0244 | AU0060
[9 empty] | KA0245 | GR0231
[9 empty] | KA0230 | XT0400
[9 empty] | KA0232 | XT0401
[9 empty] | KA0240 | FU0410
[9 empty] | XT0237 | AF0400
[9 empty] | XT0084 | AF0410
[9 empty] | GR0135 | AF0420
[9 empty] | FU0011 | AF0450
[9 empty] | XT0011 | BA0003
[9 empty] | XT0012 | BA0011
[9 empty] | FU0012 | XT0051
[9 empty] | FU0013 | FU0023
[9 empty] | FU0014 | FU0031
[9 empty] | FU0015 | GR0341
[9 empty] | FU0016 | IEG0230
FU0017
FU0018
GR0131
AF0087
AF0086
AF0085
AF0084
XT0081
XT0082
XT0050
FU0091
FU0092
FU0093
FU0094
GR0134
XT0003
XT0002
FU0136
KA0135
KA3103
GR0132
WC0080
UJ0131
XT0014
UA1200
PEG0130
IEG0010

## White Labels
(SHT 1) CONTROL,JB70;TT6 - (SHT 5) JB70 PANEL A | (SHT 13) JB1123 FO PANEL | (SHT 12) JB5 PROX PANEL | (SHT 5) JB70 PANEL A | (SHT 5) JB70 PANEL A - (SHT 6) JB70 PANEL B | (SHT 6) JB70 PANEL B | (SHT 6) JB70 PANEL B - (SHT 4) JB70 PLC PANEL | (SHT 4) JB70 PLC PANEL | (SHT 10) JB72 GEN PANEL | (SHT 10) JB72 GEN PANEL - (SHT 8) JB72 LEFT RAIL | (SHT 10) JB72 GEN PANEL - (SHT 11) JB72 VIB PANEL | (SHT 8) JB72 LEFT RAIL | (SHT 11) JB72 VIB PANEL | (SHT 14) MCC RAIL
AT1100G | GR1125 | GR1211 | 0V | IEG00104 | AF0064G | IEG02306 | UV0600G | AT0140LS(S) | IEG014008 | IEG01406 | AF0184SH | XT05001 | AU0110G
| IEG11231 |  | AF0083G | IEG02300 | AF0065G | IEG02307 |  | GR0142 | IEG01401 |  | AU0180G |  | IEG02571
|  |  | AF0084G |  | AF0066G |  |  | IEG01405 |  |  |  |  | IEG02572
|  |  | AF0085G |  | AF0071G |  |  | PEG01404 |  |  |  |  | IEG02573
|  |  | AU0080G |  | AF0072G
|  |  | AU0090G |  | AF0073G
|  |  | IEG001012 |  | AF0074G
|  |  | IEG001013 |  | AU0060G
|  |  | IEG00102 |  | AU0070G
|  |  | IEG00106 |  | IEG02301
|  |  | IEG00108 |  | IEG023011
IEG02303
IEG02304
IEG02308
XT04001
XT04002

## Heat Shrink Labels
(SHT 5) JB70 PANEL A - (SHT 6) JB70 PANEL B | (SHT 10) JB72 GEN PANEL | (SHT 10) JB72 GEN PANEL - (SHT 11) JB72 VIB PANEL
WC4524 | WC8009 | WC1242
WC1243
WC1244
WC1245
WC1246

## CONTROL,JB70;TT6
CONTROL,JB70;TT6
Project # | 4M082
Project Name | STEEL REEF BURKE LLC
Revision | C
Controls DE | J. UNGER
Phone:
Controls ME
Phone:
From | [5 empty] | To
Device ID | Cable (W) Conductor (SC) Jumper Clip (JC) | Wire No. | Wire ID | Gauge/Size | Page/Zone | Device ID | Location | Page/Zone
AT1100:GND | SC | AT1100G | GRN/YEL | 14 | 39.D3 | PEG0130:2 | JB70 PANEL A | 39.D5
SA0471:B1-13 | SC | SA0471B113 | WHT | 20 | 41.B1 | AF0087:40 | JB70 PANEL A | 41.B7
SA0471:B1-14 | SC | SA0471B114 | WHT | 20 | 41.B1 | AF0087:08 | JB70 PANEL A | 41.B7
SA0471:B2-13 | SC | SA0471B213 | WHT | 20 | 41.A1 | AF0087:39 | JB70 PANEL A | 41.A7
SA0471:B2-14 | SC | SA0471B214 | WHT | 20 | 41.A1 | AF0087:07 | JB70 PANEL A | 41.A7
SA0472:B1-13 | SC | SA0472B113 | WHT | 20 | 44.C1 | AF0091:47 | JB70 PANEL A | 44.C7
SA0472:B1-14 | SC | SA0472B114 | WHT | 20 | 44.C1 | AF0091:15 | JB70 PANEL A | 44.C7
SA0472:B2-13 | SC | SA0472B213 | WHT | 20 | 44.C1 | AF0091:46 | JB70 PANEL A | 44.C7
SA0472:B2-14 | SC | SA0472B214 | WHT | 20 | 44.C1 | AF0091:14 | JB70 PANEL A | 44.C7
SA0473:11 | SC | SA047311 | WHT | 20 | 42.D1 | AF0087:37 | JB70 PANEL A | 42.D7
SA0473:12 | SC | SA047312 | WHT | 20 | 42.D1 | AF0087:05 | JB70 PANEL A | 42.D7
SA0473:13 | SC | SA047313 | WHT | 20 | 42.D1 | AF0087:38 | JB70 PANEL A | 42.D7
SA0473:14 | SC | SA047314 | WHT | 20 | 42.D1 | AF0087:06 | JB70 PANEL A | 42.D7
SB0471:11 | SC | SB047111 | WHT | 20 | 40.D1 | AF0087:34 | JB70 PANEL A | 40.D7
SB0471:12 | SC | SB047112 | WHT | 20 | 40.D1 | AF0087:02 | JB70 PANEL A | 40.D7
SB0472:B2-11 | SC | SB0472B211 | WHT | 20 | 41.B1 | AF0081:36 | JB70 PANEL A | 41.B7
SB0472:B2-12 | SC | SB0472B212 | WHT | 20 | 41.B1 | AF0081:04 | JB70 PANEL A | 41.B7
SB0473:13 | SC | SB047313 | WHT | 20 | 40.D1 | AF0087:35 | JB70 PANEL A | 40.D7
SB0473:14 | SC | SB047314 | WHT | 20 | 40.D1 | AF0087:03 | JB70 PANEL A | 40.D7
SB0474:13 | SC | SB047413 | WHT | 20 | 41.A1 | AF0087:36 | JB70 PANEL A | 41.A7
SB0474:14 | SC | SB047414 | WHT | 20 | 41.A1 | AF0087:04 | JB70 PANEL A | 41.A7
AT1100:POS | SC | FU1100 | WHT | 14 | 39.D3 | FU1100:LD | JB70 PANEL B | 39.D3
AT1100:L1 | WC0101 | BA1100DEVICE | ENET | CABLE | 39.D3 | BA1100:DEVICE | JB70 PANEL B | 39.D1
AT1100:NEG | SC | 0V | WHT | 14 | 39.D3 | XT0111:22 | JB70 RIGHT RAIL | 39.D6
SB0472:B1-11 | SC | ESTOPB | WHT | 20 | 41.C1 | XT0111:19 | JB70 RIGHT RAIL | 41.C5
SB0472:B1-12 | SC | ESTOPA | WHT | 20 | 41.C1 | XT0111:20 | JB70 RIGHT RAIL | 41.C5
SH0470:11 | SC | SH047011 | WHT | 20 | 40.B1 | XT0111:7 | JB70 RIGHT RAIL | 40.B5
SH0470:12 | SC | SH047012 | WHT | 20 | 40.B1 | XT0111:8 | JB70 RIGHT RAIL | 40.B5
SH0470:13 | SC | SH047013 | WHT | 20 | 40.B1 | XT0111:9 | JB70 RIGHT RAIL | 40.B5
SH0470:14 | SC | SH047014 | WHT | 20 | 40.B1 | XT0111:10 | JB70 RIGHT RAIL | 40.B5
SH0470:X1 | SC | SH0470X1 | WHT | 20 | 40.B1 | XT0111:12 | JB70 RIGHT RAIL | 40.C5
SH0470:X2 | SC | SH0470X2 | WHT | 20 | 40.B1 | XT0111:11 | JB70 RIGHT RAIL | 40.B5
SH0471:11 | SC | SH047111 | WHT | 20 | 40.A1 | XT0111:1 | JB70 RIGHT RAIL | 40.A5
SH0471:12 | SC | SH047112 | WHT | 20 | 40.A1 | XT0111:2 | JB70 RIGHT RAIL | 40.A5
SH0471:13 | SC | SH047113 | WHT | 20 | 40.A1 | XT0111:3 | JB70 RIGHT RAIL | 40.A5
SH0471:14 | SC | SH047114 | WHT | 20 | 40.A1 | XT0111:4 | JB70 RIGHT RAIL | 40.A5
SH0471:X1 | SC | SH0471X1 | WHT | 20 | 40.A1 | XT0111:6 | JB70 RIGHT RAIL | 40.A5
SH0471:X2 | SC | SH0471X2 | WHT | 20 | 40.A1 | XT0111:5 | JB70 RIGHT RAIL | 40.A5
SH0472:11 | SC | SH047211 | WHT | 20 | 40.C1 | XT0111:13 | JB70 RIGHT RAIL | 40.C5
SH0472:12 | SC | SH047212 | WHT | 20 | 40.C1 | XT0111:14 | JB70 RIGHT RAIL | 40.C5
SH0472:13 | SC | FU0139 | WHT | 20 | 40.C1 | XT0111:15 | JB70 RIGHT RAIL | 40.C5
SH0472:14 | SC | KA0241A1 | WHT | 20 | 40.C1 | XT0111:16 | JB70 RIGHT RAIL | 40.C5
SH0472:X1 | SC | SH0472X1 | WHT | 20 | 40.C1 | XT0111:18 | JB70 RIGHT RAIL | 40.C5
SH0472:X2 | SC | SH0472X2 | WHT | 20 | 40.C1 | XT0111:17 | JB70 RIGHT RAIL | 40.C5
HA0472:BLK-1 | WC5072 | HA047201 | 1 | 18 | 43.A1 | XT0111:24 | JB70 RIGHT RAIL | 43.A5
HA0472:BLK-2 | WC5072 | HA047202 | 2 | 18 | 43.A1 | XT0111:23 | JB70 RIGHT RAIL | 43.A5
SolarTools ver. 24.0.84.24712 (Jul 31, 2025)
Report date: 2/27/2026 8:31 AM

## JB1123 FO PANEL
JB1123 FO PANEL
Project # | 4M082
Project Name | STEEL REEF BURKE LLC
Revision | C
Controls DE | J. UNGER
Phone:
Controls ME
Phone:
From | [5 empty] | To
Device ID | Cable (W) Conductor (SC) Jumper Clip (JC) | Wire No. | Wire ID | Gauge/Size | Page/Zone | Device ID | Location | Page/Zone
BA0005:V1(-) | SC | 0V | WHT | 16 | 8.A1 | XT1123:2 | JB1123 FO PANEL | 8.A3
BA0005:V1(+) | SC | FU1123 | WHT | 16 | 8.A1 | FU1123:LD | JB1123 FO PANEL | 8.A2
BA0006:V1(-) | SC | 0V | WHT | 16 | 8.A1 | XT1123:2 | JB1123 FO PANEL | 8.A3
BA0006:V1(+) | SC | FU1124 | WHT | 16 | 8.A1 | FU1124:LD | JB1123 FO PANEL | 8.B2
FU1123:LI | SC | FU0136 | WHT | 16 | 8.A2 | XT1123:1 | JB1123 FO PANEL | 8.A3
FU1124:LI | SC | FU0136 | WHT | 16 | 8.B2 | XT1123:1 | JB1123 FO PANEL | 8.A3
GR1123: | SC | IEG11231 | GRN | 14 | 9.D4 | IEG1123:1 | JB1123 FO PANEL | 9.D3
GR1125: | SC | GR1125 | GRN/YEL | 14 | 9.D4 | FG1125:1 | JB1123 FO PANEL | 9.D4
SolarTools ver. 24.0.84.24712 (Jul 31, 2025)
Report date: 2/27/2026 8:31 AM

## JB5 PROX PANEL
JB5 PROX PANEL
Project # | 4M082
Project Name | STEEL REEF BURKE LLC
Revision | C
Controls DE | J. UNGER
Phone:
Controls ME
Phone:
From | [5 empty] | To
Device ID | Cable (W) Conductor (SC) Jumper Clip (JC) | Wire No. | Wire ID | Gauge/Size | Page/Zone | Device ID | Location | Page/Zone
GR1210: | SC | GR1210 | GRN/YEL | 14 | 9.A6 | FRAME | JB5 PROX PANEL | 9.A6
GR1211: | SC | GR1211 | GRN/YEL | 14 | 9.A6 | FG1:88 | JB5 PROX PANEL | 9.A6
SolarTools ver. 24.0.84.24712 (Jul 31, 2025)
Report date: 2/27/2026 8:31 AM

## JB70 LEFT RAIL
JB70 LEFT RAIL
Project # | 4M082
Project Name | STEEL REEF BURKE LLC
Revision | C
Controls DE | J. UNGER
Phone:
Controls ME
Phone:
From | [5 empty] | To
Device ID | Cable (W) Conductor (SC) Jumper Clip (JC) | Wire No. | Wire ID | Gauge/Size | Page/Zone | Device ID | Location | Page/Zone
GR0431: | SC | GR0431 | GRN/YEL | 14 | 9.B2 | FRAME | JB70 LEFT RAIL | 9.B2
Report date: 2/27/2026 8:31 AM |  |  |  |  | SolarTools ver. 24.0.84.24712 (Jul 31, 2025)

## JB70 PANEL A
JB70 PANEL A
Project # | 4M082
Project Name | STEEL REEF BURKE LLC
Revision | C
Controls DE | J. UNGER
Phone:
Controls ME
Phone:
From | [5 empty] | To
Device ID | Cable (W) Conductor (SC) Jumper Clip (JC) | Wire No. | Wire ID | Gauge/Size | Page/Zone | Device ID | Location | Page/Zone
XT0002:1 | JC | FU0136 | CLIP | --- | 11.A4 | XT0002:2 | JB70 PANEL A | 11.A4
XT0002:2 | JC | FU0136 | CLIP | --- | 11.A4 | XT0002:3 | JB70 PANEL A | 11.A4
XT0002:3 | JC | FU0136 | CLIP | --- | 11.A4 | XT0002:4 | JB70 PANEL A | 11.A4
XT0002:4 | JC | FU0136 | CLIP | --- | 11.A4 | XT0002:5 | JB70 PANEL A | 11.B4
XT0002:5 | JC | FU0136 | CLIP | --- | 11.B4 | XT0002:6 | JB70 PANEL A | 11.B4
XT0002:6 | JC | FU0136 | CLIP | --- | 11.B4 | XT0002:7 | JB70 PANEL A | 11.B4
XT0002:7 | JC | FU0136 | CLIP | --- | 11.B4 | XT0002:8 | JB70 PANEL A | 11.B4
XT0002:8 | JC | FU0136 | CLIP | --- | 11.B4 | XT0002:9 | JB70 PANEL A | 11.C4
XT0002:9 | JC | FU0136 | CLIP | --- | 11.C4 | XT0002:10 | JB70 PANEL A | 11.C4
XT0003:1 | JC | 0V | CLIP | --- | 11.A4 | XT0003:2 | JB70 PANEL A | 11.A4
XT0003:2 | JC | 0V | CLIP | --- | 11.A4 | XT0003:3 | JB70 PANEL A | 11.A4
XT0003:3 | JC | 0V | CLIP | --- | 11.A4 | XT0003:4 | JB70 PANEL A | 11.B4
XT0003:4 | JC | 0V | CLIP | --- | 11.B4 | XT0003:5 | JB70 PANEL A | 11.B4
XT0003:5 | JC | 0V | CLIP | --- | 11.B4 | XT0003:6 | JB70 PANEL A | 11.B4
XT0003:6 | JC | 0V | CLIP | --- | 11.B4 | XT0003:7 | JB70 PANEL A | 11.B4
XT0003:7 | JC | 0V | CLIP | --- | 11.B4 | XT0003:8 | JB70 PANEL A | 11.C4
XT0003:8 | JC | 0V | CLIP | --- | 11.C4 | XT0003:9 | JB70 PANEL A | 11.C4
XT0003:9 | JC | 0V | CLIP | --- | 11.C4 | XT0003:10 | JB70 PANEL A | 11.C4
XT0012:1 | JC | 523NEG | CLIP | --- | 12.C3 | XT0012:2 | JB70 PANEL A | 12.C3
XT0012:2 | JC | 523NEG | CLIP | --- | 12.C3 | XT0012:3 | JB70 PANEL A | 12.C3
XT0012:3 | JC | 523NEG | CLIP | --- | 12.C3 | XT0012:4 | JB70 PANEL A | 12.C3
XT0080:1 | JC | 0V | CLIP | --- | 19.A1 | XT0080:2 | JB70 PANEL A | 19.D1
XT0080:2 | JC | 0V | CLIP | --- | 19.D1 | XT0080:3 | JB70 PANEL A | 19.D1
XT0080:3 | JC | 0V | CLIP | --- | 19.D1 | XT0080:4 | JB70 PANEL A | 19.D1
XT0080:5 | JC | 0V | CLIP | --- | 20.A6 | XT0080:6 | JB70 PANEL A | 21.A6
XT0080:6 | JC | 0V | CLIP | --- | 21.A6 | XT0080:7 | JB70 PANEL A | 22.A6
XT0080:7 | JC | 0V | CLIP | --- | 22.A6 | XT0080:8 | JB70 PANEL A | 23.A6
XT0081:1 | JC | FU0139 | CLIP | --- | 20.A2 | XT0081:2 | JB70 PANEL A | 21.A2
XT0081:2 | JC | FU0139 | CLIP | --- | 21.A2 | XT0081:3 | JB70 PANEL A | 22.A2
XT0081:3 | JC | FU0139 | CLIP | --- | 22.A2 | XT0081:4 | JB70 PANEL A | 23.A3
XT0081:4 | JC | FU0139 | CLIP | --- | 23.A3 | XT0081:5 | JB70 PANEL A | 23.A3
XT0081:5 | JC | FU0139 | CLIP | --- | 23.A3 | XT0081:6 | JB70 PANEL A | 23.A3
XT0082:1 | JC | 0V | CLIP | --- | 18.A1 | XT0082:2 | JB70 PANEL A | 18.A1
XT0082:2 | JC | 0V | CLIP | --- | 18.A1 | XT0082:3 | JB70 PANEL A | 18.B1
XT0082:3 | JC | 0V | CLIP | --- | 18.B1 | XT0082:4 | JB70 PANEL A | 18.B1
XT0082:4 | JC | 0V | CLIP | --- | 18.B1 | XT0082:5 | JB70 PANEL A | 18.B1
XT0089:6 | JC | ESTOP | CLIP | --- | 23.D5 | XT0089:7 | JB70 PANEL A | 23.D5
XT0089:8 | JC | KA0131A1 | CLIP | --- | 25.D4 | XT0089:9 | JB70 PANEL A | 25.D4
AF0081:00 | SC | UA1200J21 | WHT | 20 | 17.D7 | XT0089:20 | JB70 PANEL A | 17.D5
AF0081:01 | SC | KA024314 | WHT | 20 | 22.D7 | KA0243:14 | JB70 PANEL A | 22.D6
AF0081:02 | SC | KA024514 | WHT | 20 | 22.D7 | KA0245:14 | JB70 PANEL A | 22.D6
AF0081:03 | SC | KA013014 | WHT | 20 | 17.C7 | KA0130:14 | JB70 PANEL A | 17.D6
AF0081:08 | SC | KT014618 | WHT | 20 | 25.B6 | KT0146:18 | JB70 PANEL A | 25.B2
AF0081:09 | SC | KA023914 | WHT | 20 | 23.B6 | KA0239:14 | JB70 PANEL A | 23.B5
AF0081:19 | SC | UA1200J27 | WHT | 20 | 17.C7 | UA1200:J2-7 | JB70 PANEL A | 17.B1
AF0081:24 | SC | KA0131A2 | WHT | 20 | 25.B6 | KA0131:A2 | JB70 PANEL A | 25.C5
AF0081:33 | SC | KA024311 | WHT | 20 | 22.D7 | KA0243:11 | JB70 PANEL A | 22.D6
AF0081:34 | SC | KA024511 | WHT | 20 | 22.D7 | KA0245:11 | JB70 PANEL A | 22.D6
AF0081:35 | SC | KA0130A1 | WHT | 20 | 17.C7 | KA0130:A1 | JB70 PANEL A | 17.C5
XT0089:3 | SC | JP3 | CLIP | -- | 24.B4 | XT0089:2 | JB70 PANEL A | 24.B4
XT0089:5 | SC | JP6 | CLIP | -- | 24.C4 | XT0089:4 | JB70 PANEL A | 24.C4
AF0081:07 | SC | JP2 | VIO | 20 | 24.B6 | AF0081:39 | JB70 PANEL A | 24.B6
XT0089:2 | SC | JP0 | VIO | 20 | 24.B4 | XT0089:1 | JB70 PANEL A | 24.B4
AF0081:40 | SC | KA014124 | WHT | 20 | 25.B6 | KA0141:24 | JB70 PANEL A | 25.B5
AF0081:41 | SC | KA023911 | WHT | 20 | 23.B6 | KA0239:11 | JB70 PANEL A | 23.B5
AF0081:COM | SC | AF0081N | WHT | 16 | 19.A2 | AF0082:COM | JB70 PANEL A | 19.B3
AF0081:COM | SC | AU0080N | WHT | 16 | 19.A2 | AU0080:COM | JB70 PANEL A | 19.A1
AF0081:J | SC | * |  |  | 19.A2 | AF0082:P | JB70 PANEL A | 19.B3
AF0081:V+ | SC | AF0081P | WHT | 16 | 19.A2 | AF0082:V+ | JB70 PANEL A | 19.B3
AF0081:V+ | SC | AU0080P | WHT | 16 | 19.A2 | AU0080:V+ | JB70 PANEL A | 19.A1
AF0082:COM | SC | AF0082N | WHT | 16 | 19.B3 | AF0083:COM | JB70 PANEL A | 19.B3
AF0082:J | SC | * |  |  | 19.B3 | AF0083:P | JB70 PANEL A | 19.B3
AF0082:V+ | SC | AF0082P | WHT | 16 | 19.B3 | AF0083:V+ | JB70 PANEL A | 19.B3
AF0083:COM | SC | AF0083N | WHT | 16 | 19.B3 | AF0084:COM | JB70 PANEL A | 19.B4
AF0083:SH | SC | AF0083G | GRN | 14 | 19.B3 | AF0084:SH | JB70 PANEL A | 19.B4
AF0083:SH | SC | AU0080G | GRN | 14 | 19.B3 | AU0080:GND | JB70 PANEL A | 19.A1
AF0083:V+ | SC | AF0083P | WHT | 16 | 19.B3 | AF0084:V+ | JB70 PANEL A | 19.B4
AF0084:COM | SC | AF0084N | WHT | 16 | 19.B4 | AF0085:COM | JB70 PANEL A | 19.B5
AF0084:J | SC | * |  |  | 19.B4 | AF0085:P | JB70 PANEL A | 19.B5
AF0084:SH | SC | AF0084G | GRN | 14 | 19.B4 | AF0085:SH | JB70 PANEL A | 19.B5
AF0084:V+ | SC | AF0084P | WHT | 16 | 19.B4 | AF0085:V+ | JB70 PANEL A | 19.B5
AF0085:COM | SC | AF0085N | WHT | 16 | 19.B5 | AF0086:COM | JB70 PANEL A | 19.B5
AF0085:J | SC | * |  |  | 19.B5 | AF0086:P | JB70 PANEL A | 19.B5
AF0085:SH | SC | AF0085G | GRN | 14 | 19.B5 | AF0086:SH | JB70 PANEL A | 19.B5
AF0085:V+ | SC | AF0085P | WHT | 16 | 19.B5 | AF0086:V+ | JB70 PANEL A | 19.B5
AF0086:12 | SC | FT21082 | WHT | 20 | 78.C7 | XT0050:2 | JB70 PANEL A | 78.C5
AF0086:28 | SC | 0V | WHT | 16 | 78.C7 | XT0050:3 | JB70 PANEL A | 78.C5
AF0086:60 | SC | FT2108S | WHT | 16 | 78.C7 | XT0050:4 | JB70 PANEL A | 78.C5
AF0086:COM | SC | AF0086N | WHT | 16 | 19.B5 | AF0087:COM | JB70 PANEL A | 19.B6
AF0086:J | SC | * |  |  | 19.B5 | AF0087:P | JB70 PANEL A | 19.B6
AF0086:SH | SC | IEG00102 | GRN | 14 | 19.B5 | IEG0010:2 | JB70 PANEL A | 19.C5
AF0086:V+ | SC | AF0086P | WHT | 16 | 19.B5 | AF0087:V+ | JB70 PANEL A | 19.B6
AF0087:11 | SC | KA013624 | WHT | 20 | 20.D3 | KA0136:24 | JB70 PANEL A | 20.D3
AF0087:43 | SC | KA013621 | WHT | 20 | 20.D3 | KA0136:21 | JB70 PANEL A | 20.D3
AF0091:07 | SC | KA014114 | WHT | 20 | 25.A6 | KA0141:14 | JB70 PANEL A | 25.A5
AF0091:09 | SC | UJ0131OK2 | WHT | 20 | 12.B7 | UJ0131:OK2 | JB70 PANEL A | 12.B4
AF0091:12 | SC | KA0134A1 | WHT | 20 | 20.D5 | KA0134:A1 | JB70 PANEL A | 20.D6
AF0091:39 | SC | KA014111 | WHT | 20 | 25.A6 | KA0141:11 | JB70 PANEL A | 25.A5
AF0091:41 | SC | UJ0131OK1 | WHT | 20 | 12.B7 | UJ0131:OK1 | JB70 PANEL A | 12.B4
AF0091:COM | SC | AF0091N | WHT | 16 | 19.D2 | AF0094:COM | JB70 PANEL A | 19.D4
AF0091:COM | SC | AU0090N | WHT | 16 | 19.D2 | AU0090:COM | JB70 PANEL A | 19.C2
AF0091:J | SC | * |  |  | 19.D2 | AF0092:P | JB70 PANEL A | 19.D3
AF0091:V+ | SC | AF0091P | WHT | 16 | 19.D2 | AF0094:V+ | JB70 PANEL A | 19.D4
AF0091:V+ | SC | AU0090P | WHT | 16 | 19.D2 | AU0090:V+ | JB70 PANEL A | 19.C2
AF0092:01 | SC | 009201 | WHT | 20 | 101.B6 | KA3330:A1 | JB70 PANEL A | 101.B6
AF0092:02 | SC | KA0133A1 | WHT | 20 | 20.B4 | KA0133:A1 | JB70 PANEL A | 20.B6
AF0092:03 | SC | 009203 | WHT | 20 | 101.C6 | KA3331:A1 | JB70 PANEL A | 101.C6
AF0092:04 | SC | KA2160A1 | WHT | 20 | 16.A6 | KA2160:A1 | JB70 PANEL A | 16.A5
AF0092:06 | SC | KA013114 | WHT | 20 | 21.C3 | KA0131:14 | JB70 PANEL A | 21.C4
AF0092:07 | SC | KA2161A1 | WHT | 20 | 16.A6 | KA2161:A1 | JB70 PANEL A | 16.B5
AF0092:08 | SC | KA3103A1 | WHT | 20 | 92.A6 | KA3103:A1 | JB70 PANEL A | 92.A5
AF0092:17 | SC | 009217 | WHT | 20 | 101.B6 | KA3330:A2 | JB70 PANEL A | 101.B6
AF0092:19 | SC | 009219 | WHT | 20 | 101.C6 | KA3331:A2 | JB70 PANEL A | 101.C6
AF0092:20 | SC | KA2160A2 | WHT | 20 | 16.A6 | KA2160:A2 | JB70 PANEL A | 16.A5
AF0092:23 | SC | KA2161A2 | WHT | 20 | 16.A6 | KA2161:A2 | JB70 PANEL A | 16.B5
AF0092:24 | SC | KA3103A2 | WHT | 20 | 92.A6 | KA3103:A2 | JB70 PANEL A | 92.A5
AF0092:45 | SC | KA024022 | WHT | 20 | 40.C7 | KA0240:22 | JB70 PANEL A | 40.C6
AF0092:COM | SC | 0V | WHT | 16 | 19.D3 | XT0080:2 | JB70 PANEL A | 19.D1
AF0092:J | SC | * |  |  | 19.D3 | AF0093:P | JB70 PANEL A | 19.D3
AF0092:V+ | SC | FU0091 | WHT | 16 | 19.D3 | FU0091:LD | JB70 PANEL A | 19.D1
AF0093:COM | SC | 0V | WHT | 16 | 19.D3 | XT0080:3 | JB70 PANEL A | 19.D1
AF0093:J | SC | * |  |  | 19.D3 | AF0094:P | JB70 PANEL A | 19.D4
AF0093:V+ | SC | FU0092 | WHT | 16 | 19.D3 | FU0092:LD | JB70 PANEL A | 19.D1
AF0094:04 | SC | UJ0131VIN | WHT | 20 | 12.A7 | UJ0131:VIN | JB70 PANEL A | 12.B4
AF0094:05 | SC | 0V | WHT | 20 | 12.A7 | XT0082:5 | JB70 PANEL A | 18.B1
AF0094:06 | SC | UJ0131IOUT | WHT | 20 | 12.A7 | UJ0131:IOUT | JB70 PANEL A | 12.B4
AF0094:07 | SC | 0V | WHT | 20 | 12.A7 | XT0082:5 | JB70 PANEL A | 18.B1
AF0094:J | SC | * |  |  | 19.D4 | AF0095:P | JB70 PANEL A | 19.D5
AF0094:SH | SC | IEG00108 | GRN | 14 | 19.D4 | IEG0010:8 | JB70 PANEL A | 19.D4
AF0094:SH | SC | AU0090G | GRN | 14 | 19.D4 | AU0090:GND | JB70 PANEL A | 19.C2
AF0095:COM | SC | 0V | WHT | 16 | 19.D5 | XT0080:4 | JB70 PANEL A | 19.D1
AF0095:V+ | SC | FU0093 | WHT | 16 | 19.D5 | FU0093:LD | JB70 PANEL A | 19.D1
AU0080:COM | SC | 0V | WHT | 16 | 19.A1 | XT0080:1 | JB70 PANEL A | 19.A1
AU0080:V+ | SC | FU0081 | WHT | 16 | 19.A1 | FU0081:LD | JB70 PANEL A | 19.B1
AU0090:COM | SC | 0V | WHT | 16 | 19.C2 | XT0080:2 | JB70 PANEL A | 19.D1
AU0090:V+ | SC | FU0090 | WHT | 16 | 19.C2 | FU0090:LD | JB70 PANEL A | 19.D1
FU0011:LD | SC | UJ0131P | WHT | 12 | 12.B3 | UJ0131:+ | JB70 PANEL A | 12.B4
FU0012:LI | SC | 523POS | --- | BUS | 12.B3 | FU0013:LI | JB70 PANEL A | 12.B3
FU0012:LI | SC | 523POS | --- | BUS | 12.B3 | XT0014:1 | JB70 PANEL A | 12.B2
FU0013:LI | SC | 523POS | --- | BUS | 12.B3 | FU0014:LI | JB70 PANEL A | 12.B3
FU0014:LI | SC | 523POS | --- | BUS | 12.B3 | FU0015:LI | JB70 PANEL A | 12.B3
FU0015:LI | SC | 523POS | --- | BUS | 12.B3 | FU0016:LI | JB70 PANEL A | 12.C3
FU0016:LI | SC | 523POS | --- | BUS | 12.C3 | FU0017:LI | JB70 PANEL A | 12.C3
FU0017:LI | SC | 523POS | --- | BUS | 12.C3 | FU0018:LI | JB70 PANEL A | 12.C3
FU0080:LI | SC | FU0137 | WHT | 12 | 18.A1 | FU0137:LD | JB70 PANEL A | 18.A2
FU0080:LI | SC | FU0137 | WHT | 12 | 18.A1 | FU0139:LI | JB70 PANEL A | 18.A1
FU0081:LI | SC | FU0080 | WHT | 14 | 19.B1 | FU0080:LD | JB70 PANEL A | 18.A1
FU0081:LI | SC | FU0080 | WHT | 14 | 19.B1 | FU0090:LI | JB70 PANEL A | 19.D1
FU0090:LI | SC | FU0080 | WHT | 14 | 19.D1 | FU0091:LI | JB70 PANEL A | 19.D1
FU0091:LI | SC | FU0080 | WHT | 14 | 19.D1 | FU0092:LI | JB70 PANEL A | 19.D1
FU0092:LI | SC | FU0080 | WHT | 14 | 19.D1 | FU0093:LI | JB70 PANEL A | 19.D1
FU0093:LI | SC | FU0080 | WHT | 14 | 19.D1 | FU0094:LI | JB70 PANEL A | 19.D1
FU0136:LD | SC | FU0136 | WHT | 10 | 11.A2 | XT0002:1 | JB70 PANEL A | 11.A4
FU0136:LI | SC | 24V | WHT | 10 | 11.A2 | UJ0131:OUT(+) | JB70 PANEL A | 12.B4
FU0137:LI | SC | FU0136 | WHT | 12 | 18.A2 | XT0002:2 | JB70 PANEL A | 11.A4
FU0139:LD | SC | FU0139 | WHT | 16 | 18.A1 | XT0081:1 | JB70 PANEL A | 20.A2
FU0139:LI | SC | FU0137 | WHT | 12 | 18.A1 | FU0387:LI | JB70 PANEL A | 18.A1
FU0387:LD | SC | FU0387 | WHT | 16 | 18.A1 | XT0089:17 | JB70 PANEL A | 25.A2
FU0387:LI | SC | FU0137 | WHT | 12 | 18.A1 | FU0388:LI | JB70 PANEL A | 18.B1
FU0388:LD | SC | FU0388 | WHT | 16 | 18.B1 | KA0138:14 | JB70 PANEL A | 99.C5
FU0388:LI | SC | FU0137 | WHT | 12 | 18.B1 | FU0389:LI | JB70 PANEL A | 18.B1
FU0389:LD | SC | FU0389 | WHT | 16 | 18.B1 | XT0089:21 | JB70 PANEL A | 17.D5
GR0131: | SC | GR0131 | GRN/YEL | 14 | 9.A4 | FRAME | JB70 PANEL A | 9.A3
GR0132: | SC | GR0132 | GRN/YEL | 14 | 9.A4 | FRAME | JB70 PANEL A | 9.A3
GR0133: | SC | IEG00106 | GRN | 14 | 9.A4 | IEG0010:6 | JB70 PANEL A | 9.A5
GR0134: | SC | IEG001013 | GRN | 14 | 9.A4 | IEG0010:13 | JB70 PANEL A | 9.A5
GR0135: | SC | GR0135 | GRN/YEL | 14 | 9.A4 | FRAME | JB70 PANEL A | 9.A5
IEG0010:12 | SC | IEG001012 | GRN | 16 | 17.D2 | UA1200:J3-4 | JB70 PANEL A | 17.B1
KA0130:A1 | SC | KA0130A1 | WHT | 20 | 17.C5 | KA0130:11 | JB70 PANEL A | 17.D6
KA0130:A2 | SC | UA1200J26 | WHT | 20 | 17.C5 | UA1200:J2-6 | JB70 PANEL A | 17.B1
KA0131:11 | SC | KA0135A1 | WHT | 20 | 21.C4 | KA0135:A1 | JB70 PANEL A | 21.C6
KA0131:12 | SC | KA013112 | WHT | 20 | 21.C4 | KA0137:24 | JB70 PANEL A | 21.C1
KA0131:A1 | SC | KA0131A1 | WHT | 20 | 25.C5 | KA0132:A1 | JB70 PANEL A | 25.C5
KA0131:A1 | SC | KA0131A1 | WHT | 20 | 25.C5 | KA0242:14 | JB70 PANEL A | 25.C3
KA0131:A2 | SC | KA0131A2 | WHT | 20 | 25.C5 | KA0132:A2 | JB70 PANEL A | 25.C5
KA0132:11 | SC | FU0139 | WHT | 20 | 20.A1 | KA0133:11 | JB70 PANEL A | 20.B1
KA0132:11 | SC | FU0139 | WHT | 20 | 20.A1 | XT0081:1 | JB70 PANEL A | 20.A2
KA0132:12 | SC | KT014315 | WHT | 20 | 20.A1 | KT0142:A1 | JB70 PANEL A | 20.A6
KA0132:12 | SC | KT014315 | WHT | 20 | 20.A1 | KA0133:12 | JB70 PANEL A | 20.B1
KA0132:21 | SC | KA0138A1 | WHT | 20 | 20.C3 | KA0138:A1 | JB70 PANEL A | 20.C6
KA0132:22 | SC | KA013222 | WHT | 20 | 20.C3 | KT0141:18 | JB70 PANEL A | 20.C2
KA0132:24 | SC | KA013224 | WHT | 20 | 20.C3 | KA0134:14 | JB70 PANEL A | 20.C1
KA0132:A1 | SC | KA0131A1 | WHT | 20 | 25.C5 | KA0141:A1 | JB70 PANEL A | 25.C5
KA0132:A2 | SC | KA0131A2 | WHT | 20 | 25.C5 | KA0141:A2 | JB70 PANEL A | 25.C5
KA0133:11 | SC | FU0139 | WHT | 20 | 20.B1 | KT0144:A1 | JB70 PANEL A | 20.B6
KA0133:A2 | SC | 0V | WHT | 20 | 20.B6 | KA0136:A2 | JB70 PANEL A | 20.C6
KA0133:A2 | SC | 0V | WHT | 20 | 20.B6 | KT0144:A2 | JB70 PANEL A | 20.B6
KA0134:11 | SC | FU0139 | WHT | 20 | 20.C1 | KT0144:15 | JB70 PANEL A | 20.C1
KA0134:11 | SC | FU0139 | WHT | 20 | 20.C1 | KA0136:11 | JB70 PANEL A | 20.B1
KA0134:A2 | SC | 0V | WHT | 20 | 20.D6 | KT0143:A2 | JB70 PANEL A | 20.D6
KA0135:A1 | SC | KA0135A1 | WHT | 20 | 21.C6 | XT0089:23 | JB70 PANEL A | 21.C5
KA0135:A2 | SC | 0V | WHT | 20 | 21.C6 | KA0137:A2 | JB70 PANEL A | 21.D6
KA0135:A2 | SC | 0V | WHT | 20 | 21.C6 | KT0145:A2 | JB70 PANEL A | 21.B6
KA0136:11 | SC | FU0139 | WHT | 20 | 20.B1 | KT0144:A1 | JB70 PANEL A | 20.B6
KA0136:14 | SC | KA013821 | WHT | 20 | 20.B1 | KA0138:21 | JB70 PANEL A | 20.B2
KA0136:A1 | SC | PS32002 | WHT | 20 | 20.C6 | XT0089:14 | JB70 PANEL A | 95.D5
KA0136:A2 | SC | 0V | WHT | 20 | 20.C6 | KA0138:A2 | JB70 PANEL A | 20.C6
KA0137:11 | SC | FU0139 | WHT | 20 | 20.C1 | KT0140:15 | JB70 PANEL A | 20.C1
KA0137:11 | SC | FU0139 | WHT | 20 | 20.C1 | KT0144:15 | JB70 PANEL A | 20.C1
KA0137:14 | SC | KA013222 | WHT | 20 | 20.C1 | KT0141:18 | JB70 PANEL A | 20.C2
KA0137:14 | SC | KA013222 | WHT | 20 | 20.C1 | KT0144:18 | JB70 PANEL A | 20.C1
KA0137:21 | SC | FU0139 | WHT | 20 | 21.C1 | KA0244:11 | JB70 PANEL A | 21.B1
KA0137:21 | SC | FU0139 | WHT | 20 | 21.C1 | KT0142:15 | JB70 PANEL A | 21.D1
KA0137:24 | SC | KA013112 | WHT | 20 | 21.C1 | AF0087:09 | JB70 PANEL A | 21.C2
KA0137:A1 | SC | KA0137A1 | WHT | 20 | 21.D6 | KT0145:18 | JB70 PANEL A | 21.D1
KA0138:11 | SC | KM3170EP | WHT | 20 | 99.C5 | XT0081:8 | JB70 PANEL A | 99.C5
KA0138:24 | SC | KT0144B1 | WHT | 20 | 20.B2 | KT0144:B1 | JB70 PANEL A | 20.B6
KA0138:A2 | SC | 0V | WHT | 20 | 20.C6 | KT0143:A2 | JB70 PANEL A | 20.D6
KA0141:21 | SC | KT0146A1 | WHT | 20 | 25.B5 | KA0241:21 | JB70 PANEL A | 25.A5
KA0141:21 | SC | KT0146A1 | WHT | 20 | 25.B5 | KT0146:A1 | JB70 PANEL A | 25.B4
KA0141:24 | SC | KA014124 | WHT | 20 | 25.B5 | KA0241:24 | JB70 PANEL A | 25.A5
KA0141:A1 | SC | KA0131A1 | WHT | 20 | 25.C5 | KA0230:A1 | JB70 PANEL A | 25.C5
KA0141:A2 | SC | KA0131A2 | WHT | 20 | 25.C5 | KA0230:A2 | JB70 PANEL A | 25.C5
KA0230:A1 | SC | KA0131A1 | WHT | 20 | 25.C5 | KA0231:A1 | JB70 PANEL A | 25.C5
KA0230:A2 | SC | KA0131A2 | WHT | 20 | 25.C5 | KA0231:A2 | JB70 PANEL A | 25.C5
KA0231:24 | SC | KA023124 | WHT | 20 | 23.C2 | KA0245:21 | JB70 PANEL A | 23.C3
KA0231:A1 | SC | KA0131A1 | WHT | 20 | 25.C5 | KA0232:A1 | JB70 PANEL A | 25.D5
KA0231:A2 | SC | KA0131A2 | WHT | 20 | 25.C5 | KA0232:A2 | JB70 PANEL A | 25.D5
KA0236:11 | SC | FU0139 | WHT | 20 | 23.A2 | XT0081:5 | JB70 PANEL A | 23.A3
KA0236:21 | SC | UA1200J21 | WHT | 20 | 23.C2 | KA0241:11 | JB70 PANEL A | 23.C2
KA0236:24 | SC | KA024114 | WHT | 20 | 23.C2 | KA0241:14 | JB70 PANEL A | 23.C2
KA0239:22 | SC | KA024224 | WHT | 16 | 17.C6 | KA0242:24 | JB70 PANEL A | 17.C5
KA0239:A1 | SC | ESTOP | WHT | 20 | 23.C6 | KA0240:A1 | JB70 PANEL A | 23.C6
KA0239:A2 | SC | 0V | WHT | 20 | 23.C6 | KA0240:A2 | JB70 PANEL A | 23.C6
KA0240:11 | SC | PS32004 | WHT | 20 | 95.D6 | XT0089:15 | JB70 PANEL A | 95.D5
KA0240:14 | SC | UF1300 | WHT | 20 | 95.D6 | XT0084:1 | JB70 PANEL A | 95.D6
KA0241:11 | SC | UA1200J21 | WHT | 20 | 23.C2 | XT0089:20 | JB70 PANEL A | 17.D5
KA0241:14 | SC | KA024114 | WHT | 20 | 23.C2 | KA0231:21 | JB70 PANEL A | 23.C2
KA0241:A1 | SC | KA0241A1 | WHT | 20 | 23.A6 | KA0242:A1 | JB70 PANEL A | 23.B6
KA0241:A1 | SC | KA0241A1 | WHT | 20 | 23.A6 | XT0081:7 | JB70 PANEL A | 23.A3
KA0241:A2 | SC | 0V | WHT | 20 | 23.A6 | KA0242:A2 | JB70 PANEL A | 23.B6
KA0241:A2 | SC | 0V | WHT | 20 | 23.A6 | XT0080:8 | JB70 PANEL A | 23.A6
KA0242:11 | SC | KT014618 | WHT | 20 | 25.C3 | KA0231:11 | JB70 PANEL A | 25.C3
KA0242:11 | SC | KT014618 | WHT | 20 | 25.C3 | KT0146:18 | JB70 PANEL A | 25.B2
KA0242:14 | SC | KA0131A1 | WHT | 20 | 25.C3 | KA0231:14 | JB70 PANEL A | 25.C3
KA0242:21 | SC | KA024221 | WHT | 20 | 17.C5 | XT0237:1 T2 | JB70 PANEL A | 17.C4
KA0243:21 | SC | KA024524 | WHT | 20 | 23.C4 | KA0245:24 | JB70 PANEL A | 23.C3
KA0243:24 | SC | ESTOPD | WHT | 20 | 23.C4 | XT0089:1 | JB70 PANEL A | 24.B4
KA0243:A1 | SC | KA9982C | WHT | 20 | 22.A6 | KA0244:A1 | JB70 PANEL A | 22.B6
KA0243:A1 | SC | KA9982C | WHT | 20 | 22.A6 | XT0089:10 | JB70 PANEL A | 22.A5
KA0243:A2 | SC | 0V | WHT | 20 | 22.A6 | KA0244:A2 | JB70 PANEL A | 22.B6
KA0243:A2 | SC | 0V | WHT | 20 | 22.A6 | XT0080:7 | JB70 PANEL A | 22.A6
KA0244:11 | SC | FU0139 | WHT | 20 | 21.B1 | XT0081:2 | JB70 PANEL A | 21.A2
KA0244:12 | SC | KT0145A1 | WHT | 20 | 21.B1 | KT0145:A1 | JB70 PANEL A | 21.B6
KA0244:A2 | SC | 0V | WHT | 20 | 22.B6 | KA0245:A2 | JB70 PANEL A | 22.C6
KA0245:A1 | SC | KA9984C | WHT | 20 | 22.C6 | XT0089:11 | JB70 PANEL A | 22.C5
KT0140:16 | SC | KT014115 | WHT | 20 | 20.C1 | KT0141:15 | JB70 PANEL A | 20.C2
KT0140:18 | SC | KT0143A1 | WHT | 20 | 20.D1 | KT0143:A1 | JB70 PANEL A | 20.D6
KT0140:A1 | SC | KT0140A1 | WHT | 20 | 20.A6 | KT0143:16 | JB70 PANEL A | 20.A5
KT0140:A2 | SC | 0V | WHT | 20 | 20.A6 | KT0141:A2 | JB70 PANEL A | 20.A6
KT0140:A2 | SC | 0V | WHT | 20 | 20.A6 | XT0080:5 | JB70 PANEL A | 20.A6
KT0141:A1 | SC | KT014315 | WHT | 20 | 20.A6 | KT0143:15 | JB70 PANEL A | 20.A5
KT0141:A1 | SC | KT014315 | WHT | 20 | 20.A6 | KT0142:A1 | JB70 PANEL A | 20.A6
KT0141:A2 | SC | 0V | WHT | 20 | 20.A6 | KT0142:A2 | JB70 PANEL A | 20.A6
KT0142:15 | SC | FU0139 | WHT | 20 | 21.D1 | KT0145:15 | JB70 PANEL A | 21.D1
KT0142:A2 | SC | 0V | WHT | 20 | 20.A6 | KT0144:A2 | JB70 PANEL A | 20.B6
KT0145:18 | SC | KA0137A1 | WHT | 20 | 21.D1 | KT0142:18 | JB70 PANEL A | 21.D1
KT0145:A2 | SC | 0V | WHT | 20 | 21.B6 | XT0080:6 | JB70 PANEL A | 21.A6
PEG0130:1 | SC | 0V | GRN/YEL | 8 | 11.C5 | XT0003:10 | JB70 PANEL A | 11.C4
RR0941:-3.01K OHM | SC | FU0387 | LEAD | --- | 25.A2 | XT0089:17 | JB70 PANEL A | 25.A2
RR0941:-3.01K OHM | SC | 007405 | LEAD | --- | 25.A2 | XT0089:18 | JB70 PANEL A | 25.A2
RR0942:-1.0K OHM | SC | 0V | LEAD | --- | 25.A2 | XT0089:19 | JB70 PANEL A | 25.A2
RR0942:-1.0K OHM | SC | 007405 | LEAD | --- | 25.A2 | XT0089:18 | JB70 PANEL A | 25.A2
UA1200:J1-10 | SC | FU0389 | WHT | 20 | 17.B1 | XT0089:21 | JB70 PANEL A | 17.D5
UA1200:J1-5 | SC | UA1200J15 | WHT | 20 | 17.B1 | XT0237:1 B1 | JB70 PANEL A | 17.C4
UA1200:J1-8 | SC | UA1200J | WHT | 20 | 58.B6 | UA1200:J3-5 | JB70 PANEL A | 58.B6
UA1200:J1-9 | SC | 0V | WHT | 20 | 17.B1 | XT0089:22 | JB70 PANEL A | 17.D5
UA1200:J2-1 | SC | UA1200J21 | WHT | 20 | 17.B1 | XT0089:20 | JB70 PANEL A | 17.D5
UA1200:J2-2 | SC | FU0389 | WHT | 20 | 17.B1 | XT0089:21 | JB70 PANEL A | 17.D5
UJ0131:- | SC | 521NEG | WHT | 12 | 12.B4 | XT0011:1 | JB70 PANEL A | 12.B3
UJ0131:G | SC | UJ0131G | GRN/YEL | 12 | 12.B4 | FRAME | JB70 PANEL A | 12.B4
UJ0131:OUT(-) | SC | 0V | WHT | 10 | 12.B4 | XT0003:1 | JB70 PANEL A | 11.A4
XT0003:2 | SC | 0V | WHT | 12 | 11.A4 | XT0082:1 | JB70 PANEL A | 18.A1
XT0050:1 | SC | FU0136 | WHT | 14 | 78.C5 | XT0002:5 | JB70 PANEL A | 11.B4
XT0050:3 | SC | 0V | WHT | 14 | 78.C5 | XT0003:5 | JB70 PANEL A | 11.B4
XT0080:1 | SC | 0V | WHT | 14 | 19.A1 | XT0082:2 | JB70 PANEL A | 18.A1
XT0081:3 | SC | FU0139 | WHT | 20 | 22.A2 | XT0089:12 | JB70 PANEL A | 22.A2
XT0082:2 | SC | 0V | WHT | 20 | 18.A1 | XT0080:5 | JB70 PANEL A | 20.A6
XT0082:3 | SC | 0V | WHT | 20 | 18.B1 | XT0089:19 | JB70 PANEL A | 25.A2
XT0082:4 | SC | 0V | WHT | 16 | 18.B1 | XT0089:22 | JB70 PANEL A | 17.D5
XT0089:13 | SC | FU0139 | WHT | 20 | 95.D5 | XT0081:4 | JB70 PANEL A | 23.A3
AU0080:L1 | WC0009 | AU0090L2 | ENET | CABLE | 2.A4 | AU0090:L2 | JB70 PANEL A | 2.A3
AF0083:J | WC0080 | AF0083J | COMM | USB | 19.B3 | AF0084:P | JB70 PANEL A | 19.B4
AF0081:04 | SC | SB0472B212 | WHT | 20 | 41.B7 | SB0472:B2-12 | CONTROL,JB70;TT6 | 41.B1
AF0081:36 | SC | SB0472B211 | WHT | 20 | 41.B7 | SB0472:B2-11 | CONTROL,JB70;TT6 | 41.B1
AF0087:02 | SC | SB047112 | WHT | 20 | 40.D7 | SB0471:12 | CONTROL,JB70;TT6 | 40.D1
AF0087:03 | SC | SB047314 | WHT | 20 | 40.D7 | SB0473:14 | CONTROL,JB70;TT6 | 40.D1
AF0087:04 | SC | SB047414 | WHT | 20 | 41.A7 | SB0474:14 | CONTROL,JB70;TT6 | 41.A1
AF0087:05 | SC | SA047312 | WHT | 20 | 42.D7 | SA0473:12 | CONTROL,JB70;TT6 | 42.D1
AF0087:06 | SC | SA047314 | WHT | 20 | 42.D7 | SA0473:14 | CONTROL,JB70;TT6 | 42.D1
AF0087:07 | SC | SA0471B214 | WHT | 20 | 41.A7 | SA0471:B2-14 | CONTROL,JB70;TT6 | 41.A1
AF0087:08 | SC | SA0471B114 | WHT | 20 | 41.B7 | SA0471:B1-14 | CONTROL,JB70;TT6 | 41.B1
AF0087:34 | SC | SB047111 | WHT | 20 | 40.D7 | SB0471:11 | CONTROL,JB70;TT6 | 40.D1
AF0087:35 | SC | SB047313 | WHT | 20 | 40.D7 | SB0473:13 | CONTROL,JB70;TT6 | 40.D1
AF0087:36 | SC | SB047413 | WHT | 20 | 41.A7 | SB0474:13 | CONTROL,JB70;TT6 | 41.A1
AF0087:37 | SC | SA047311 | WHT | 20 | 42.D7 | SA0473:11 | CONTROL,JB70;TT6 | 42.D1
AF0087:38 | SC | SA047313 | WHT | 20 | 42.D7 | SA0473:13 | CONTROL,JB70;TT6 | 42.D1
AF0087:39 | SC | SA0471B213 | WHT | 20 | 41.A7 | SA0471:B2-13 | CONTROL,JB70;TT6 | 41.A1
AF0087:40 | SC | SA0471B113 | WHT | 20 | 41.B7 | SA0471:B1-13 | CONTROL,JB70;TT6 | 41.B1
AF0091:14 | SC | SA0472B214 | WHT | 20 | 44.C7 | SA0472:B2-14 | CONTROL,JB70;TT6 | 44.C1
AF0091:15 | SC | SA0472B114 | WHT | 20 | 44.C7 | SA0472:B1-14 | CONTROL,JB70;TT6 | 44.C1
AF0091:46 | SC | SA0472B213 | WHT | 20 | 44.C7 | SA0472:B2-13 | CONTROL,JB70;TT6 | 44.C1
AF0091:47 | SC | SA0472B113 | WHT | 20 | 44.C7 | SA0472:B1-13 | CONTROL,JB70;TT6 | 44.C1
PEG0130:2 | SC | AT1100G | GRN/YEL | 14 | 39.D5 | AT1100:GND | CONTROL,JB70;TT6 | 39.D3
AF0093:12 | SC | 009312 | WHT | 20 | 18.D7 | PC0470:INP_A | JB70 PANEL B | 18.D5
AF0093:28 | SC | 009328 | WHT | 20 | 18.D7 | PC0470:-PWR | JB70 PANEL B | 18.D5
AF0093:44 | SC | 009344 | WHT | 20 | 18.D7 | PC0470:+PWR | JB70 PANEL B | 18.D5
AF0095:02 | SC | 009502 | WHT | 20 | 69.B7 | KA0221:14 | JB70 PANEL B | 69.B6
IEG0010:1 | SC | IEG02300 | GRN | 8 | 9.A2 | IEG0230:0 | JB70 PANEL B | 9.A2
IEG0010:4 | SC | IEG00104 | GRN | 14 | 15.C6 | XT0400:3 | JB70 PANEL B | 15.C5
KA0134:A1 | SC | KA0134A1 | WHT | 20 | 20.D6 | AF0067:12 | JB70 PANEL B | 20.D4
KA0232:A1 | SC | KA0131A1 | WHT | 20 | 25.D5 | KA0233:A1 | JB70 PANEL B | 25.D5
KA0232:A2 | SC | KA0131A2 | WHT | 20 | 25.D5 | KA0233:A2 | JB70 PANEL B | 25.D5
KA0236:A1 | SC | ESTOP | WHT | 20 | 23.C6 | KA0235:A1 | JB70 PANEL B | 23.C6
KA0236:A1 | SC | ESTOP | WHT | 20 | 23.C6 | KA0237:A1 | JB70 PANEL B | 23.C6
KA0236:A2 | SC | 0V | WHT | 20 | 23.C6 | KA0237:A2 | JB70 PANEL B | 23.C6
KA0236:A2 | SC | 0V | WHT | 20 | 23.C6 | KA0235:A2 | JB70 PANEL B | 23.C6
KA0239:21 | SC | FU0212 | WHT | 16 | 17.C6 | FU0212:LD | JB70 PANEL B | 13.B1
KA0239:A1 | SC | ESTOP | WHT | 20 | 23.C6 | KA0237:A1 | JB70 PANEL B | 23.C6
KA0239:A2 | SC | 0V | WHT | 20 | 23.C6 | KA0237:A2 | JB70 PANEL B | 23.C6
KA0240:A1 | SC | ESTOP | WHT | 20 | 23.C6 | KA0251:A1 | JB70 PANEL B | 23.D6
KA0240:A2 | SC | 0V | WHT | 20 | 23.C6 | KA0251:A2 | JB70 PANEL B | 23.D6
KA0242:A2 | SC | 0V | WHT | 20 | 23.B6 | KA0235:A2 | JB70 PANEL B | 23.C6
KT0146:15 | SC | KT014615 | WHT | 20 | 25.B2 | AF0076:10 | JB70 PANEL B | 25.B2
KT0146:A2 | SC | KT0146A2 | WHT | 20 | 25.B4 | AF0076:29 | JB70 PANEL B | 25.B6
KT0146:B1 | SC | KT0146B1 | WHT | 20 | 25.B4 | AF0076:13 | JB70 PANEL B | 25.B6
UA1200:J1-4 | SC | UA1200J14 | WHT | 20 | 17.B1 | AF0076:11 | JB70 PANEL B | 17.C7
XT0002:1 | SC | FU0136 | WHT | 14 | 11.A4 | FU0210:LI | JB70 PANEL B | 13.A2
XT0002:3 | SC | FU0136 | WHT | 14 | 11.A4 | FU0410:LI | JB70 PANEL B | 15.C1
XT0002:7 | SC | FU0136 | WHT | 14 | 11.B4 | XT0051:1 | JB70 PANEL B | 7.A4
XT0003:1 | SC | 0V | WHT | 12 | 11.A4 | XT0062:1 | JB70 PANEL B | 13.A1
XT0003:3 | SC | 0V | WHT | 14 | 11.A4 | XT0401:1 | JB70 PANEL B | 15.A1
XT0003:7 | SC | 0V | WHT | 14 | 11.B4 | XT0051:5 | JB70 PANEL B | 7.A3
XT0089:18 | SC | 007405 | WHT | 20 | 25.A2 | AF0074:05 | JB70 PANEL B | 25.A2
XT0089:19 | SC | 0V | WHT | 20 | 25.A2 | AF0074:21 | JB70 PANEL B | 25.A2
XT0089:5 | SC | ESTOP | WHT | 20 | 24.C4 | KA0235:A1 | JB70 PANEL B | 23.C6
XT0089:6 | SC | ESTOP | WHT | 20 | 23.D5 | KA0251:A1 | JB70 PANEL B | 23.D6
XT0089:8 | SC | KA0131A1 | WHT | 20 | 25.D4 | KA0234:A1 | JB70 PANEL B | 25.D5
XT0237:1 B2 | SC | 007612 | WHT | 20 | 17.C4 | AF0076:12 | JB70 PANEL B | 17.C7
AU0080:L2 | WC0008 | AU0080L2 | ENET | CABLE | 2.A4 | BA1100:L1 | JB70 PANEL B | 2.A5
AU0090:L1 | WC0045 | AF0450L2 | ENET | CABLE | 2.A3 | AF0450:L2 | JB70 PANEL B | 2.A1
UA1200:J1-3 | WC4524 | UA1200J13 | CLR | 20 | 17.B1 | AF0065:12 | JB70 PANEL B | 17.B7
UA1200:J1-1 | WC4524 | UA1200J11 | BLK | 20 | 17.B1 | AF0065:28 | JB70 PANEL B | 17.B7
FLOATING | WC4524 | UJA1200S | SH | 20 | 17.B2 | AF0065:60 | JB70 PANEL B | 17.B7
XT0002:4 | SC | FU0136 | WHT | 14 | 11.A4 | FU0010:LI | JB70 PLC PANEL | 5.B1
XT0003:4 | SC | 0V | WHT | 14 | 11.B4 | UV0600:(-) | JB70 PLC PANEL | 5.B2
AF0087:00 | SC | SH047114 | WHT | 20 | 40.A7 | XT0111:4 | JB70 RIGHT RAIL | 40.A5
AF0087:01 | SC | SH047012 | WHT | 20 | 40.B7 | XT0111:8 | JB70 RIGHT RAIL | 40.B5
AF0087:32 | SC | SH047113 | WHT | 20 | 40.A7 | XT0111:3 | JB70 RIGHT RAIL | 40.A5
AF0087:33 | SC | SH047011 | WHT | 20 | 40.B7 | XT0111:7 | JB70 RIGHT RAIL | 40.B5
AF0092:12 | SC | HA047202 | WHT | 20 | 43.A6 | XT0111:23 | JB70 RIGHT RAIL | 43.A5
AF0092:13 | SC | SH0472X2 | WHT | 20 | 40.C7 | XT0111:17 | JB70 RIGHT RAIL | 40.C5
AF0092:28 | SC | HA047201 | WHT | 20 | 43.A6 | XT0111:24 | JB70 RIGHT RAIL | 43.A5
AF0092:29 | SC | SH0472X1 | WHT | 20 | 40.C7 | XT0111:18 | JB70 RIGHT RAIL | 40.C5
AF0093:06 | SC | SH0470X2 | WHT | 20 | 40.B7 | XT0111:11 | JB70 RIGHT RAIL | 40.B5
AF0093:15 | SC | SH0471X2 | WHT | 20 | 40.A7 | XT0111:5 | JB70 RIGHT RAIL | 40.A5
AF0093:22 | SC | SH0470X1 | WHT | 20 | 40.B7 | XT0111:12 | JB70 RIGHT RAIL | 40.C5
AF0093:31 | SC | SH0471X1 | WHT | 20 | 40.A7 | XT0111:6 | JB70 RIGHT RAIL | 40.A5
KA0240:21 | SC | SH0472X2 | WHT | 20 | 40.C6 | XT0111:17 | JB70 RIGHT RAIL | 40.C5
XT0002:6 | SC | FU0136 | WHT | 14 | 11.B4 | XT0111:21 | JB70 RIGHT RAIL | 39.D6
XT0003:6 | SC | 0V | WHT | 14 | 11.B4 | XT0111:22 | JB70 RIGHT RAIL | 39.D6
XT0081:6 | SC | FU0139 | WHT | 20 | 23.A3 | XT0111:15 | JB70 RIGHT RAIL | 40.C5
XT0081:7 | SC | KA0241A1 | WHT | 20 | 23.A3 | XT0111:16 | JB70 RIGHT RAIL | 40.C5
XT0089:3 | SC | ESTOPB | WHT | 20 | 24.B4 | XT0111:19 | JB70 RIGHT RAIL | 41.C5
XT0089:4 | SC | ESTOPA | WHT | 20 | 24.C4 | XT0111:20 | JB70 RIGHT RAIL | 41.C5
AF0092:00 | SC | KA3420A1 | WHT | 20 | 88.B7 | KA3420:A1 | JB72 GEN PANEL | 88.B5
AF0092:16 | SC | KA3420A2 | WHT | 20 | 88.B7 | KA3420:A2 | JB72 GEN PANEL | 88.B5
SolarTools ver. 24.0.84.24712 (Jul 31, 2025)
Report date: 2/27/2026 8:31 AM

## JB70 PANEL B
JB70 PANEL B
Project # | 4M082
Project Name | STEEL REEF BURKE LLC
Revision | C
Controls DE | J. UNGER
Phone:
Controls ME
Phone:
From | [5 empty] | To
Device ID | Cable (W) Conductor (SC) Jumper Clip (JC) | Wire No. | Wire ID | Gauge/Size | Page/Zone | Device ID | Location | Page/Zone
XT0051:1 | JC | FU0136 | CLIP | --- | 7.A4 | XT0051:2 | JB70 PANEL B | 7.B4
XT0051:2 | JC | FU0136 | CLIP | --- | 7.B4 | XT0051:3 | JB70 PANEL B | 7.C4
XT0051:3 | JC | FU0136 | CLIP | --- | 7.C4 | XT0051:4 | JB70 PANEL B | 7.C4
XT0051:5 | JC | 0V | CLIP | --- | 7.A3 | XT0051:6 | JB70 PANEL B | 7.B3
XT0051:6 | JC | 0V | CLIP | --- | 7.B3 | XT0051:7 | JB70 PANEL B | 7.C3
XT0051:7 | JC | 0V | CLIP | --- | 7.C3 | XT0051:8 | JB70 PANEL B | 7.C3
XT0060:1 | JC | 0V | CLIP | --- | 14.A1 | XT0060:2 | JB70 PANEL B | 14.B1
XT0060:2 | JC | 0V | CLIP | --- | 14.B1 | XT0060:3 | JB70 PANEL B | 14.B1
XT0060:3 | JC | 0V | CLIP | --- | 14.B1 | XT0060:4 | JB70 PANEL B | 14.C1
XT0062:1 | JC | 0V | CLIP | --- | 13.A1 | XT0062:2 | JB70 PANEL B | 13.A1
XT0062:2 | JC | 0V | CLIP | --- | 13.A1 | XT0062:3 | JB70 PANEL B | 13.B1
XT0062:3 | JC | 0V | CLIP | --- | 13.B1 | XT0062:4 | JB70 PANEL B | 13.B1
XT0401:1 | JC | 0V | CLIP | --- | 15.A1 | XT0401:2 | JB70 PANEL B | 15.C1
AF0061:02 | SC | 006102 | WHT | 20 | 61.B7 | KA0233:14 | JB70 PANEL B | 61.B5
AF0061:14 | SC | 006114 | WHT | 20 | 59.B7 | KA0234:14 | JB70 PANEL B | 59.B5
AF0061:COM | SC | 0V | WHT | 16 | 14.B2 | XT0060:2 | JB70 PANEL B | 14.B1
AF0061:J | SC | * |  |  | 14.B2 | AF0062:P | JB70 PANEL B | 14.B3
AF0061:V+ | SC | FU0062 | WHT | 16 | 14.B2 | FU0062:LD | JB70 PANEL B | 14.B1
AF0062:00 | SC | 006200 | WHT | 20 | 69.C7 | KA0222:14 | JB70 PANEL B | 69.C6
AF0062:COM | SC | 0V | WHT | 16 | 14.B3 | XT0060:3 | JB70 PANEL B | 14.B1
AF0062:J | SC | * |  |  | 14.B3 | AF0063:P | JB70 PANEL B | 14.B3
AF0062:V+ | SC | FU0063 | WHT | 16 | 14.B3 | FU0063:LD | JB70 PANEL B | 14.B1
AF0063:COM | SC | AF0063N | WHT | 16 | 14.B3 | AF0064:COM | JB70 PANEL B | 14.A4
AF0063:COM | SC | AU0060N | WHT | 16 | 14.B3 | AU0060:COM | JB70 PANEL B | 14.A2
AF0063:J | SC | * |  |  | 14.B3 | AF0064:P | JB70 PANEL B | 14.A4
AF0063:V+ | SC | AF0063P | WHT | 16 | 14.B3 | AF0064:V+ | JB70 PANEL B | 14.A4
AF0063:V+ | SC | AU0060P | WHT | 16 | 14.B3 | AU0060:V+ | JB70 PANEL B | 14.A2
AF0064:COM | SC | AF0064N | WHT | 16 | 14.A4 | AF0065:COM | JB70 PANEL B | 14.A5
AF0064:J | SC | * |  |  | 14.A4 | AF0065:P | JB70 PANEL B | 14.A5
AF0064:SH | SC | AF0064G | GRN | 14 | 14.A4 | AF0065:SH | JB70 PANEL B | 14.A5
AF0064:SH | SC | AU0060G | GRN | 14 | 14.A4 | AU0060:GND | JB70 PANEL B | 14.A2
AF0064:V+ | SC | AF0064P | WHT | 16 | 14.A4 | AF0065:V+ | JB70 PANEL B | 14.A5
AF0065:COM | SC | AF0065N | WHT | 16 | 14.A5 | AF0066:COM | JB70 PANEL B | 14.B5
AF0065:J | SC | * |  |  | 14.A5 | AF0066:P | JB70 PANEL B | 14.B5
AF0065:SH | SC | AF0065G | GRN | 14 | 14.A5 | AF0066:SH | JB70 PANEL B | 14.B5
AF0065:V+ | SC | AF0065P | WHT | 16 | 14.A5 | AF0066:V+ | JB70 PANEL B | 14.B5
AF0066:COM | SC | AF0066N | WHT | 16 | 14.B5 | AF0068:COM | JB70 PANEL B | 14.B6
AF0066:J | SC | * |  |  | 14.B5 | AF0067:P | JB70 PANEL B | 14.B6
AF0066:SH | SC | AF0066G | GRN | 14 | 14.B5 | AF0068:SH | JB70 PANEL B | 14.B6
AF0066:V+ | SC | AF0066P | WHT | 16 | 14.B5 | AF0068:V+ | JB70 PANEL B | 14.B6
AF0067:COM | SC | 0V | WHT | 16 | 14.B6 | XT0060:3 | JB70 PANEL B | 14.B1
AF0067:J | SC | * |  |  | 14.B6 | AF0068:P | JB70 PANEL B | 14.B6
AF0067:V+ | SC | FU0064 | WHT | 16 | 14.B6 | FU0064:LD | JB70 PANEL B | 14.B1
AF0068:SH | SC | IEG02304 | GRN | 14 | 14.B6 | IEG0230:4 | JB70 PANEL B | 14.B6
AF0071:COM | SC | AF0071N | WHT | 16 | 14.C2 | AF0072:COM | JB70 PANEL B | 14.C3
AF0071:COM | SC | AU0070N | WHT | 16 | 14.C2 | AU0070:COM | JB70 PANEL B | 14.C2
AF0071:J | SC | * |  |  | 14.C2 | AF0072:P | JB70 PANEL B | 14.C3
AF0071:SH | SC | AF0071G | GRN | 14 | 14.C2 | AF0072:SH | JB70 PANEL B | 14.C3
AF0071:SH | SC | AU0070G | GRN | 14 | 14.C2 | AU0070:GND | JB70 PANEL B | 14.C2
AF0071:V+ | SC | AF0071P | WHT | 16 | 14.C2 | AF0072:V+ | JB70 PANEL B | 14.C3
AF0071:V+ | SC | AU0070P | WHT | 16 | 14.C2 | AU0070:V+ | JB70 PANEL B | 14.C2
AF0072:COM | SC | AF0072N | WHT | 16 | 14.C3 | AF0073:COM | JB70 PANEL B | 14.C3
AF0072:J | SC | * |  |  | 14.C3 | AF0073:P | JB70 PANEL B | 14.C3
AF0072:SH | SC | AF0072G | GRN | 14 | 14.C3 | AF0073:SH | JB70 PANEL B | 14.C3
AF0072:V+ | SC | AF0072P | WHT | 16 | 14.C3 | AF0073:V+ | JB70 PANEL B | 14.C3
AF0073:COM | SC | AF0073N | WHT | 16 | 14.C3 | AF0074:COM | JB70 PANEL B | 14.C4
AF0073:J | SC | * |  |  | 14.C3 | AF0074:P | JB70 PANEL B | 14.C4
AF0073:SH | SC | AF0073G | GRN | 14 | 14.C3 | AF0074:SH | JB70 PANEL B | 14.C4
AF0073:V+ | SC | AF0073P | WHT | 16 | 14.C3 | AF0074:V+ | JB70 PANEL B | 14.C4
AF0074:COM | SC | AF0074N | WHT | 16 | 14.C4 | AF0075:COM | JB70 PANEL B | 14.C5
AF0074:J | SC | * |  |  | 14.C4 | AF0075:P | JB70 PANEL B | 14.C5
AF0074:SH | SC | AF0074G | GRN | 14 | 14.C4 | AF0075:SH | JB70 PANEL B | 14.C5
AF0074:V+ | SC | AF0074P | WHT | 16 | 14.C4 | AF0075:V+ | JB70 PANEL B | 14.C5
AF0075:J | SC | * |  |  | 14.C5 | AF0076:P | JB70 PANEL B | 14.C5
AF0075:SH | SC | IEG02301 | GRN | 14 | 14.C5 | IEG0230:1 | JB70 PANEL B | 14.D5
AF0076:00 | SC | KA023514 | WHT | 20 | 73.B7 | KA0235:14 | JB70 PANEL B | 73.B5
AF0076:01 | SC | KA023714 | WHT | 20 | 74.B7 | KA0237:14 | JB70 PANEL B | 74.B5
AF0076:02 | SC | 007602 | WHT | 20 | 69.B7 | KA0221:A1 | JB70 PANEL B | 69.B6
AF0076:04 | SC | 007604 | WHT | 20 | 69.C7 | KA0222:A1 | JB70 PANEL B | 69.C6
AF0076:08 | SC | KA1020A1 | WHT | 20 | 13.C7 | KA1020:A1 | JB70 PANEL B | 13.C5
AF0076:15 | SC | 007615 | WHT | 20 | 24.D6 | KA0224:A1 | JB70 PANEL B | 24.D6
AF0076:18 | SC | 007618 | WHT | 20 | 69.B7 | KA0221:A2 | JB70 PANEL B | 69.B6
AF0076:20 | SC | 007620 | WHT | 20 | 69.C7 | KA0222:A2 | JB70 PANEL B | 69.C6
AF0076:24 | SC | KA1020A2 | WHT | 20 | 13.C7 | KA1020:A2 | JB70 PANEL B | 13.C5
AF0076:31 | SC | 007631 | WHT | 20 | 24.D6 | KA0224:A2 | JB70 PANEL B | 24.D6
AF0076:COM | SC | 0V | WHT | 16 | 14.C5 | XT0060:4 | JB70 PANEL B | 14.C1
AF0076:V+ | SC | FU0076 | WHT | 16 | 14.C5 | FU0076:LD | JB70 PANEL B | 14.D1
AF0400:12 | SC | XT04002 | GRN | 16 | 15.A6 | XT0400:2 | JB70 PANEL B | 15.C6
AF0410:32 | SC | XT04001 | GRN | 16 | 15.A5 | XT0400:1 | JB70 PANEL B | 15.C5
AF0410:53 | SC | 0V | WHT | 16 | 15.A5 | XT0401:2 | JB70 PANEL B | 15.C1
AF0410:54 | SC | 0V | WHT | 16 | 15.A5 | AF0420:53 | JB70 PANEL B | 15.A4
AF0410:55 | SC | FU0410 | WHT | 16 | 15.A5 | FU0410:LD | JB70 PANEL B | 15.C1
AF0410:56 | SC | FU0410 | WHT | 16 | 15.A5 | AF0420:55 | JB70 PANEL B | 15.A4
AF0420:32 | SC | XT04001 | GRN | 16 | 15.A4 | XT0400:1 | JB70 PANEL B | 15.C5
AF0420:54 | SC | 0V | WHT | 16 | 15.A4 | AF0450:53 | JB70 PANEL B | 15.A1
AF0420:56 | SC | FU0410 | WHT | 16 | 15.A4 | AF0450:55 | JB70 PANEL B | 15.A1
AF0450:32 | SC | XT04001 | GRN | 16 | 15.A1 | XT0400:1 | JB70 PANEL B | 15.C5
AU0060:COM | SC | 0V | WHT | 16 | 14.A2 | XT0060:2 | JB70 PANEL B | 14.B1
AU0060:V+ | SC | FU0061 | WHT | 16 | 14.A2 | FU0061:LD | JB70 PANEL B | 14.B1
AU0070:COM | SC | 0V | WHT | 16 | 14.C2 | XT0060:4 | JB70 PANEL B | 14.C1
AU0070:V+ | SC | FU0070 | WHT | 16 | 14.C2 | FU0070:LD | JB70 PANEL B | 14.C1
BA0003:V1(-) | SC | 0V | WHT | 16 | 7.C2 | XT0051:7 | JB70 PANEL B | 7.C3
BA0003:V1(+) | SC | FU0023 | WHT | 16 | 7.C2 | FU0023:LD | JB70 PANEL B | 7.C3
BA0011:V1(-) | SC | 0V | WHT | 16 | 7.C5 | XT0051:7 | JB70 PANEL B | 7.C3
BA0011:V1(+) | SC | FU0031 | WHT | 16 | 7.C5 | FU0031:LD | JB70 PANEL B | 7.C4
BA1100:NEG | SC | BA1100N | WHT | 16 | 39.D1 | UV0291:OUT1(-) | JB70 PANEL B | 39.C5
BA1100:POS | SC | FU1101LD | WHT | 16 | 39.D1 | FU1101:LD | JB70 PANEL B | 39.C2
FU0023:LI | SC | FU0136 | WHT | 14 | 7.C3 | XT0051:3 | JB70 PANEL B | 7.C4
FU0031:LI | SC | FU0136 | WHT | 16 | 7.C4 | XT0051:3 | JB70 PANEL B | 7.C4
FU0060:LI | SC | FU0210 | WHT | 12 | 13.A1 | FU0210:LD | JB70 PANEL B | 13.A2
FU0060:LI | SC | FU0210 | WHT | 12 | 13.A1 | FU0100:LI | JB70 PANEL B | 13.A1
FU0061:LI | SC | FU0060 | WHT | 14 | 14.B1 | FU0060:LD | JB70 PANEL B | 13.A1
FU0061:LI | SC | FU0060 | WHT | 14 | 14.B1 | FU0062:LI | JB70 PANEL B | 14.B1
FU0062:LI | SC | FU0060 | WHT | 14 | 14.B1 | FU0063:LI | JB70 PANEL B | 14.B1
FU0063:LI | SC | FU0060 | WHT | 14 | 14.B1 | FU0064:LI | JB70 PANEL B | 14.B1
FU0064:LI | SC | FU0060 | WHT | 14 | 14.B1 | FU0070:LI | JB70 PANEL B | 14.C1
FU0070:LI | SC | FU0060 | WHT | 14 | 14.C1 | FU0076:LI | JB70 PANEL B | 14.D1
FU0100:LD | SC | FU0100 | WHT | 16 | 13.A1 | KA1020:14 | JB70 PANEL B | 65.A5
FU0100:LI | SC | FU0210 | WHT | 12 | 13.A1 | FU0113:LI | JB70 PANEL B | 13.B1
FU0113:LI | SC | FU0210 | WHT | 12 | 13.B1 | FU0114:LI | JB70 PANEL B | 13.B1
FU0114:LI | SC | FU0210 | WHT | 12 | 13.B1 | FU0115:LI | JB70 PANEL B | 13.B1
FU0115:LI | SC | FU0210 | WHT | 12 | 13.B1 | FU0212:LI | JB70 PANEL B | 13.B1
FU0291:LD | SC | FU0291LD | WHT | 16 | 39.C6 | UV0291:24V(+) | JB70 PANEL B | 39.C5
FU1101:LI | SC | FU1101LI | WHT | 16 | 39.C2 | UV0291:OUT1(+) | JB70 PANEL B | 39.C5
GR0231: | SC | IEG02303 | GRN | 14 | 9.A4 | IEG0230:3 | JB70 PANEL B | 9.A3
GR0233: | SC | IEG02308 | GRN | 14 | 9.A4 | IEG0230:8 | JB70 PANEL B | 9.A5
GR0341: | SC | IEG023011 | GRN | 14 | 9.B2 | IEG0230:11 | JB70 PANEL B | 9.B2
KA0221:11 | SC | 023524 | WHT | 20 | 69.B6 | KA0235:24 | JB70 PANEL B | 69.B5
KA0222:11 | SC | 023724 | WHT | 20 | 69.C6 | KA0237:24 | JB70 PANEL B | 69.C5
KA0224:11 | SC | KA022411 | WHT | 20 | 24.D5 | XT0224:1 | JB70 PANEL B | 24.D4
KA0224:14 | SC | KA022414 | WHT | 20 | 24.D5 | XT0224:2 | JB70 PANEL B | 24.D4
KA0233:A1 | SC | KA0131A1 | WHT | 20 | 25.D5 | KA0234:A1 | JB70 PANEL B | 25.D5
KA0233:A2 | SC | KA0131A2 | WHT | 20 | 25.D5 | KA0234:A2 | JB70 PANEL B | 25.D5
KA1020:24 | SC | 0V | WHT | 14 | 65.A5 | XT0062:2 | JB70 PANEL B | 13.A1
PC0470:INP_A | SC | 009312 | WHT | 20 | 18.D5 | PC0470:INP_B | JB70 PANEL B | 18.D5
XT0062:2 | SC | 0V | WHT | 14 | 13.A1 | XT0060:1 | JB70 PANEL B | 14.A1
AU0060:L1 | WC0007 | AU0070L2 | ENET | CABLE | 2.B1 | AU0070:L2 | JB70 PANEL B | 2.A6
AU0070:L1 | WC0010 | BA1100L2 | ENET | CABLE | 2.A6 | BA1100:L2 | JB70 PANEL B | 2.A5
AF0410:L2 | WC0041 | AF0410L2 | ENET | CABLE | 2.A5 | AF0420:L1 | JB70 PANEL B | 2.A5
AF0420:L2 | WC0042 | AF0420L2 | ENET | CABLE | 2.A5 | AF0450:L1 | JB70 PANEL B | 2.A1
AF0400:LBUS | WC8040 | AF0400LBUS | BUS | CABLE | 15.A6 | AF0410:RBUS | JB70 PANEL B | 15.A5
AF0410:LBUS | WC8041 | AF0420RBUS | BUS | CABLE | 15.A5 | AF0420:RBUS | JB70 PANEL B | 15.A4
AF0420:LBUS | WC8042 | AF0450RBUS | BUS | CABLE | 15.A4 | AF0450:RBUS | JB70 PANEL B | 15.A1
FU1100:LD | SC | FU1100 | WHT | 14 | 39.D3 | AT1100:POS | CONTROL,JB70;TT6 | 39.D3
BA1100:DEVICE | WC0101 | BA1100DEVICE | ENET | CABLE | 39.D1 | AT1100:L1 | CONTROL,JB70;TT6 | 39.D3
AF0067:12 | SC | KA0134A1 | WHT | 20 | 20.D4 | KA0134:A1 | JB70 PANEL A | 20.D6
AF0074:05 | SC | 007405 | WHT | 20 | 25.A2 | XT0089:18 | JB70 PANEL A | 25.A2
AF0074:21 | SC | 0V | WHT | 20 | 25.A2 | XT0089:19 | JB70 PANEL A | 25.A2
AF0076:10 | SC | KT014615 | WHT | 20 | 25.B2 | KT0146:15 | JB70 PANEL A | 25.B2
AF0076:11 | SC | UA1200J14 | WHT | 20 | 17.C7 | UA1200:J1-4 | JB70 PANEL A | 17.B1
AF0076:12 | SC | 007612 | WHT | 20 | 17.C7 | XT0237:1 B2 | JB70 PANEL A | 17.C4
AF0076:13 | SC | KT0146B1 | WHT | 20 | 25.B6 | KT0146:B1 | JB70 PANEL A | 25.B4
AF0076:29 | SC | KT0146A2 | WHT | 20 | 25.B6 | KT0146:A2 | JB70 PANEL A | 25.B4
FU0210:LI | SC | FU0136 | WHT | 14 | 13.A2 | XT0002:1 | JB70 PANEL A | 11.A4
FU0212:LD | SC | FU0212 | WHT | 16 | 13.B1 | KA0239:21 | JB70 PANEL A | 17.C6
FU0410:LI | SC | FU0136 | WHT | 14 | 15.C1 | XT0002:3 | JB70 PANEL A | 11.A4
IEG0230:0 | SC | IEG02300 | GRN | 8 | 9.A2 | IEG0010:1 | JB70 PANEL A | 9.A2
KA0221:14 | SC | 009502 | WHT | 20 | 69.B6 | AF0095:02 | JB70 PANEL A | 69.B7
KA0233:A1 | SC | KA0131A1 | WHT | 20 | 25.D5 | KA0232:A1 | JB70 PANEL A | 25.D5
KA0233:A2 | SC | KA0131A2 | WHT | 20 | 25.D5 | KA0232:A2 | JB70 PANEL A | 25.D5
KA0234:A1 | SC | KA0131A1 | WHT | 20 | 25.D5 | XT0089:8 | JB70 PANEL A | 25.D4
KA0235:A1 | SC | ESTOP | WHT | 20 | 23.C6 | XT0089:5 | JB70 PANEL A | 24.C4
KA0235:A1 | SC | ESTOP | WHT | 20 | 23.C6 | KA0236:A1 | JB70 PANEL A | 23.C6
KA0235:A2 | SC | 0V | WHT | 20 | 23.C6 | KA0236:A2 | JB70 PANEL A | 23.C6
KA0235:A2 | SC | 0V | WHT | 20 | 23.C6 | KA0242:A2 | JB70 PANEL A | 23.B6
KA0237:A1 | SC | ESTOP | WHT | 20 | 23.C6 | KA0236:A1 | JB70 PANEL A | 23.C6
KA0237:A1 | SC | ESTOP | WHT | 20 | 23.C6 | KA0239:A1 | JB70 PANEL A | 23.C6
KA0237:A2 | SC | 0V | WHT | 20 | 23.C6 | KA0239:A2 | JB70 PANEL A | 23.C6
KA0237:A2 | SC | 0V | WHT | 20 | 23.C6 | KA0236:A2 | JB70 PANEL A | 23.C6
KA0251:A1 | SC | ESTOP | WHT | 20 | 23.D6 | KA0240:A1 | JB70 PANEL A | 23.C6
KA0251:A1 | SC | ESTOP | WHT | 20 | 23.D6 | XT0089:6 | JB70 PANEL A | 23.D5
KA0251:A2 | SC | 0V | WHT | 20 | 23.D6 | KA0240:A2 | JB70 PANEL A | 23.C6
PC0470:+PWR | SC | 009344 | WHT | 20 | 18.D5 | AF0093:44 | JB70 PANEL A | 18.D7
PC0470:INP_A | SC | 009312 | WHT | 20 | 18.D5 | AF0093:12 | JB70 PANEL A | 18.D7
PC0470:-PWR | SC | 009328 | WHT | 20 | 18.D5 | AF0093:28 | JB70 PANEL A | 18.D7
XT0051:1 | SC | FU0136 | WHT | 14 | 7.A4 | XT0002:7 | JB70 PANEL A | 11.B4
XT0051:5 | SC | 0V | WHT | 14 | 7.A3 | XT0003:7 | JB70 PANEL A | 11.B4
XT0062:1 | SC | 0V | WHT | 12 | 13.A1 | XT0003:1 | JB70 PANEL A | 11.A4
XT0400:3 | SC | IEG00104 | GRN | 14 | 15.C5 | IEG0010:4 | JB70 PANEL A | 15.C6
XT0401:1 | SC | 0V | WHT | 14 | 15.A1 | XT0003:3 | JB70 PANEL A | 11.A4
BA1100:L1 | WC0008 | AU0080L2 | ENET | CABLE | 2.A5 | AU0080:L2 | JB70 PANEL A | 2.A4
AF0450:L2 | WC0045 | AF0450L2 | ENET | CABLE | 2.A1 | AU0090:L1 | JB70 PANEL A | 2.A3
AF0065:12 | WC4524 | UA1200J13 | CLR | 20 | 17.B7 | UA1200:J1-3 | JB70 PANEL A | 17.B1
AF0065:28 | WC4524 | UA1200J11 | BLK | 20 | 17.B7 | UA1200:J1-1 | JB70 PANEL A | 17.B1
AF0065:60 | WC4524 | UJA1200S | SH | 20 | 17.B7 | FLOATING | JB70 PANEL A | 17.B2
IEG0230:6 | SC | IEG02306 | GRN | 12 | 5.B6 | AR0600:IE2 | JB70 PLC PANEL | 5.A1
IEG0230:7 | SC | IEG02307 | GRN | 14 | 9.B4 | GR0234: | JB70 PLC PANEL | 9.B4
XT0051:1 | SC | FU0136 | WHT | 16 | 7.A4 | FU0021:LI | JB70 PLC PANEL | 7.A3
XT0051:2 | SC | FU0136 | WHT | 16 | 7.B4 | FU0022:LI | JB70 PLC PANEL | 7.B3
XT0051:4 | SC | FU0136 | WHT | 16 | 7.C4 | FU0680:LI | JB70 PLC PANEL | 6.A4
XT0051:5 | SC | 0V | WHT | 16 | 7.A3 | BA0001:V1(-) | JB70 PLC PANEL | 7.A2
XT0051:6 | SC | 0V | WHT | 16 | 7.B3 | BA0002:V1(-) | JB70 PLC PANEL | 7.B2
XT0051:8 | SC | 0V | WHT | 14 | 7.C3 | XT0680:2 | JB70 PLC PANEL | 6.A4
AF0410:L1 | WC0003 | AP0603L2 | ENET | CABLE | 2.A5 | AP0603:L2 | JB70 PLC PANEL | 2.A3
BA0003:RJ45 | WC0605 | AP0605ENET | ENET | CABLE | 5.C4 | AP0605:ENET | JB70 PLC PANEL | 5.C5
BA0011:RJ45 | WC9111 | AT0680LAN3 | ENET | CABLE | 3.B3 | AT0680:LAN3 | JB70 PLC PANEL | 3.A2
FU0291:LI | SC | FU0136 | WHT | 16 | 39.C6 | XT0111:21 | JB70 RIGHT RAIL | 39.D6
FU1100:LI | SC | FU0136 | WHT | 16 | 39.D3 | XT0111:21 | JB70 RIGHT RAIL | 39.D6
UV0291:24V(-) | SC | 0V | WHT | 14 | 39.C5 | XT0111:22 | JB70 RIGHT RAIL | 39.D6
AU0060:L2 | WC006 | AU0060L2 | ENET | CABLE | 2.B1 | AU0120:L1 | JB72 GEN PANEL | 2.C1
AF0076:03 | SC | KA0183A1 | WHT | 20 | 45.D7 | KA0183:A1 | JB72 LEFT RAIL | 45.D5
AF0076:14 | SC | KA0182A1 | WHT | 20 | 45.D7 | KA0182:A1 | JB72 LEFT RAIL | 45.D5
AF0076:19 | SC | KA0183A2 | WHT | 20 | 45.D7 | KA0183:A2 | JB72 LEFT RAIL | 45.D5
AF0076:30 | SC | KA0182A2 | WHT | 20 | 45.D7 | KA0182:A2 | JB72 LEFT RAIL | 45.D5
SolarTools ver. 24.0.84.24712 (Jul 31, 2025)
Report date: 2/27/2026 8:31 AM

## JB70 PLC PANEL
JB70 PLC PANEL
Project # | 4M082
Project Name | STEEL REEF BURKE LLC
Revision | C
Controls DE | J. UNGER
Phone:
Controls ME
Phone:
From | [5 empty] | To
Device ID | Cable (W) Conductor (SC) Jumper Clip (JC) | Wire No. | Wire ID | Gauge/Size | Page/Zone | Device ID | Location | Page/Zone
AR0600:IE1 | SC | UV0600G | GRN | 14 | 5.A1 | UV0600:GND | JB70 PLC PANEL | 5.B2
AT0680:NEG | SC | 0V | WHT | 14 | 6.A5 | XT0680:2 | JB70 PLC PANEL | 6.A4
AT0680:POS | SC | AT0680POS | WHT | 14 | 6.A5 | XT0680:1 | JB70 PLC PANEL | 6.A4
BA0001:V1(+) | SC | FU0021 | WHT | 16 | 7.A2 | FU0021:LD | JB70 PLC PANEL | 7.A3
BA0002:V1(+) | SC | FU0022 | WHT | 16 | 7.B2 | FU0022:LD | JB70 PLC PANEL | 7.B3
FU0010:LD | SC | FU0010 | WHT | 14 | 5.B1 | UV0600:(+) | JB70 PLC PANEL | 5.B2
FU0680:LD | SC | AT0680POS | WHT | 14 | 6.A4 | XT0680:1 | JB70 PLC PANEL | 6.A4
AP0602:L2 | WC0001 | AP0602L2 | ENET | CABLE | 2.A2 | AP0603:L1 | JB70 PLC PANEL | 2.A3
AP0609:L1 | WC0680 | AP0609L1 | ENET | CABLE | 3.A2 | AT0680:LAN1 | JB70 PLC PANEL | 3.A2
AP0602:L1 | WC9001 | BA0001RJ45 | ENET | CABLE | 2.A2 | BA0001:RJ45 | JB70 PLC PANEL | 2.A2
FU0010:LI | SC | FU0136 | WHT | 14 | 5.B1 | XT0002:4 | JB70 PANEL A | 11.A4
UV0600:(-) | SC | 0V | WHT | 14 | 5.B2 | XT0003:4 | JB70 PANEL A | 11.B4
AR0600:IE2 | SC | IEG02306 | GRN | 12 | 5.A1 | IEG0230:6 | JB70 PANEL B | 5.B6
BA0001:V1(-) | SC | 0V | WHT | 16 | 7.A2 | XT0051:5 | JB70 PANEL B | 7.A3
BA0002:V1(-) | SC | 0V | WHT | 16 | 7.B2 | XT0051:6 | JB70 PANEL B | 7.B3
FU0021:LI | SC | FU0136 | WHT | 16 | 7.A3 | XT0051:1 | JB70 PANEL B | 7.A4
FU0022:LI | SC | FU0136 | WHT | 16 | 7.B3 | XT0051:2 | JB70 PANEL B | 7.B4
FU0680:LI | SC | FU0136 | WHT | 16 | 6.A4 | XT0051:4 | JB70 PANEL B | 7.C4
GR0234: | SC | IEG02307 | GRN | 14 | 9.B4 | IEG0230:7 | JB70 PANEL B | 9.B4
XT0680:2 | SC | 0V | WHT | 14 | 6.A4 | XT0051:8 | JB70 PANEL B | 7.C3
AP0603:L2 | WC0003 | AP0603L2 | ENET | CABLE | 2.A3 | AF0410:L1 | JB70 PANEL B | 2.A5
AP0605:ENET | WC0605 | AP0605ENET | ENET | CABLE | 5.C5 | BA0003:RJ45 | JB70 PANEL B | 5.C4
AT0680:LAN3 | WC9111 | AT0680LAN3 | ENET | CABLE | 3.A2 | BA0011:RJ45 | JB70 PANEL B | 3.B3
BA0002:RJ45 | WC0014 | AT0140P2 | ENET | CABLE | 2.B5 | AT0140:P2 | JB72 GEN PANEL | 2.C3
SolarTools ver. 24.0.84.24712 (Jul 31, 2025)
Report date: 2/27/2026 8:31 AM

## JB70 RIGHT RAIL
JB70 RIGHT RAIL
Project # | 4M082
Project Name | STEEL REEF BURKE LLC
Revision | C
Controls DE | J. UNGER
Phone:
Controls ME
Phone:
From | [5 empty] | To
Device ID | Cable (W) Conductor (SC) Jumper Clip (JC) | Wire No. | Wire ID | Gauge/Size | Page/Zone | Device ID | Location | Page/Zone
GR0532: | SC | GR0532 | GRN/YEL | 14 | 9.B4 | FRAME | JB70 RIGHT RAIL | 9.B4
XT0111:1 | SC | SH047111 | WHT | 20 | 40.A5 | SH0471:11 | CONTROL,JB70;TT6 | 40.A1
XT0111:10 | SC | SH047014 | WHT | 20 | 40.B5 | SH0470:14 | CONTROL,JB70;TT6 | 40.B1
XT0111:11 | SC | SH0470X2 | WHT | 20 | 40.B5 | SH0470:X2 | CONTROL,JB70;TT6 | 40.B1
XT0111:12 | SC | SH0470X1 | WHT | 20 | 40.C5 | SH0470:X1 | CONTROL,JB70;TT6 | 40.B1
XT0111:13 | SC | SH047211 | WHT | 20 | 40.C5 | SH0472:11 | CONTROL,JB70;TT6 | 40.C1
XT0111:14 | SC | SH047212 | WHT | 20 | 40.C5 | SH0472:12 | CONTROL,JB70;TT6 | 40.C1
XT0111:15 | SC | FU0139 | WHT | 20 | 40.C5 | SH0472:13 | CONTROL,JB70;TT6 | 40.C1
XT0111:16 | SC | KA0241A1 | WHT | 20 | 40.C5 | SH0472:14 | CONTROL,JB70;TT6 | 40.C1
XT0111:17 | SC | SH0472X2 | WHT | 20 | 40.C5 | SH0472:X2 | CONTROL,JB70;TT6 | 40.C1
XT0111:18 | SC | SH0472X1 | WHT | 20 | 40.C5 | SH0472:X1 | CONTROL,JB70;TT6 | 40.C1
XT0111:19 | SC | ESTOPB | WHT | 20 | 41.C5 | SB0472:B1-11 | CONTROL,JB70;TT6 | 41.C1
XT0111:2 | SC | SH047112 | WHT | 20 | 40.A5 | SH0471:12 | CONTROL,JB70;TT6 | 40.A1
XT0111:20 | SC | ESTOPA | WHT | 20 | 41.C5 | SB0472:B1-12 | CONTROL,JB70;TT6 | 41.C1
XT0111:22 | SC | 0V | WHT | 14 | 39.D6 | AT1100:NEG | CONTROL,JB70;TT6 | 39.D3
XT0111:3 | SC | SH047113 | WHT | 20 | 40.A5 | SH0471:13 | CONTROL,JB70;TT6 | 40.A1
XT0111:4 | SC | SH047114 | WHT | 20 | 40.A5 | SH0471:14 | CONTROL,JB70;TT6 | 40.A1
XT0111:5 | SC | SH0471X2 | WHT | 20 | 40.A5 | SH0471:X2 | CONTROL,JB70;TT6 | 40.A1
XT0111:6 | SC | SH0471X1 | WHT | 20 | 40.A5 | SH0471:X1 | CONTROL,JB70;TT6 | 40.A1
XT0111:7 | SC | SH047011 | WHT | 20 | 40.B5 | SH0470:11 | CONTROL,JB70;TT6 | 40.B1
XT0111:8 | SC | SH047012 | WHT | 20 | 40.B5 | SH0470:12 | CONTROL,JB70;TT6 | 40.B1
XT0111:9 | SC | SH047013 | WHT | 20 | 40.B5 | SH0470:13 | CONTROL,JB70;TT6 | 40.B1
XT0111:24 | WC5072 | HA047201 | 1 | 18 | 43.A5 | HA0472:BLK-1 | CONTROL,JB70;TT6 | 43.A1
XT0111:23 | WC5072 | HA047202 | 2 | 18 | 43.A5 | HA0472:BLK-2 | CONTROL,JB70;TT6 | 43.A1
XT0111:11 | SC | SH0470X2 | WHT | 20 | 40.B5 | AF0093:06 | JB70 PANEL A | 40.B7
XT0111:12 | SC | SH0470X1 | WHT | 20 | 40.C5 | AF0093:22 | JB70 PANEL A | 40.B7
XT0111:15 | SC | FU0139 | WHT | 20 | 40.C5 | XT0081:6 | JB70 PANEL A | 23.A3
XT0111:16 | SC | KA0241A1 | WHT | 20 | 40.C5 | XT0081:7 | JB70 PANEL A | 23.A3
XT0111:17 | SC | SH0472X2 | WHT | 20 | 40.C5 | AF0092:13 | JB70 PANEL A | 40.C7
XT0111:17 | SC | SH0472X2 | WHT | 20 | 40.C5 | KA0240:21 | JB70 PANEL A | 40.C6
XT0111:18 | SC | SH0472X1 | WHT | 20 | 40.C5 | AF0092:29 | JB70 PANEL A | 40.C7
XT0111:19 | SC | ESTOPB | WHT | 20 | 41.C5 | XT0089:3 | JB70 PANEL A | 24.B4
XT0111:20 | SC | ESTOPA | WHT | 20 | 41.C5 | XT0089:4 | JB70 PANEL A | 24.C4
XT0111:21 | SC | FU0136 | WHT | 14 | 39.D6 | XT0002:6 | JB70 PANEL A | 11.B4
XT0111:22 | SC | 0V | WHT | 14 | 39.D6 | XT0003:6 | JB70 PANEL A | 11.B4
XT0111:23 | SC | HA047202 | WHT | 20 | 43.A5 | AF0092:12 | JB70 PANEL A | 43.A6
XT0111:24 | SC | HA047201 | WHT | 20 | 43.A5 | AF0092:28 | JB70 PANEL A | 43.A6
XT0111:3 | SC | SH047113 | WHT | 20 | 40.A5 | AF0087:32 | JB70 PANEL A | 40.A7
XT0111:4 | SC | SH047114 | WHT | 20 | 40.A5 | AF0087:00 | JB70 PANEL A | 40.A7
XT0111:5 | SC | SH0471X2 | WHT | 20 | 40.A5 | AF0093:15 | JB70 PANEL A | 40.A7
XT0111:6 | SC | SH0471X1 | WHT | 20 | 40.A5 | AF0093:31 | JB70 PANEL A | 40.A7
XT0111:7 | SC | SH047011 | WHT | 20 | 40.B5 | AF0087:33 | JB70 PANEL A | 40.B7
XT0111:8 | SC | SH047012 | WHT | 20 | 40.B5 | AF0087:01 | JB70 PANEL A | 40.B7
XT0111:21 | SC | FU0136 | WHT | 16 | 39.D6 | FU0291:LI | JB70 PANEL B | 39.C6
XT0111:21 | SC | FU0136 | WHT | 16 | 39.D6 | FU1100:LI | JB70 PANEL B | 39.D3
XT0111:22 | SC | 0V | WHT | 14 | 39.D6 | UV0291:24V(-) | JB70 PANEL B | 39.C5
SolarTools ver. 24.0.84.24712 (Jul 31, 2025)
Report date: 2/27/2026 8:31 AM

## JB72 GEN PANEL
JB72 GEN PANEL
Project # | 4M082
Project Name | STEEL REEF BURKE LLC
Revision | C.1_M1
Controls DE | J. UNGER
Phone:
Controls ME
Phone:
From | [5 empty] | To
Device ID | Cable (W) Conductor (SC) Jumper Clip (JC) | Wire No. | Wire ID | Gauge/Size | Page/Zone | Device ID | Location | Page/Zone
XT0335:1 | JC | FU0332 | CLIP | --- | 26.A4 | XT0335:2 | JB72 GEN PANEL | 26.A4
XT0335:2 | JC | FU0332 | CLIP | --- | 26.A4 | XT0335:3 | JB72 GEN PANEL | 26.B4
XT0335:3 | JC | FU0332 | CLIP | --- | 26.B4 | XT0335:4 | JB72 GEN PANEL | 26.B4
XT0335:4 | JC | FU0332 | CLIP | --- | 26.B4 | XT0335:5 | JB72 GEN PANEL | 26.B4
XT0335:5 | JC | FU0332 | CLIP | --- | 26.B4 | XT0335:6 | JB72 GEN PANEL | 26.B4
XT0335:6 | JC | FU0332 | CLIP | --- | 26.B4 | XT0335:7 | JB72 GEN PANEL | 26.C4
XT0335:7 | JC | FU0332 | CLIP | --- | 26.C4 | XT0335:8 | JB72 GEN PANEL | 26.C4
XT0335:8 | JC | FU0332 | CLIP | --- | 26.C4 | XT0335:9 | JB72 GEN PANEL | 26.C4
XT0335:9 | JC | FU0332 | CLIP | --- | 26.C4 | XT0335:10 | JB72 GEN PANEL | 26.C4
XT0336:1 | JC | 0V | CLIP | --- | 26.A4 | XT0336:2 | JB72 GEN PANEL | 26.B4
XT0336:2 | JC | 0V | CLIP | --- | 26.B4 | XT0336:3 | JB72 GEN PANEL | 26.B4
XT0336:3 | JC | 0V | CLIP | --- | 26.B4 | XT0336:4 | JB72 GEN PANEL | 26.B4
XT0336:4 | JC | 0V | CLIP | --- | 26.B4 | XT0336:5 | JB72 GEN PANEL | 26.B4
XT0336:5 | JC | 0V | CLIP | --- | 26.B4 | XT0336:6 | JB72 GEN PANEL | 26.C4
XT0336:6 | JC | 0V | CLIP | --- | 26.C4 | XT0336:7 | JB72 GEN PANEL | 26.C4
XT0336:7 | JC | 0V | CLIP | --- | 26.C4 | XT0336:8 | JB72 GEN PANEL | 26.C4
XT0336:8 | JC | 0V | CLIP | --- | 26.C4 | XT0336:9 | JB72 GEN PANEL | 26.C4
XT0336:9 | JC | 0V | CLIP | --- | 26.C4 | XT0336:10 | JB72 GEN PANEL | 26.D4
XT0350:2 | JC | CCT1(+) | CLIP | --- | 82.A4 | XT0350:1 | JB72 GEN PANEL | 82.A4
XT0350:4 | JC | CCT1(-) | CLIP | --- | 82.A4 | XT0350:3 | JB72 GEN PANEL | 82.A4
XT0351:1 | JC | VBUSA | CLIP | --- | 80.B4 | XT0351:2 | JB72 GEN PANEL | 80.B4
XT0351:11 | JC | VGENB | CLIP | --- | 81.B5 | XT0351:12 | JB72 GEN PANEL | 81.B5
XT0351:13 | JC | VGENC | CLIP | --- | 81.B5 | XT0351:14 | JB72 GEN PANEL | 81.B5
XT0351:3 | JC | VBUSB | CLIP | --- | 80.B4 | XT0351:4 | JB72 GEN PANEL | 80.B4
XT0351:5 | JC | VBUSC | CLIP | --- | 80.B4 | XT0351:6 | JB72 GEN PANEL | 80.B4
XT0351:9 | JC | VGENA | CLIP | --- | 81.B5 | XT0351:10 | JB72 GEN PANEL | 81.B5
XT0352:4 | SC | JW03524 | CLIP | -- | 82.B4 | XT0352:5 | JB72 GEN PANEL | 82.B4
XT0352:5 | SC | JW03525 | CLIP | -- | 82.B4 | XT0352:6 | JB72 GEN PANEL | 82.B4
XT0352:6 | SC | JW03526 | CLIP | -- | 82.B4 | XT0352:7 | JB72 GEN PANEL | 82.B4
AF0122:06 | SC | JP10 | VIO | 20 | 35.C7 | AF0122:38 | JB72 GEN PANEL | 35.C7
AF0121:01 | SC | 012101 | WHT | 20 | 35.C4 | KA0121:A1 | JB72 GEN PANEL | 35.C3
AF0121:03 | SC | KA0123A1 | WHT | 20 | 37.C7 | KA0123:A1 | JB72 GEN PANEL | 37.C5
AF0121:08 | SC | 012108 | WHT | 20 | 35.C7 | KA0128:A1 | JB72 GEN PANEL | 35.C5
AF0121:09 | SC | KA7610A1 | WHT | 20 | 105.B6 | KA7610:A1 | JB72 GEN PANEL | 105.B5
AF0121:14 | SC | KA033611 | WHT | 20 | 84.A6 | KA0336:11 | JB72 GEN PANEL | 84.A5
AF0121:17 | SC | 012117 | WHT | 20 | 35.C4 | KA0121:A2 | JB72 GEN PANEL | 35.C3
AF0121:19 | SC | KA0123A2 | WHT | 20 | 37.C7 | KA0123:A2 | JB72 GEN PANEL | 37.C5
AF0121:24 | SC | 012124 | WHT | 20 | 35.C7 | KA0128:A2 | JB72 GEN PANEL | 35.C5
AF0121:25 | SC | KA7610A2 | WHT | 20 | 105.B6 | KA7610:A2 | JB72 GEN PANEL | 105.B5
AF0121:30 | SC | KA4100A2 | WHT | 20 | 84.A6 | KA4100:A2 | JB72 GEN PANEL | 84.A6
AF0121:COM | SC | 0V | WHT | 16 | 28.B2 | XT0120:2 | JB72 GEN PANEL | 28.B1
AF0121:J | SC | * |  |  | 28.B2 | AF0122:P | JB72 GEN PANEL | 28.B3
AF0121:V+ | SC | FU0121 | WHT | 16 | 28.B2 | FU0121:LD | JB72 GEN PANEL | 28.B1
AF0122:00 | SC | 012200 | WHT | 20 | 36.C7 | KA0330:11 | JB72 GEN PANEL | 36.C6
AF0122:01 | SC | 012201 | WHT | 20 | 36.D7 | KA0331:11 | JB72 GEN PANEL | 36.D6
AF0122:02 | SC | KA031011 | WHT | 20 | 37.B7 | KA0310:11 | JB72 GEN PANEL | 37.B6
AF0122:32 | SC | 012232 | WHT | 20 | 36.C7 | KA0330:14 | JB72 GEN PANEL | 36.C6
AF0122:33 | SC | 012233 | WHT | 20 | 36.D7 | KA0331:14 | JB72 GEN PANEL | 36.D6
AF0122:34 | SC | KA031014 | WHT | 20 | 37.B7 | KA0310:14 | JB72 GEN PANEL | 37.B6
AF0122:COM | SC | AF0122N | WHT | 16 | 28.B3 | AF0123:COM | JB72 GEN PANEL | 28.B3
AF0122:COM | SC | AU0120N | WHT | 16 | 28.B3 | AU0120:COM | JB72 GEN PANEL | 28.A2
AF0122:J | SC | * |  |  | 28.B3 | AF0123:P | JB72 GEN PANEL | 28.B3
AF0122:V+ | SC | AF0122P | WHT | 16 | 28.B3 | AF0123:V+ | JB72 GEN PANEL | 28.B3
AF0122:V+ | SC | AU0120P | WHT | 16 | 28.B3 | AU0120:V+ | JB72 GEN PANEL | 28.A2
AF0123:SH | SC | IEG01405 | GRN | 14 | 28.B3 | IEG0140:5 | JB72 GEN PANEL | 28.B4
AF0123:SH | SC | AU0120G | GRN | 14 | 28.B3 | AU0120:GND | JB72 GEN PANEL | 28.A2 | C.1_M1: Updated wire color to Green
AT0140:13 VGEN-A | SC | VGENA | RED | 16 | 81.B6 | XT0351:9 | JB72 GEN PANEL | 81.B5
AT0140:14 VGEN-B | SC | VGENB | RED | 16 | 81.B6 | XT0351:11 | JB72 GEN PANEL | 81.B5
AT0140:15 VGEN-C | SC | VGENC | RED | 16 | 81.B6 | XT0351:13 | JB72 GEN PANEL | 81.B5
AT0140:17 VBUS-A | SC | VBUSA | RED | 16 | 80.B7 | XT0351:2 | JB72 GEN PANEL | 80.B4
AT0140:18 VBUS-B | SC | VBUSB | RED | 16 | 80.B7 | XT0351:3 | JB72 GEN PANEL | 80.B4
AT0140:19 VBUS-C | SC | VBUSC | RED | 16 | 80.B7 | XT0351:5 | JB72 GEN PANEL | 80.B4
AT0140:3 EX-D(-) | SC | 0V | WHT | 16 | 83.C7 | XT0336:6 | JB72 GEN PANEL | 26.C4
AT0140:36 I1(+) | SC | MCTA | BLU | 12 | 82.B7 | XT0352:1 | JB72 GEN PANEL | 82.B4
AT0140:37 I1(-) | SC | MCTAN | BLU | 12 | 82.B7 | XT0352:10 | JB72 GEN PANEL | 82.B6
AT0140:38 I2(+) | SC | MCTB | BLU | 12 | 82.B7 | XT0352:2 | JB72 GEN PANEL | 82.B4
AT0140:39 I2(-) | SC | MCTBN | BLU | 12 | 82.B7 | XT0352:9 | JB72 GEN PANEL | 82.B6
AT0140:4 EX-D(+) | SC | KA012314 | WHT | 16 | 83.C7 | KA0123:14 | JB72 GEN PANEL | 37.A6
AT0140:40 I3(+) | SC | MCTC | BLU | 12 | 82.B7 | XT0352:3 | JB72 GEN PANEL | 82.B4
AT0140:41 I3(-) | SC | MCTCN | BLU | 12 | 82.B7 | XT0352:8 | JB72 GEN PANEL | 82.B6
AT0140:56 FG | SC | AT0140G | GRN/YEL | 12 | 37.B3 | FRAME | JB72 GEN PANEL | 37.B2
AT0140:BAT(-) 48 | SC | 0V | WHT | 16 | 37.B3 | XT0336:6 | JB72 GEN PANEL | 26.C4
AT0140:BAT(+) 47 | SC | FU0334 | WHT | 16 | 37.B3 | XT0339:1 | JB72 GEN PANEL | 37.B5
AT0140:FLT 29 | SC | KA0310A2 | WHT | 20 | 37.B3 | KA0310:A2 | JB72 GEN PANEL | 37.B4
AT0140:FLT 30 | SC | 0V | WHT | 16 | 37.B3 | XT0336:6 | JB72 GEN PANEL | 26.C4
AU0120:COM | SC | 0V | WHT | 16 | 28.A2 | XT0120:2 | JB72 GEN PANEL | 28.B1
AU0120:V+ | SC | FU0120 | WHT | 16 | 28.A2 | FU0120:LD | JB72 GEN PANEL | 28.B1
FU0120:LI | SC | FU0122 | WHT | 14 | 28.B1 | FU0121:LI | JB72 GEN PANEL | 28.B1
FU0120:LI | SC | FU0122 | WHT | 14 | 28.B1 | FU0122:LD | JB72 GEN PANEL | 28.A1
FU0122:LI | SC | FU0332 | WHT | 14 | 28.A1 | XT0335:2 | JB72 GEN PANEL | 26.A4
FU0332:LD | SC | FU0332 | WHT | 12 | 26.A3 | XT0335:1 | JB72 GEN PANEL | 26.A4
FU0333:LD | SC | FU0333 | WHT | 16 | 35.A2 | XT0338:1 | JB72 GEN PANEL | 35.A3
FU0333:LI | SC | FU0332 | WHT | 16 | 35.A2 | XT0335:4 | JB72 GEN PANEL | 26.B4
FU0334:LD | SC | FU0334 | WHT | 16 | 37.A6 | XT0339:1 | JB72 GEN PANEL | 37.B5
FU0334:LI | SC | FU0332 | WHT | 16 | 37.A6 | XT0335:6 | JB72 GEN PANEL | 26.B4
GR0142: | SC | GR0142 | GRN | 14 | 10.A5 | IEG0140:4 | JB72 GEN PANEL | 10.A4
GR0143: | SC | GR0143 | GRN/YEL | 14 | 10.A4 | FRAME | JB72 GEN PANEL | 10.A3
GR0144: | SC | GR0144 | GRN/YEL | 14 | 10.A4 | FRAME | JB72 GEN PANEL | 10.A3
GR0145: | SC | GR0145 | GRN/YEL | 14 | 10.A4 | FRAME | JB72 GEN PANEL | 10.A3
IEG0140:7 | SC | AT0140LS(S) | GRN | 14 | 83.C6 | XT0354:3 | JB72 GEN PANEL | 83.C4
KA0121:11 | SC | FU0333 | WHT | 20 | 35.B3 | XT0338:1 | JB72 GEN PANEL | 35.A3
KA0121:14 | SC | KA018511 | WHT | 20 | 35.B3 | XT0338:3 | JB72 GEN PANEL | 35.B4
KA0123:11 | SC | FU0334 | WHT | 16 | 37.A6 | XT0339:1 | JB72 GEN PANEL | 37.B5
KA0123:A1 | SC | KA0123A1 | WHT | 20 | 37.C5 | KA0313:2 | JB72 GEN PANEL | 37.C5
KA0123:A2 | SC | KA0123A2 | WHT | 20 | 37.C5 | KA0313:7 | JB72 GEN PANEL | 37.C5
KA0128:11 | SC | FU0333 | WHT | 20 | 35.A3 | XT0338:1 | JB72 GEN PANEL | 35.A3
KA0128:11 | SC | FU0333 | WHT | 20 | 35.A3 | KA0335:21 | JB72 GEN PANEL | 35.A3
KA0128:21 | SC | KA012821 | WHT | 20 | 35.C6 | XT0337:1 | JB72 GEN PANEL | 35.C5
KA0128:24 | SC | KA012824 | WHT | 20 | 35.C6 | XT0337:2 | JB72 GEN PANEL | 35.D5
KA0310:24 | SC | KA0333A1 | WHT | 20 | 35.A3 | XT0338:2 | JB72 GEN PANEL | 35.A5
KA0310:24 | SC | KA0333A1 | WHT | 20 | 35.A3 | KA0335:22 | JB72 GEN PANEL | 35.A3
KA0310:A1 | SC | FU0334 | WHT | 20 | 37.B4 | XT0339:1 | JB72 GEN PANEL | 37.B5
KA0313:2 | SC | KA0123A1 | WHT | 20 | 37.C5 | KA0314:2 | JB72 GEN PANEL | 37.C5
KA0313:7 | SC | KA0123A2 | WHT | 20 | 37.C5 | KA0314:7 | JB72 GEN PANEL | 37.C5
KA0330:A1 | SC | KA0330A1 | WHT | 20 | 36.A5 | XT0338:5 | JB72 GEN PANEL | 36.A3
KA0330:A2 | SC | 0V | WHT | 20 | 36.A5 | KA0331:A2 | JB72 GEN PANEL | 36.A5
KA0331:A1 | SC | KA0331A1 | WHT | 20 | 36.A5 | XT0338:6 | JB72 GEN PANEL | 36.A3
KA0331:A2 | SC | 0V | WHT | 20 | 36.A5 | XT0336:5 | JB72 GEN PANEL | 26.B4
KA0332:11 | SC | KA033211 | WHT | 20 | 35.D6 | XT0337:3 | JB72 GEN PANEL | 35.D5
KA0332:14 | SC | KA033214 | WHT | 20 | 35.D6 | XT0337:4 | JB72 GEN PANEL | 35.D5
KA0332:A1 | SC | KA0332A1 | WHT | 20 | 35.B5 | XT0338:4 | JB72 GEN PANEL | 35.B5
KA0332:A2 | SC | 0V | WHT | 20 | 35.B5 | KA0333:A2 | JB72 GEN PANEL | 35.A5
KA0333:11 | SC | KA033311 | WHT | 20 | 35.D6 | KA0335:11 | JB72 GEN PANEL | 35.D6
KA0333:11 | SC | KA033311 | WHT | 20 | 35.D6 | XT0337:5 | JB72 GEN PANEL | 35.D5
KA0333:14 | SC | KA033314 | WHT | 20 | 35.D6 | KA0335:12 | JB72 GEN PANEL | 35.D6
KA0333:14 | SC | KA033314 | WHT | 20 | 35.D6 | XT0337:6 | JB72 GEN PANEL | 35.D5
KA0333:A1 | SC | KA0333A1 | WHT | 20 | 35.A5 | XT0338:2 | JB72 GEN PANEL | 35.A5
KA0333:A2 | SC | 0V | WHT | 20 | 35.A5 | XT0336:4 | JB72 GEN PANEL | 26.B4
KA0335:21 | SC | FU0333 | WHT | 20 | 35.A3 | KA0310:21 | JB72 GEN PANEL | 35.A3
KA0335:22 | SC | KA0333A1 | WHT | 20 | 35.A3 | KA0128:14 | JB72 GEN PANEL | 35.A3
KA0335:A1 | SC | ESTOP | WHT | 16 | 27.A5 | XT0120:4 | JB72 GEN PANEL | 27.A3
KA0335:A2 | SC | 0V | WHT | 20 | 27.A5 | XT0120:3 | JB72 GEN PANEL | 27.A6
KA0335:A2 | SC | 0V | WHT | 20 | 27.A5 | KA0336:A2 | JB72 GEN PANEL | 27.B5
KA0336:14 | SC | KA4100A1 | WHT | 20 | 84.A5 | KA4100:A1 | JB72 GEN PANEL | 84.A6
KA0336:A1 | SC | KA0131A1 | WHT | 16 | 27.B5 | XT0120:5 | JB72 GEN PANEL | 27.B3
PEG0140:4 | SC | PEG01404 | GRN/YEL | 12 | 82.B5 | XT0352:7 | JB72 GEN PANEL | 82.B4
XT0120:1 | SC | 0V | WHT | 14 | 28.A1 | XT0120:2 | JB72 GEN PANEL | 28.B1
XT0120:3 | SC | 0V | WHT | 14 | 27.A6 | XT0120:2 | JB72 GEN PANEL | 28.B1
XT0336:2 | SC | 0V | WHT | 14 | 26.B4 | XT0120:1 | JB72 GEN PANEL | 28.A1
AT0140:1 LS(+) | WC8009 | AT0140LS(+) | CLR | 16 | 83.C7 | XT0354:1 | JB72 GEN PANEL | 83.C4
AT0140:2 LS(-) | WC8009 | AT0140LS(-) | BLK | 16 | 83.C7 | XT0354:2 | JB72 GEN PANEL | 83.C4
FW5:1 | WC8009 | AT0140LS(S) | SH | 16 | 83.C6 | XT0354:3 | JB72 GEN PANEL | 83.C4
KA3420:A1 | SC | KA3420A1 | WHT | 20 | 88.B5 | AF0092:00 | JB70 PANEL A | 88.B7
KA3420:A2 | SC | KA3420A2 | WHT | 20 | 88.B5 | AF0092:16 | JB70 PANEL A | 88.B7
AU0120:L1 | WC006 | AU0060L2 | ENET | CABLE | 2.C1 | AU0060:L2 | JB70 PANEL B | 2.B1
AT0140:P2 | WC0014 | AT0140P2 | ENET | CABLE | 2.C3 | BA0002:RJ45 | JB70 PLC PANEL | 2.B5
IEG0140:1 | SC | IEG01401 | GRN | 14 | 10.B2 | GR0241: | JB72 LEFT RAIL | 10.B2
IEG0140:8 | SC | IEG014008 | GRN | 14 | 46.C6 | AF0185:SH | JB72 LEFT RAIL | 46.C6
XT0335:3 | SC | FU0332 | WHT | 14 | 26.B4 | FU0182:LI | JB72 LEFT RAIL | 46.B3
XT0335:8 | SC | FU0332 | WHT | 12 | 26.C4 | XT1207:1 | JB72 LEFT RAIL | 8.C3
XT0336:3 | SC | 0V | WHT | 14 | 26.B4 | XT0180:1 | JB72 LEFT RAIL | 46.C2
XT0336:8 | SC | 0V | WHT | 14 | 26.C4 | XT1207:2 | JB72 LEFT RAIL | 8.C3
XT0338:3 | SC | KA018511 | WHT | 20 | 35.B4 | KA0185:11 | JB72 LEFT RAIL | 35.B4
XT0338:4 | SC | KA0332A1 | WHT | 20 | 35.B5 | KA0185:14 | JB72 LEFT RAIL | 35.B4
AT0140:P1 | WC0140 | AT0140P1 | ENET | CABLE | 2.C3 | BA0121:RJ45 | JB72 LEFT RAIL | 2.C4
IEG0140:6 | SC | IEG01406 | GRN | 14 | 38.C6 | XT0500:2 | JB72 VIB PANEL | 38.C5
XT0335:3 | SC | FU0332 | WHT | 14 | 26.B4 | FU0510:LI | JB72 VIB PANEL | 38.C1
XT0336:3 | SC | 0V | WHT | 14 | 26.B4 | XT0501:1 | JB72 VIB PANEL | 38.A1
AU0120:L2 | WC0012 | AU0120L2 | ENET | CABLE | 2.C1 | AF0510:L1 | JB72 VIB PANEL | 2.C2
XT0525:1 | WC1242 | UA42011 | RED | 20 | 87.A5 | AF0500:01 | JB72 VIB PANEL | 87.A6
XT0525:2 | WC1242 | UA42012 | CLR | 20 | 87.A5 | AF0500:02 | JB72 VIB PANEL | 87.A6
XT0525:3 | WC1242 | UA42013 | BLK | 20 | 87.A5 | AF0500:03 | JB72 VIB PANEL | 87.A6
XT0525:4 | WC1242 | UA4201S | SH | 20 | 87.A5 | AF0500:07 | JB72 VIB PANEL | 87.A6
XT0525:5 | WC1243 | UA42311 | RED | 20 | 87.B5 | AF0510:09 | JB72 VIB PANEL | 87.B6
XT0525:6 | WC1243 | UA42312 | CLR | 20 | 87.B5 | AF0510:10 | JB72 VIB PANEL | 87.B6
XT0525:7 | WC1243 | UA42313 | BLK | 20 | 87.B5 | AF0510:12 | JB72 VIB PANEL | 87.B6
XT0525:8 | WC1243 | UA4231S | SH | 20 | 87.B5 | AF0510:27 | JB72 VIB PANEL | 87.B6
XT0525:9 | WC1244 | UA42301 | RED | 20 | 87.B5 | AF0510:13 | JB72 VIB PANEL | 87.B6
XT0525:10 | WC1244 | UA42302 | CLR | 20 | 87.B5 | AF0510:14 | JB72 VIB PANEL | 87.B6
XT0525:11 | WC1244 | UA42303 | BLK | 20 | 87.B5 | AF0510:16 | JB72 VIB PANEL | 87.B6
XT0525:12 | WC1244 | UA4230S | SH | 20 | 87.B5 | AF0510:31 | JB72 VIB PANEL | 87.B6
XT0525:13 | WC1245 | UA42411 | RED | 20 | 87.B5 | AF0510:01 | JB72 VIB PANEL | 87.B6
XT0525:14 | WC1245 | UA42412 | CLR | 20 | 87.B5 | AF0510:02 | JB72 VIB PANEL | 87.B6
XT0525:15 | WC1245 | UA42413 | BLK | 20 | 87.B5 | AF0510:04 | JB72 VIB PANEL | 87.B6
XT0525:16 | WC1245 | UA4241S | SH | 20 | 87.B5 | AF0510:19 | JB72 VIB PANEL | 87.B6
XT0525:17 | WC1246 | UA42401 | RED | 20 | 87.C5 | AF0510:05 | JB72 VIB PANEL | 87.C6
XT0525:18 | WC1246 | UA42402 | CLR | 20 | 87.C5 | AF0510:06 | JB72 VIB PANEL | 87.C6
XT0525:19 | WC1246 | UA42403 | BLK | 20 | 87.C5 | AF0510:08 | JB72 VIB PANEL | 87.C6
XT0525:20 | WC1246 | UA4240S | SH | 20 | 87.C5 | AF0510:23 | JB72 VIB PANEL | 87.C6
SolarTools ver. 24.0.84.24712 (Jul 31, 2025)
Report date: 2/27/2026 8:31 AM

## JB72 LEFT RAIL
JB72 LEFT RAIL
Project # | 4M082
Project Name | STEEL REEF BURKE LLC
Revision | C
Controls DE | J. UNGER
Phone:
Controls ME
Phone:
From | [5 empty] | To
Device ID | Cable (W) Conductor (SC) Jumper Clip (JC) | Wire No. | Wire ID | Gauge/Size | Page/Zone | Device ID | Location | Page/Zone
AF0182:01 | SC | JP1 | VIO | 20 | 47.A7 | AF0182:33 | JB72 LEFT RAIL | 47.A7
AF0182:07 | SC | JP4 | VIO | 20 | 45.A7 | AF0182:39 | JB72 LEFT RAIL | 45.A7
AF0182:15 | SC | JP19 | VIO | 20 | 45.B7 | AF0182:47 | JB72 LEFT RAIL | 45.B7
AF0181:00 | SC | 018100 | WHT | 20 | 48.A7 | KA0180:A1 | JB72 LEFT RAIL | 48.A5
AF0181:02 | SC | KA0181A1 | WHT | 20 | 45.C7 | KA0181:A1 | JB72 LEFT RAIL | 45.C5
AF0181:10 | SC | 018110 | WHT | 20 | 48.B7 | KA0185:A1 | JB72 LEFT RAIL | 48.B5
AF0181:16 | SC | 018116 | WHT | 20 | 48.A7 | KA0180:A2 | JB72 LEFT RAIL | 48.A5
AF0181:18 | SC | KA0181A2 | WHT | 20 | 45.C7 | KA0181:A2 | JB72 LEFT RAIL | 45.C5
AF0181:26 | SC | 018126 | WHT | 20 | 48.B7 | XT0181:2 | JB72 LEFT RAIL | 48.B5
AF0181:COM | SC | 0V | WHT | 16 | 46.C3 | XT0180:1 | JB72 LEFT RAIL | 46.C2
AF0181:J | SC | * |  |  | 46.C3 | AF0182:P | JB72 LEFT RAIL | 46.C4
AF0181:V+ | SC | FU0181 | WHT | 16 | 46.C3 | FU0181:LD | JB72 LEFT RAIL | 46.C2
AF0182:COM | SC | AF0182N | WHT | 16 | 46.C4 | AF0183:COM | JB72 LEFT RAIL | 46.B4
AF0182:COM | SC | AU0180N | WHT | 16 | 46.C4 | AU0180:COM | JB72 LEFT RAIL | 46.B3
AF0182:J | SC | * |  |  | 46.C4 | AF0183:P | JB72 LEFT RAIL | 46.B4
AF0182:V+ | SC | AF0182P | WHT | 16 | 46.C4 | AF0183:V+ | JB72 LEFT RAIL | 46.B4
AF0182:V+ | SC | AU0180P | WHT | 16 | 46.C4 | AU0180:V+ | JB72 LEFT RAIL | 46.B3
AF0183:COM | SC | AF0183N | WHT | 16 | 46.B4 | AF0184:COM | JB72 LEFT RAIL | 46.C5
AF0183:J | SC | * |  |  | 46.B4 | AF0184:P | JB72 LEFT RAIL | 46.C5
AF0183:V+ | SC | AF0183P | WHT | 16 | 46.B4 | AF0184:V+ | JB72 LEFT RAIL | 46.C5
AF0184:COM | SC | AF0184N | WHT | 16 | 46.C5 | AF0185:COM | JB72 LEFT RAIL | 46.C6
AF0184:J | SC | * |  |  | 46.C5 | AF0185:P | JB72 LEFT RAIL | 46.C6
AF0184:SH | SC | AF0184SH | GRN | 14 | 46.C5 | AF0185:SH | JB72 LEFT RAIL | 46.C6
AF0184:SH | SC | AU0180G | GRN | 14 | 46.C5 | AU0180:GND | JB72 LEFT RAIL | 46.B3
AF0184:V+ | SC | AF0184P | WHT | 16 | 46.C5 | AF0185:V+ | JB72 LEFT RAIL | 46.C6
AU0180:COM | SC | 0V | WHT | 16 | 46.B3 | XT0180:1 | JB72 LEFT RAIL | 46.C2
AU0180:V+ | SC | FU0180 | WHT | 16 | 46.B3 | FU0180:LD | JB72 LEFT RAIL | 46.C2
BA0120:V1(-) | SC | 0V | WHT | 16 | 8.C1 | XT1207:2 | JB72 LEFT RAIL | 8.C3
BA0120:V1(+) | SC | FU0133LD | WHT | 16 | 8.C1 | FU0133:LD | JB72 LEFT RAIL | 8.C2
BA0121:V1(-) | SC | 0V | WHT | 16 | 8.C1 | XT1207:2 | JB72 LEFT RAIL | 8.C3
BA0121:V1(+) | SC | FU0134LD | WHT | 16 | 8.C1 | FU0134:LD | JB72 LEFT RAIL | 8.D2
FU0133:LI | SC | FU0332 | WHT | 16 | 8.C2 | XT1207:1 | JB72 LEFT RAIL | 8.C3
FU0134:LI | SC | FU0332 | WHT | 16 | 8.D2 | XT1207:1 | JB72 LEFT RAIL | 8.C3
FU0180:LI | SC | FU0182 | WHT | 14 | 46.C2 | FU0181:LI | JB72 LEFT RAIL | 46.C2
FU0180:LI | SC | FU0182 | WHT | 14 | 46.C2 | FU0182:LD | JB72 LEFT RAIL | 46.B3
KA0185:A2 | SC | KA0185A2 | WHT | 20 | 48.B5 | XT0181:1 | JB72 LEFT RAIL | 48.B5
AU0180:L2 | WC0018 | AU0180L2 | ENET | CABLE | 2.C3 | BA0120:RJ45 | JB72 LEFT RAIL | 2.C4
KA0182:A1 | SC | KA0182A1 | WHT | 20 | 45.D5 | AF0076:14 | JB70 PANEL B | 45.D7
KA0182:A2 | SC | KA0182A2 | WHT | 20 | 45.D5 | AF0076:30 | JB70 PANEL B | 45.D7
KA0183:A1 | SC | KA0183A1 | WHT | 20 | 45.D5 | AF0076:03 | JB70 PANEL B | 45.D7
KA0183:A2 | SC | KA0183A2 | WHT | 20 | 45.D5 | AF0076:19 | JB70 PANEL B | 45.D7
AF0185:SH | SC | IEG014008 | GRN | 14 | 46.C6 | IEG0140:8 | JB72 GEN PANEL | 46.C6
FU0182:LI | SC | FU0332 | WHT | 14 | 46.B3 | XT0335:3 | JB72 GEN PANEL | 26.B4
GR0241: | SC | IEG01401 | GRN | 14 | 10.B2 | IEG0140:1 | JB72 GEN PANEL | 10.B2
KA0185:11 | SC | KA018511 | WHT | 20 | 35.B4 | XT0338:3 | JB72 GEN PANEL | 35.B4
KA0185:14 | SC | KA0332A1 | WHT | 20 | 35.B4 | XT0338:4 | JB72 GEN PANEL | 35.B5
XT0180:1 | SC | 0V | WHT | 14 | 46.C2 | XT0336:3 | JB72 GEN PANEL | 26.B4
XT1207:1 | SC | FU0332 | WHT | 12 | 8.C3 | XT0335:8 | JB72 GEN PANEL | 26.C4
XT1207:2 | SC | 0V | WHT | 14 | 8.C3 | XT0336:8 | JB72 GEN PANEL | 26.C4
BA0121:RJ45 | WC0140 | AT0140P1 | ENET | CABLE | 2.C4 | AT0140:P1 | JB72 GEN PANEL | 2.C3
AU0180:L1 | WC0051 | AF0510L2 | ENET | CABLE | 2.C3 | AF0510:L2 | JB72 VIB PANEL | 2.C2
Report date: 2/27/2026 8:31 AM |  |  |  |  | SolarTools ver. 24.0.84.24712 (Jul 31, 2025)

## JB72 RIGHT RAIL
JB72 RIGHT RAIL
Project # | 4M082
Project Name | STEEL REEF BURKE LLC
Revision | C
Controls DE | J. UNGER
Phone:
Controls ME
Phone:
From | [5 empty] | To
Device ID | Cable (W) Conductor (SC) Jumper Clip (JC) | Wire No. | Wire ID | Gauge/Size | Page/Zone | Device ID | Location | Page/Zone
GR0141: | SC | GR0141 | GRN/YEL | 14 | 10.B4 | FRAME | JB72 RIGHT RAIL | 10.B4
Report date: 2/27/2026 8:31 AM |  |  |  |  | SolarTools ver. 24.0.84.24712 (Jul 31, 2025)

## JB72 VIB PANEL
JB72 VIB PANEL
Project # | 4M082
Project Name | STEEL REEF BURKE LLC
Revision | C
Controls DE | J. UNGER
Phone:
Controls ME
Phone:
From | [5 empty] | To
Device ID | Cable (W) Conductor (SC) Jumper Clip (JC) | Wire No. | Wire ID | Gauge/Size | Page/Zone | Device ID | Location | Page/Zone
XT0501:1 | JC | 0V | CLIP | --- | 38.A1 | XT0501:2 | JB72 VIB PANEL | 38.C1
AF0500:12 | SC | XT05001 | GRN | 16 | 38.A6 | XT0500:1 | JB72 VIB PANEL | 38.C5
AF0510:32 | SC | XT05001 | GRN | 16 | 38.A5 | XT0500:1 | JB72 VIB PANEL | 38.C5
AF0510:53 | SC | 0V | WHT | 16 | 38.A5 | XT0501:2 | JB72 VIB PANEL | 38.C1
AF0510:55 | SC | FU0510 | WHT | 16 | 38.A5 | FU0510:LD | JB72 VIB PANEL | 38.C1
AF0500:LBUS | WC8050 | AF0500LBUS | BUS | CABLE | 38.A6 | AF0510:RBUS | JB72 VIB PANEL | 38.A5
FU0510:LI | SC | FU0332 | WHT | 14 | 38.C1 | XT0335:3 | JB72 GEN PANEL | 26.B4
XT0500:2 | SC | IEG01406 | GRN | 14 | 38.C5 | IEG0140:6 | JB72 GEN PANEL | 38.C6
XT0501:1 | SC | 0V | WHT | 14 | 38.A1 | XT0336:3 | JB72 GEN PANEL | 26.B4
AF0510:L1 | WC0012 | AU0120L2 | ENET | CABLE | 2.C2 | AU0120:L2 | JB72 GEN PANEL | 2.C1
AF0500:01 | WC1242 | UA42011 | RED | 20 | 87.A6 | XT0525:1 | JB72 GEN PANEL | 87.A5
AF0500:02 | WC1242 | UA42012 | CLR | 20 | 87.A6 | XT0525:2 | JB72 GEN PANEL | 87.A5
AF0500:03 | WC1242 | UA42013 | BLK | 20 | 87.A6 | XT0525:3 | JB72 GEN PANEL | 87.A5
AF0500:07 | WC1242 | UA4201S | SH | 20 | 87.A6 | XT0525:4 | JB72 GEN PANEL | 87.A5
AF0510:09 | WC1243 | UA42311 | RED | 20 | 87.B6 | XT0525:5 | JB72 GEN PANEL | 87.B5
AF0510:10 | WC1243 | UA42312 | CLR | 20 | 87.B6 | XT0525:6 | JB72 GEN PANEL | 87.B5
AF0510:12 | WC1243 | UA42313 | BLK | 20 | 87.B6 | XT0525:7 | JB72 GEN PANEL | 87.B5
AF0510:27 | WC1243 | UA4231S | SH | 20 | 87.B6 | XT0525:8 | JB72 GEN PANEL | 87.B5
AF0510:13 | WC1244 | UA42301 | RED | 20 | 87.B6 | XT0525:9 | JB72 GEN PANEL | 87.B5
AF0510:14 | WC1244 | UA42302 | CLR | 20 | 87.B6 | XT0525:10 | JB72 GEN PANEL | 87.B5
AF0510:16 | WC1244 | UA42303 | BLK | 20 | 87.B6 | XT0525:11 | JB72 GEN PANEL | 87.B5
AF0510:31 | WC1244 | UA4230S | SH | 20 | 87.B6 | XT0525:12 | JB72 GEN PANEL | 87.B5
AF0510:01 | WC1245 | UA42411 | RED | 20 | 87.B6 | XT0525:13 | JB72 GEN PANEL | 87.B5
AF0510:02 | WC1245 | UA42412 | CLR | 20 | 87.B6 | XT0525:14 | JB72 GEN PANEL | 87.B5
AF0510:04 | WC1245 | UA42413 | BLK | 20 | 87.B6 | XT0525:15 | JB72 GEN PANEL | 87.B5
AF0510:19 | WC1245 | UA4241S | SH | 20 | 87.B6 | XT0525:16 | JB72 GEN PANEL | 87.B5
AF0510:05 | WC1246 | UA42401 | RED | 20 | 87.C6 | XT0525:17 | JB72 GEN PANEL | 87.C5
AF0510:06 | WC1246 | UA42402 | CLR | 20 | 87.C6 | XT0525:18 | JB72 GEN PANEL | 87.C5
AF0510:08 | WC1246 | UA42403 | BLK | 20 | 87.C6 | XT0525:19 | JB72 GEN PANEL | 87.C5
AF0510:23 | WC1246 | UA4240S | SH | 20 | 87.C6 | XT0525:20 | JB72 GEN PANEL | 87.C5
AF0510:L2 | WC0051 | AF0510L2 | ENET | CABLE | 2.C2 | AU0180:L1 | JB72 LEFT RAIL | 2.C3
SolarTools ver. 24.0.84.24712 (Jul 31, 2025)
Report date: 2/27/2026 8:31 AM

## MCC RAIL
MCC RAIL
Project # | 4M082
Project Name | STEEL REEF BURKE LLC
Revision | C.1_M2
Controls DE | J. UNGER
Phone:
Controls ME
Phone:
From | [5 empty] | To
Device ID | Cable (W) Conductor (SC) Jumper Clip (JC) | Wire No. | Wire ID | Gauge/Size | Page/Zone | Device ID | Location | Page/Zone
XT0100:1 | JC | 0V | CLIP | --- | 30.C2 | XT0100:2 | MCC RAIL | 30.C2
XT1124:1 | JC | FU0332 | CLIP | --- | 29.A4 | XT1124:2 | MCC RAIL | 29.B4
XT1124:2 | JC | FU0332 | CLIP | --- | 29.B4 | XT1124:3 | MCC RAIL | 29.C4
XT1124:3 | JC | FU0332 | CLIP | --- | 29.C4 | XT1124:4 | MCC RAIL | 29.C4 | C.1_M2:Updated the XT1124 terminal sequence, so terminals 1 through 4 (24V) and 5 through 8 (0V) can be jumpered.
XT1124:5 | JC | 0V | CLIP | --- | 29.A4 | XT1124:6 | MCC RAIL | 29.B4
XT1124:6 | JC | 0V | CLIP | --- | 29.B4 | XT1124:7 | MCC RAIL | 29.C4
XT1124:7 | JC | 0V | CLIP | --- | 29.C4 | XT1124:8 | MCC RAIL | 29.C4
AF0111:00 | SC | 011100 | WHT | 20 | 34.A6 | KA7000:A1 | MCC RAIL | 34.A6
AF0111:01 | SC | 011101 | WHT | 20 | 34.A6 | KA7001:A1 | MCC RAIL | 34.A6
AF0111:02 | SC | 011102 | WHT | 20 | 34.B6 | KA7002:A1 | MCC RAIL | 34.B6
AF0111:03 | SC | 011103 | WHT | 20 | 34.B6 | KA7003:A1 | MCC RAIL | 34.B6
AF0111:04 | SC | 011104 | WHT | 20 | 34.C6 | KA7004:A1 | MCC RAIL | 34.C6
AF0111:05 | SC | 011105 | WHT | 20 | 34.C6 | KA7005:A1 | MCC RAIL | 34.C6
AF0111:06 | SC | 011106 | WHT | 20 | 34.D6 | KA7006:A1 | MCC RAIL | 34.D6
AF0111:07 | SC | 011107 | WHT | 20 | 34.D6 | KA7007:A1 | MCC RAIL | 34.D6
AF0111:09 | SC | 011109 | WHT | 20 | 34.B4 | KA7009:A1 | MCC RAIL | 34.B3
AF0111:10 | SC | 011110 | WHT | 20 | 34.B4 | KA7010:A1 | MCC RAIL | 34.C3
AF0111:11 | SC | 011111 | WHT | 20 | 34.C4 | KA7011:A1 | MCC RAIL | 34.C3
AF0111:12 | SC | 011112 | WHT | 20 | 34.D4 | KA7012:A1 | MCC RAIL | 34.D3
AF0111:13 | SC | 011113 | WHT | 20 | 34.D4 | KA7013:A1 | MCC RAIL | 34.D3
AF0111:16 | SC | 011116 | WHT | 20 | 34.A6 | KA7000:A2 | MCC RAIL | 34.A6
AF0111:17 | SC | 011117 | WHT | 20 | 34.A6 | KA7001:A2 | MCC RAIL | 34.A6
AF0111:18 | SC | 011118 | WHT | 20 | 34.B6 | KA7002:A2 | MCC RAIL | 34.B6
AF0111:19 | SC | 011119 | WHT | 20 | 34.B6 | KA7003:A2 | MCC RAIL | 34.B6
AF0111:20 | SC | 011120 | WHT | 20 | 34.C6 | KA7004:A2 | MCC RAIL | 34.C6
AF0111:21 | SC | 011121 | WHT | 20 | 34.C6 | KA7005:A2 | MCC RAIL | 34.C6
AF0111:22 | SC | 011122 | WHT | 20 | 34.D6 | KA7006:A2 | MCC RAIL | 34.D6
AF0111:23 | SC | 011123 | WHT | 20 | 34.D6 | KA7007:A2 | MCC RAIL | 34.D6
AF0111:24 | SC | 011124 | WHT | 20 | 34.A4 | KA7008:A2 | MCC RAIL | 34.A4
AF0111:25 | SC | 011125 | WHT | 20 | 34.B4 | KA7009:A2 | MCC RAIL | 34.B3
AF0111:26 | SC | 011126 | WHT | 20 | 34.B4 | KA7010:A2 | MCC RAIL | 34.C3
AF0111:27 | SC | 011127 | WHT | 20 | 34.C4 | KA7011:A2 | MCC RAIL | 34.C3
AF0111:28 | SC | 011128 | WHT | 20 | 34.D4 | KA7012:A2 | MCC RAIL | 34.D3
AF0111:29 | SC | 011129 | WHT | 20 | 34.D4 | KA7013:A2 | MCC RAIL | 34.D3
AF0111:COM | SC | AU0110N | WHT | 20 | 30.B3 | AU0110:COM | MCC RAIL | 30.B2
AF0111:J | SC | * |  |  | 30.B3 | AF0112:P | MCC RAIL | 30.B3
AF0111:V+ | SC | AU0110P | WHT | 20 | 30.B3 | AU0110:V+ | MCC RAIL | 30.B2
AF0112:COM | SC | 0V | WHT | 14 | 30.B3 | XT0100:2 | MCC RAIL | 30.C2
AF0112:COM | SC | AF0113N | WHT | 20 | 30.B3 | AF0113:COM | MCC RAIL | 30.B4
AF0112:J | SC | * |  |  | 30.B3 | AF0113:P | MCC RAIL | 30.B4
AF0112:V+ | SC | FU0111 | WHT | 16 | 30.B3 | FU0111:LD | MCC RAIL | 30.C2
AF0112:V+ | SC | AF0113P | WHT | 20 | 30.B3 | AF0113:V+ | MCC RAIL | 30.B4
AF0113:COM | SC | AF0114N | WHT | 20 | 30.B4 | AF0114:COM | MCC RAIL | 30.B5
AF0113:J | SC | * |  |  | 30.B4 | AF0114:P | MCC RAIL | 30.B5
AF0113:V+ | SC | AF0114P | WHT | 20 | 30.B4 | AF0114:V+ | MCC RAIL | 30.B5
AF0114:SH | SC | IEG02573 | GRN | 14 | 30.B5 | IEG0257:3 | MCC RAIL | 30.C5
AF0114:SH | SC | AU0110G | GRN | 14 | 30.B5 | AU0110:GND | MCC RAIL | 30.B2
AU0110:COM | SC | 0V | WHT | 14 | 30.B2 | XT0100:1 | MCC RAIL | 30.C2 | C.1_M2: Added 0V wire for AU0110:COM.
AU0110:V+ | SC | FU0110 | WHT | 14 | 30.B2 | FU0110:LD | MCC RAIL | 30.C2
BA0110:V1(-) | SC | 0V | WHT | 16 | 29.A2 | XT1124:5 | MCC RAIL | 29.A4
BA0110:V1(+) | SC | FU1110 | WHT | 16 | 29.A2 | FU1110:LD | MCC RAIL | 29.A3
BA0111:V1(-) | SC | 0V | WHT | 16 | 29.B2 | XT1124:6 | MCC RAIL | 29.B4
BA0111:V1(+) | SC | FU1111 | WHT | 16 | 29.B2 | FU1111:LD | MCC RAIL | 29.B3
BA0112:V1(-) | SC | 0V | WHT | 16 | 29.C2 | XT1124:8 | MCC RAIL | 29.C4
BA0112:V1(+) | SC | FU1112 | WHT | 16 | 29.C2 | FU1112:LD | MCC RAIL | 29.C3
FU0110:LI | SC | FU0332 | WHT | 14 | 30.C2 | FU0111:LI | MCC RAIL | 30.C2
FU0110:LI | SC | FU0332 | WHT | 14 | 30.C2 | XT1124:3 | MCC RAIL | 29.C4
FU1110:LI | SC | FU0332 | WHT | 14 | 29.A3 | XT1124:1 | MCC RAIL | 29.A4
FU1111:LI | SC | FU0332 | WHT | 14 | 29.B3 | XT1124:2 | MCC RAIL | 29.B4
FU1112:LI | SC | FU0332 | WHT | 14 | 29.C3 | XT1124:4 | MCC RAIL | 29.C4
GR0257: | SC | IEG02572 | GRN | 14 | 10.C4 | IEG0257:2 | MCC RAIL | 10.C4
IEG0110: | SC | IEG02571 | GRN | 14 | 30.C4 | IEG0257:1 | MCC RAIL | 30.C4
KA7002:11 | SC | KA700211 | WHT | 20 | 32.C3 | KA7003:22 | MCC RAIL | 32.C3
KA7002:14 | SC | KA700214 | WHT | 20 | 32.C3 | KA7003:14 | MCC RAIL | 32.C3
KA7002:22 | SC | KA700311 | WHT | 20 | 32.C3 | KA7003:11 | MCC RAIL | 32.C3
KA7004:11 | SC | KA700411 | WHT | 20 | 32.D3 | KA7005:22 | MCC RAIL | 32.D3
KA7004:14 | SC | KA700414 | WHT | 20 | 32.D3 | KA7005:14 | MCC RAIL | 32.D3
KA7004:22 | SC | KA700511 | WHT | 20 | 32.D3 | KA7005:11 | MCC RAIL | 32.D3
KA7006:11 | SC | KA700611 | WHT | 20 | 32.D7 | KA7007:22 | MCC RAIL | 32.D6
KA7006:14 | SC | KA700614 | WHT | 20 | 32.D7 | KA7007:14 | MCC RAIL | 32.D7
KA7006:22 | SC | KA700711 | WHT | 20 | 32.D6 | KA7007:11 | MCC RAIL | 32.D7
XT1124:6 | SC | 0V | WHT | 14 | 29.C4 | XT0100:1 | MCC RAIL | 30.C2
AU0110:L1 | WC0110 | AU0110L1 | ENET | CABLE | 2.C7 | BA0110:RJ45 | MCC RAIL | 2.C6
AU0110:L2 | WC0111 | AU0110L2 | ENET | CABLE | 2.C7 | BA0111:RJ45 | MCC RAIL | 2.C6
SolarTools ver. 24.0.84.24712 (Jul 31, 2025)
Report date: 2/27/2026 8:31 AM

## Panel Errors
Panel Errors
Project # | 4M082
Project Name | STEEL REEF BURKE LLC
Revision | C
Controls DE | J. UNGER
Phone:
Controls ME
Phone:
From | [6 empty] | To
Device ID | Location | Cable (W) Conductor (SC) Jumper Clip (JC) | Wire ID | Wire No. | Gauge/Size | Page/Zone | Device ID | Location | Page/Zone
XTFG1:122 | PANEL | SC |  | * |  | 9.A6 | FG1:88 | PANEL | 9.A6
Report date: 2/27/2026 8:31 AM |  |  |  | SolarTools ver. 24.0.84.24712 (Jul 31, 2025)

## Cable Part Numbers
Cable Part Numbers |  |  | SolarTools ver. 24.0.84.24712 (Jul 31, 2025)
Project # | 4M082
Report date: 2/27/2026 8:31 AM
Project Name | STEEL REEF BURKE LLC
Revision | C
Controls DE | J. UNGER
Phone:
Controls ME
Phone:
Device ID |  | Part Number |  | Description
WC0101 |  | 1302073-36 |  | CABLE, ETHERNET - 36 INCHES
WC5072 |  | PART OF 1103208-100 |  | CABLE, 2 CONDUCTOR UNSHIELDED PART OF HORN
WC0080 |  | 2684693-54 |  | CABLE, EXTENSION, BACKPLANE
WC0001 |  | 1302073-36 |  | CABLE, ETHERNET - 36 INCHES
WC0003 |  | 1302073-36 |  | CABLE, ETHERNET - 36 INCHES
WC0007 |  | 1302073-36 |  | CABLE, ETHERNET - 36 INCHES
WC0008 |  | 1302073-36 |  | CABLE, ETHERNET - 36 INCHES
WC0009 |  | 1302073-36 |  | CABLE, ETHERNET - 36 INCHES
WC0010 |  | 1302073-36 |  | CABLE, ETHERNET - 36 INCHES
WC0012 |  | 1302073-36 |  | CABLE, ETHERNET - 36 INCHES
WC0018 |  | 1302073-36 |  | CABLE, ETHERNET - 36 INCHES
WC0041 |  | 1302073-36 |  | CABLE, ETHERNET - 36 INCHES
WC0042 |  | 1302073-36 |  | CABLE, ETHERNET - 36 INCHES
WC0045 |  | 1302073-36 |  | CABLE, ETHERNET - 36 INCHES
WC0051 |  | 1302073-36 |  | CABLE, ETHERNET - 36 INCHES
WC0110 |  | 1302073-36 |  | CABLE, ETHERNET - 36 INCHES
WC0111 |  | 1302073-36 |  | CABLE, ETHERNET - 36 INCHES
WC0140 |  | 1302073-36 |  | CABLE, ETHERNET - 36 INCHES
WC0605 |  | 1302073-36 |  | CABLE, ETHERNET - 36 INCHES
WC0680 |  | 1302073-36 |  | CABLE
WC1242 |  | 1075034-5 |  | PVC, 1 TRIAD TWISTED SHIELDED
WC1243 |  | 1075034-5 |  | PVC, 1 TRIAD TWISTED SHIELDED
WC1244 |  | 1075034-5 |  | PVC, 1 TRIAD TWISTED SHIELDED
WC1245 |  | 1075034-5 |  | PVC, 1 TRIAD TWISTED SHIELDED
WC1246 |  | 1075034-5 |  | PVC, 1 TRIAD TWISTED SHIELDED
WC4524 |  | 1075034-2 |  | PVC, 1 PAIR TWISTED SHIELDED
WC8009 |  | 1075034-3 |  | PVC, 1 PAIR TWISTED SHIELDED
WC8040 |  | 1322418-90 |  | CABLE, SUPPLIED BY OTHERS
WC8041 |  | 1322418-90 |  | CABLE, SYTSTEM FUNCTION
WC8042 |  | 1322418-90 |  | CABLE, SYTSTEM FUNCTION
WC8050 |  | 1322418-90 |  | CABLE, SUPPLIED BY OTHERS
WC9001 |  | 1302073-36 |  | CABLE, ETHERNET - 36 INCHES
WC9111 |  | 1302073-36 |  | CABLE, ETHERNET - 36 INCHES

## Part Number List
Part Number List |  | SolarTools ver. 24.0.84.24712 (Jul 31, 2025)
Project # | 4M082
Report date: 2/27/2026 8:31 AM
Project Name | STEEL REEF BURKE LLC
Revision | C
Controls DE | J. UNGER
Phone:
Controls ME
Phone:
Device ID | Part Number | Description | Location
AT1100 | 1577354-4502 | WORKSTATION, VERSA VIEW 1200H | CONTROL,JB70;TT6
HA0472 | 1103208-101 | HORN, START SYSTEM ALARM | CONTROL,JB70;TT6
SA0471 | 1035040-1652,2380746-2 | SELECTOR SWITCH, SPEED/LOAD | CONTROL,JB70;TT6
SA0472 | 1035040-125,2380746-2 | SELECTOR SWITCH, VOLTAGE | CONTROL,JB70;TT6
SA0473 | 1035040-862,2380746-5 | SELECTOR SWITCH, OFF/LOCAL/AUXILIARY | CONTROL,JB70;TT6
SB0471 | 1035040-119,2380746-1 | PUSHBUTTON SWITCH, HORN SILENCE | CONTROL,JB70;TT6
SB0472 | 1035040-32,2380746-4 | PUSHBUTTON SWITCH, EMERGENCY STOP | CONTROL,JB70;TT6
SB0473 | 1035040-855,2380746-1 | PUSHBUTTON SWITCH, ACKNOWLEDGE | CONTROL,JB70;TT6
SB0474 | 1035040-856,2380746-1 | PUSHBUTTON SWITCH, RESET | CONTROL,JB70;TT6
SH0470 | 1035040-108,2380746-3 | LIGHTED SWITCH, STOP/STOPPING, RED | CONTROL,JB70;TT6
SH0471 | 1035040-857,2380746-3 | LIGHTED SWITCH, START/STARTING, GREEN | CONTROL,JB70;TT6
SH0472 | 1035040-106,2380746-3 | LIGHTED SWITCH, BACKUP SYSTEM ACTIVE/RESET, AMBER | CONTROL,JB70;TT6
BA0005 | 1271449-1 | MEDIA CONVERTER, ETHERNET-FIBER OPTIC | JB1123 FO PANEL
BA0006 | 1271449-1 | MEDIA CONVERTER, ETHERNET-FIBER OPTIC | JB1123 FO PANEL
FU1123 | 1043265-1,1043265-3 | FUSE, 2A | JB1123 FO PANEL
FU1124 | 1043265-1,1043265-3 | FUSE, 2A | JB1123 FO PANEL
GR1123 | 903849C1 | RAIL GROUND, DIN RAIL GROUNDING | JB1123 FO PANEL
GR1125 | 903849C1 | RAIL GROUND, DIN RAIL GROUNDING | JB1123 FO PANEL
IEG1123 | 232941-200 | BUS BAR, JB1123 - INSTRUMENT EARTH GROUNDING | JB1123 FO PANEL
XT1123 | 1066730-7,1066730-8,1067996-4 | TERMINAL BLOCK, SPRING, 4 CONDUCTOR,30-12 AWG (0.05-3.31 MM2),NON-IS | JB1123 FO PANEL
GR1211 | 903849C1 | RAIL GROUND, DIN RAIL GROUNDING | JB5 PROX PANEL
GR0431 | 903849C1 | RAIL GROUND, DIN RAIL GROUNDING | JB70 LEFT RAIL
AF0081 | 2684693-18,2684693-28 | 5094-IB16SXT, 16 DISCRETE INPUT, S | JB70 PANEL A
AF0082 | 2684693-17,2684693-23 | 5094-IB16XT, 16 DISCRETE INPUT | JB70 PANEL A
AF0083 | 2684693-19,2684693-33 | 5094-IY8XT, 8 ANALOG INPUT,TC/RTD/I&V | JB70 PANEL A
AF0084 | 2684693-19,2684693-33 | 5094-IY8XT, 8 ANALOG INPUT, TC/RTD/ I&V | JB70 PANEL A
AF0085 | 2684693-18,2684693-26 | 5094-IF8IHXT, 8 ANALOG INPUT, ISOLATED | JB70 PANEL A
AF0086 | 2684693-18,2684693-26 | 5094-IF8IHXT, 8 ANALOG INPUT, ISOLATED | JB70 PANEL A
AF0087 | 2684693-17,2684693-23 | 5094-IB16XT, 16 DISCRETE INPUT | JB70 PANEL A
AF0091 | 2684693-17,2684693-23 | 5094-IB16XT, 16 DISCRETE INPUT | JB70 PANEL A
AF0092 | 2684693-17,2684693-24 | 5094-OB16XT, 16 DISCRETE OUTPUT | JB70 PANEL A
AF0093 | 2684693-17,2684693-24 | 5094-OB16XT, 16 DISCRETE OUTPUT | JB70 PANEL A
AF0094 | 2684693-19,2684693-33 | 5094-IY8XT, 8 ANALOG INPUT, TC/RTD/ I&V | JB70 PANEL A
AF0095 | 2684693-17,2684693-25 | 5094-OB8XT, 8 DISCRETE OUTPUT | JB70 PANEL A
AU0080 | 2684693-22 | 5094-AENTRXT, FLEX 5000 I/O | JB70 PANEL A
AU0090 | 2684693-22 | 5094-AENTRXT, FLEX 5000 I/O | JB70 PANEL A
FU0011 | 1043265-1,1043265-7 | FUSE, 20A | JB70 PANEL A
FU0012 | 1043265-1,1043265-5 | FUSE, 10A | JB70 PANEL A
FU0013 | 1043265-1,1043265-5 | FUSE, 10A | JB70 PANEL A
FU0014 | 1043265-1,1043265-5 | FUSE, 10A | JB70 PANEL A
FU0015 | 1043265-1,1043265-5 | FUSE, 10A | JB70 PANEL A
FU0016 | 1043265-1,1043265-5 | FUSE, 10A | JB70 PANEL A
FU0017 | 1043265-1,1043265-5 | FUSE, 10A | JB70 PANEL A
FU0018 | 1043265-1,1043265-5 | FUSE, 10A | JB70 PANEL A
FU0080 | 1043265-1,1043265-6 | FUSE, 15A | JB70 PANEL A
FU0081 | 1043265-1,1043265-5 | FUSE, 10A | JB70 PANEL A
FU0090 | 1043265-1,1043265-5 | FUSE, 10A | JB70 PANEL A
FU0091 | 1043265-1,1043265-5 | FUSE, 10A | JB70 PANEL A
FU0092 | 1043265-1,1043265-5 | FUSE, 10A | JB70 PANEL A
FU0093 | 1043265-1,1043265-5 | FUSE, 10A | JB70 PANEL A
FU0094 | 1043265-1,1043265-5 | FUSE, 10A | JB70 PANEL A
FU0136 | 1043265-1,1043265-9 | FUSE, 30A | JB70 PANEL A
FU0137 | 1043265-1,1043265-7 | FUSE, 20A | JB70 PANEL A
FU0139 | 1043265-1,1043265-4 | FUSE, 5A | JB70 PANEL A
FU0387 | 1043265-1,1043265-4 | FUSE, 5A | JB70 PANEL A
FU0388 | 1043265-1,1043265-4 | FUSE, 5A | JB70 PANEL A
FU0389 | 1043265-1,1043265-3 | FUSE, 2A | JB70 PANEL A
GR0131 | 903849C1 | RAIL GROUND, DIN RAIL GROUNDING | JB70 PANEL A
GR0132 | 903849C1 | RAIL GROUND, DIN RAIL GROUNDING | JB70 PANEL A
GR0133 | 903849C1 | RAIL GROUND, DIN RAIL GROUNDING | JB70 PANEL A
GR0134 | 903849C1 | RAIL GROUND, DIN RAIL GROUNDING | JB70 PANEL A
GR0135 | 903849C1 | RAIL GROUND, DIN RAIL GROUNDING | JB70 PANEL A
IEG0010 | 232941-300 | BUS BAR, PANEL A - INSTRUMENT EARTH GROUNDING | JB70 PANEL A
KA0130 | 1061979-1 | RELAY, LOWSPEED/OPEN PROBE SETPOINT | JB70 PANEL A
KA0131 | 1061979-1 | RELAY, CONTROLLER ACTIVE | JB70 PANEL A
KA0132 | 1061979-1 | RELAY, CONTROLLER ACTIVE | JB70 PANEL A
KA0133 | 1061979-1 | RELAY, POST LUBE NOT REQUIRED | JB70 PANEL A
KA0134 | 1061979-1 | RELAY, BACKUP COMMAND OFF | JB70 PANEL A
KA0135 | 1061979-1 | RELAY, AC PRE/POST PUMP DRIVE | JB70 PANEL A
KA0136 | 1061979-1 | RELAY, LUBE OIL HEADER^PRESSURE HIGH | JB70 PANEL A
KA0137 | 1061979-1 | RELAY, LUBE PUMP INHIBIT | JB70 PANEL A
KA0138 | 1061979-1 | RELAY, BACKUP LUBE OIL PUMP OFF | JB70 PANEL A
KA0141 | 1061979-1 | RELAY, CONTROLLER ACTIVE | JB70 PANEL A
KA0230 | 1061979-1 | RELAY, CONTROLLER ACTIVE | JB70 PANEL A
KA0231 | 1061979-1 | RELAY, CONTROLLER ACTIVE | JB70 PANEL A
KA0232 | 1061979-1 | RELAY, CONTROLLER ACTIVE | JB70 PANEL A
KA0236 | 1061979-1 | RELAY, NO EMERGENCY SHUTDOWN SUMMARY | JB70 PANEL A
KA0239 | 1061979-1 | RELAY, NO EMERGENCY SHUTDOWN SUMMARY | JB70 PANEL A
KA0240 | 1061979-1 | RELAY, NO EMERGENCY SHUTDOWN SUMMARY | JB70 PANEL A
KA0241 | 1061979-1 | RELAY, BACKUP SYSTEM RESET | JB70 PANEL A
KA0242 | 1061979-1 | RELAY, BACKUP SYSTEM RESET | JB70 PANEL A
KA0243 | 1061979-1 | RELAY, NO FIRE DETECTED | JB70 PANEL A
KA0244 | 1061979-1 | RELAY, NO FIRE DETECTED | JB70 PANEL A
KA0245 | 1061979-1 | RELAY, NO GAS DETECTED | JB70 PANEL A
KA2160 | 1061979-1 | RELAY, CLOSE GAS BLOCK VALVE | JB70 PANEL A
KA2161 | 1061979-1 | RELAY, OPEN GAS BLEED VALVE | JB70 PANEL A
KA3103 | 1061979-1 | RELAY, LUBE OIL TANK HEATER | JB70 PANEL A
KA3330 | 1061979-1 | RELAY, LOC RUN COMMAND | JB70 PANEL A
KA3331 | 1061979-1 | RELAY, LOC SHUTDOWN COMMAND | JB70 PANEL A
KT0140 | 2651077-1 | TIMER RELAY, BACKUP PUMP^POST LUBE OFF CYCLE | JB70 PANEL A
KT0141 | 2651077-1 | TIMER RELAY, BACKUP POST LUBE CONTINUOUS | JB70 PANEL A
KT0142 | 2651077-1 | TIMER RELAY, TOTAL POST LUBE | JB70 PANEL A
KT0143 | 2651077-1 | TIMER RELAY, BACKUP PUMP POST LUBE ON CYCLE | JB70 PANEL A
KT0144 | 2651077-1 | TIMER RELAY, HEADER PRESSURE HIGH^BACKUP PUMP OFF | JB70 PANEL A
KT0145 | 2651077-1 | TIMER RELAY, FIRE DETECTED ROLLDOWN LUBE | JB70 PANEL A
KT0146 | 2651077-3 | TIMER RELAY, WATCHDOG | JB70 PANEL A
PEG0130 | 232941-300 | BUS BAR, PANEL A - POWER EARTH GROUNDING | JB70 PANEL A
RR0941 | 981090C1 | RESISTOR, 3.01K OHM | JB70 PANEL A
RR0942 | 981089C1 | RESISTOR, 1.0K OHM | JB70 PANEL A
UA1200 | 1053834-11 | BUOS MODULE, BACKUP OVERSPEED | JB70 PANEL A
UJ0131 | 1286570-1 | POWER CONVERTER, AC/DC INPUT TO 28V DC OUTPUT | JB70 PANEL A
WC0080 | 2684693-54 |  | JB70 PANEL A
XT0002 | 1066730-16,1066730-17,1066730-18 | TERMINAL STRIP, 2 CONDUCTOR | JB70 PANEL A
XT0003 | 1066730-16,1066730-17,1066730-18 | TERMINAL STRIP, 2 CONDUCTOR | JB70 PANEL A
XT0011 | 1066730-16,1066730-17,1066730-18 | TERMINAL STRIP, 2 CONDUCTOR | JB70 PANEL A
XT0012 | 1066730-16,1066730-17,1066730-18 | TERMINAL STRIP, 2 CONDUCTOR | JB70 PANEL A
XT0014 | 1247052-1 | BUS BAR, SYSTEM FUNCTION (USE) | JB70 PANEL A
XT0050 | 1066730-7,1066730-8,1067996-4 | TERMINAL BLOCK, SPRING, 4 CONDUCTOR,30-12 AWG (0.05-3.31 MM2),NON-IS | JB70 PANEL A
XT0080 | 1066730-7,1066730-8,1067996-4 | TERMINAL BLOCK, SPRING, 4 CONDUCTOR,30-12 AWG (0.05-3.31 MM2),NON-IS | JB70 PANEL A
XT0081 | 1066730-7,1066730-8,1067996-4 | TERMINAL BLOCK, SPRING, 4 CONDUCTOR,30-12 AWG (0.05-3.31 MM2),NON-IS | JB70 PANEL A
XT0082 | 1066730-7,1066730-8,1067996-4 | TERMINAL BLOCK, SPRING, 4 CONDUCTOR,30-12 AWG (0.05-3.31 MM2),NON-IS | JB70 PANEL A
XT0084 | 1066730-7,1066730-8,1067996-4 | TERMINAL BLOCK, SPRING, 4 CONDUCTOR,30-12 AWG (0.05-3.31 MM2),NON-IS | JB70 PANEL A
XT0089 | 1066730-7,1066730-8,1067996-4 | TERMINAL BLOCK, SPRING, 4 CONDUCTOR,30-12 AWG (0.05-3.31 MM2),NON-IS | JB70 PANEL A
XT0237 | 1066730-9 | DIODE TERMINAL STRIP, 4 CONDUCTOR | JB70 PANEL A
AF0061 | 2684693-17,2684693-25 | 5094-OB8XT, 8 DISCRETE OUTPUT | JB70 PANEL B
AF0062 | 2684693-17,2684693-25 | 5094-OB8XT, 8 DISCRETE OUTPUT | JB70 PANEL B
AF0063 | 2684693-17,2684693-23 | 5094-IB16XT, 16 DISCRETE INPUT | JB70 PANEL B
AF0064 | 2684693-18,2684693-30 | 5094-IF4IHSXT, 4 ANALOG INPUT, S | JB70 PANEL B
AF0065 | 2684693-18,2684693-30 | 5094-IF4IHSXT, 4 ANALOG INPUT, S | JB70 PANEL B
AF0066 | 2684693-18,2684693-27 | 5094-OF8IHXT, 8 ANALOG OUTPUT, ISOLATED | JB70 PANEL B
AF0067 | 2684693-17,2684693-25 | 5094-OB8XT, 8 DISCRETE OUTPUT | JB70 PANEL B
AF0068 | 2684693-21,2684693-36 | 5094-IRT8SXT, 8 RTD/TC ANALOG INPUT, S | JB70 PANEL B
AF0071 | 2684693-18,2684693-32 | 5094-IJ2ISXT, 2 FAST COUNTER INPUT, S | JB70 PANEL B
AF0072 | 2684693-18,2684693-30 | 5094-IF4IHSXT, 4 ANALOG INPUT, S | JB70 PANEL B
AF0073 | 2684693-21,2684693-36 | 5094-IRT8SXT, 8 RTD/TC ANALOG INPUT, S | JB70 PANEL B
AF0074 | 2684693-18,2684693-26 | 5094-IF8IHXT, 8 ANALOG INPUT, ISOLATED | JB70 PANEL B
AF0075 | 2684693-18,2684693-30 | 5094-IF4IHSXT, 4 ANALOG INPUT, S | JB70 PANEL B
AF0076 | 2684693-18,2684693-55 | 5094-OB16SXT, 16 DISCRETE OUTPUT, S | JB70 PANEL B
AF0400 | 1322418-31,1322418-40,1322418-72,1322418-73 | 1444-TSCX02-02RB, 2-CH TACHOMETER INPUT^DYNAMIX 1444 VIBRATION | JB70 PANEL B
AF0410 | 1322418-11,1322418-20,1322418-70,1322418-71 | 1444-DYN04-01RA, 4-CH VIBRATION INPUT^DYNAMIX 1444 VIBRATION | JB70 PANEL B
AF0420 | 1322418-11,1322418-20,1322418-70,1322418-71 | 1444-DYN04-01RA, 4-CH VIBRATION INPUT^DYNAMIX 1444 VIBRATION | JB70 PANEL B
AF0450 | 1322418-11,1322418-20,1322418-70,1322418-71 | 1444-DYN04-01RA, 4-CH VIBRATION INPUT^DYNAMIX 1444 VIBRATION | JB70 PANEL B
AU0060 | 2684693-22 | 5094-AENTRXT, FLEX 5000 I/O | JB70 PANEL B
AU0070 | 2684693-22 | 5094-AENTRXT, FLEX 5000 I/O | JB70 PANEL B
BA0003 | 1271449-1 | MEDIA CONVERTER, ETHERNET-FIBER OPTIC | JB70 PANEL B
BA0011 | 1271449-1 | MEDIA CONVERTER, ETHERNET-FIBER OPTIC | JB70 PANEL B
BA1100 | 1337728-10 | SWITCH, ETAP, DLR INTERFACE | JB70 PANEL B
FU0023 | 1043265-1,1043265-3 | FUSE, 2A | JB70 PANEL B
FU0031 | 1043265-1,1043265-3 | FUSE, 2A | JB70 PANEL B
FU0060 | 1043265-1,1043265-6 | FUSE, 15A | JB70 PANEL B
FU0061 | 1043265-1,1043265-5 | FUSE, 10A | JB70 PANEL B
FU0062 | 1043265-1,1043265-5 | FUSE, 10A | JB70 PANEL B
FU0063 | 1043265-1,1043265-5 | FUSE, 10A | JB70 PANEL B
FU0064 | 1043265-1,1043265-5 | FUSE, 10A | JB70 PANEL B
FU0070 | 1043265-1,1043265-5 | FUSE, 10A | JB70 PANEL B
FU0076 | 1043265-1,1043265-5 | FUSE, 10A | JB70 PANEL B
FU0100 | 1043265-1,1043265-4 | FUSE, 5A | JB70 PANEL B
FU0113 | 1043265-1,1043265-5 | FUSE, 10A | JB70 PANEL B
FU0114 | 1043265-1,1043265-5 | FUSE, 10A | JB70 PANEL B
FU0115 | 1043265-1,1043265-5 | FUSE, 10A | JB70 PANEL B
FU0210 | 1043265-1,1043265-7 | FUSE, 20A | JB70 PANEL B
FU0212 | 1043265-3 | FUSE, 2A | JB70 PANEL B
FU0291 | 1043265-1,1043265-4 | FUSE, 5A | JB70 PANEL B
FU0410 | 1043265-1,1043265-4 | FUSE, 5A | JB70 PANEL B
FU1100 | 1043265-1,1043265-5 | FUSE, 10A | JB70 PANEL B
FU1101 | 1043265-1,1043265-3 | FUSE, 2A | JB70 PANEL B
GR0231 | 903849C1 | RAIL GROUND, DIN RAIL GROUNDING | JB70 PANEL B
GR0233 | 903849C1 | RAIL GROUND, DIN RAIL GROUNDING | JB70 PANEL B
GR0341 | 903849C1 | RAIL GROUND, DIN RAIL GROUNDING | JB70 PANEL B
IEG0230 | 232941-300 | BUS BAR, PANEL B - INSTRUMENT EARTH GROUNDING | JB70 PANEL B
KA0221 | 1061979-1 | RELAY, PRIMARY GAS FUEL SHUTOFF VALVE | JB70 PANEL B
KA0222 | 1061979-1 | RELAY, SECONDARY GAS FUEL SHUTOFF VALVE | JB70 PANEL B
KA0224 | 1061979-1 | RELAY, EMERGENCY SHUTDOWN ACTIVE | JB70 PANEL B
KA0233 | 1061979-1 | RELAY, CONTROLLER ACTIVE | JB70 PANEL B
KA0234 | 1061979-1 | RELAY, CONTROLLER ACTIVE | JB70 PANEL B
KA0235 | 1061979-1 | RELAY, NO EMERGENCY SHUTDOWN SUMMARY | JB70 PANEL B
KA0237 | 1061979-1 | RELAY, NO EMERGENCY SHUTDOWN SUMMARY | JB70 PANEL B
KA0251 | 1061979-1 | RELAY, NO EMERGENCY SHUTDOWN SUMMARY | JB70 PANEL B
KA1020 | 1061979-1 | RELAY, IGNITION START | JB70 PANEL B
PC0470 | 2271605-1 | TIMER/COUNTER, ENGINE HOUR / START COUNTER | JB70 PANEL B
UV0291 | 1088442-4 | POWER CONVERTER, DC/DC INPUT TO 24V DC OUTPUT | JB70 PANEL B
XT0051 | 1066730-7,1066730-8,1067996-4 | TERMINAL BLOCK, SPRING, 4 CONDUCTOR,30-12 AWG (0.05-3.31 MM2),NON-IS | JB70 PANEL B
XT0060 | 1066730-7 | TERMINAL BLOCK, SPRING, 4 CONDUCTOR,30-12 AWG (0.05-3.31 MM2),NON-IS | JB70 PANEL B
XT0062 | 1066730-7,1066730-8,1067996-4 | TERMINAL BLOCK, SPRING, 4 CONDUCTOR,30-12 AWG (0.05-3.31 MM2),NON-IS | JB70 PANEL B
XT0224 | 1066730-7 | TERMINAL BLOCK, SPRING, 4 CONDUCTOR,30-12 AWG (0.05-3.31 MM2),NON-IS | JB70 PANEL B
XT0400 | 1066730-1,1066730-2,1067996-4 | TERMINAL STRIP, 4 CONDUCTOR | JB70 PANEL B
XT0401 | 1066730-7,1066730-8,1067996-4 | TERMINAL BLOCK, SPRING, 4 CONDUCTOR,30-12 AWG (0.05-3.31 MM2),NON-IS | JB70 PANEL B
AP0601 | 1089241-20 | MODULE, BLANK FILLER | JB70 PLC PANEL
AP0602 | 1089241-40 | 1756-EN2TRXT, ETHERNET | JB70 PLC PANEL
AP0603 | 1089241-40 | 1756-EN2TRXT, ETHERNET | JB70 PLC PANEL
AP0604 | 1089241-20 | MODULE, BLANK FILLER | JB70 PLC PANEL
AP0605 | 1089241-15 | MVI 56-MNETXT, ETHERNET/MODBUS | JB70 PLC PANEL
AP0606 | 1089241-36 | 1756-EN2TXT, ETHERNET | JB70 PLC PANEL
AP0607 | 1089241-36 | 1756-EN2TXT, ETHERNET | JB70 PLC PANEL
AP0608 | 1089241-20 | MODULE, BLANK FILLER | JB70 PLC PANEL
AP0609 | 1089241-40 | 1756-EN2TRXT, ETHERNET | JB70 PLC PANEL
AR0600 | 1089241-42 | RACK CHASSIS, 1756-A10XT (10 SLOT) | JB70 PLC PANEL
AT0600 | 1089241-43 | 1756-L83EXTS, CONTROLLER^GUARDLOGIX | JB70 PLC PANEL
AT0680 | 1634974-100 | GATEWAY MODULE, TURBOTRONIC GATEWAY | JB70 PLC PANEL
BA0001 | 1271449-1 | MEDIA CONVERTER, ETHERNET-FIBER OPTIC | JB70 PLC PANEL
BA0002 | 1271449-1 | MEDIA CONVERTER, ETHERNET-FIBER OPTIC | JB70 PLC PANEL
FU0010 | 1043265-1,1043265-5 | FUSE, 10A | JB70 PLC PANEL
FU0021 | 1043265-1,1043265-3 | FUSE, 2A | JB70 PLC PANEL
FU0022 | 1043265-1,1043265-3 | FUSE, 2A | JB70 PLC PANEL
FU0680 | 1043265-1,1043265-4 | FUSE, 5A | JB70 PLC PANEL
GR0234 | 903849C1 | RAIL GROUND, DIN RAIL GROUNDING | JB70 PLC PANEL
UV0600 | 1089241-28 | POWER SUPPLY, RSLOGIX CHASSIS | JB70 PLC PANEL
XT0680 | 1066730-32,1066730-7,1066730-8 | TERMINAL BLOCK, SPRING, 4 CONDUCTOR,30-12 AWG (0.05-3.31 MM2),NON-IS | JB70 PLC PANEL
GR0532 | 903849C1 | RAIL GROUND, DIN RAIL GROUNDING | JB70 RIGHT RAIL
XT0111 | 1066730-7,1066730-8,1067996-4 | TERMINAL BLOCK, SPRING, 4 CONDUCTOR,30-12 AWG (0.05-3.31 MM2),NON-IS | JB70 RIGHT RAIL
XT0355 | 1066730-7,1066730-8,1067996-4 | TERMINAL BLOCK, SPRING, 4 CONDUCTOR,30-12 AWG (0.05-3.31 MM2),NON-IS | JB72
AF0121 | 2684693-17,2684693-24 | 5094-OB16XT, 16 DISCRETE OUTPUT | JB72 GEN PANEL
AF0122 | 2684693-17,2684693-23 | 5094-IB16XT, 16 DISCRETE INPUT | JB72 GEN PANEL
AF0123 | 2684693-19,2684693-33 | 5094-IY8XT, 8 ANALOG INPUT, TC/RTD/ I&V | JB72 GEN PANEL
AT0140 | 2769310-1,2769310-4 | MODULE, DESC-250 | JB72 GEN PANEL
AU0120 | 2684693-22 | 5094-AENTRXT, FLEX 5000 I/O | JB72 GEN PANEL
FU0120 | 1043265-1,1043265-5 | FUSE, 10A | JB72 GEN PANEL
FU0121 | 1043265-1,1043265-5 | FUSE, 10A | JB72 GEN PANEL
FU0122 | 1043265-1,1043265-6 | FUSE, 15A | JB72 GEN PANEL
FU0332 | 1043265-1,1043265-7 | FUSE, 20A | JB72 GEN PANEL
FU0333 | 1043265-1,1043265-4 | FUSE, 5A | JB72 GEN PANEL
FU0334 | 1043265-1,1043265-4 | FUSE, 5A | JB72 GEN PANEL
GR0142 | 903849C1 | RAIL GROUND, DIN RAIL GROUNDING | JB72 GEN PANEL
GR0143 | 903849C1 | RAIL GROUND, DIN RAIL GROUNDING | JB72 GEN PANEL
GR0144 | 903849C1 | RAIL GROUND, DIN RAIL GROUNDING | JB72 GEN PANEL
GR0145 | 903849C1 | RAIL GROUND, DIN RAIL GROUNDING | JB72 GEN PANEL
IEG0140 | 232941-110 | BUS BAR, DRIVEN - INSTRUMENT EARTH GROUNDING | JB72 GEN PANEL
KA0121 | 1061979-1 | RELAY, AUTOMATIC CLOSE CIRCUIT BREAKER | JB72 GEN PANEL
KA0123 | 1061979-1 | RELAY, CGCM #1 ENABLED | JB72 GEN PANEL
KA0128 | 1061979-1 | RELAY, GENERATOR TRIP SUMMARY CIRCUIT BREAKER | JB72 GEN PANEL
KA0310 | 1061979-1 | RELAY, CGCM #1 FAULT | JB72 GEN PANEL
KA0313 | 1076251-1,1076251-2 | RELAY, PMG INPUT #1 | JB72 GEN PANEL
KA0314 | 1076251-1,1076251-2 | RELAY, PMG INPUT #1 | JB72 GEN PANEL
KA0330 | 1061979-1 | RELAY, CLOSED CIRCUIT BREAKER | JB72 GEN PANEL
KA0331 | 1061979-1 | RELAY, MAIN UTILITY BREAKER AUXILIARY CONTACT CLOSED | JB72 GEN PANEL
KA0332 | 1061979-1 | RELAY, CLOSE CONTROL CIRCUIT BREAKER | JB72 GEN PANEL
KA0333 | 1061979-1 | RELAY, TRIP CONTROL CIRCUIT BREAKER | JB72 GEN PANEL
KA0335 | 1061979-1 | RELAY, NO EMERGENCY SHUTDOWN SUMMARY | JB72 GEN PANEL
KA0336 | 1061979-1 | RELAY, CONTROLLER ACTIVE | JB72 GEN PANEL
KA3420 | 1061979-1 | RELAY, GENERATOR JACKING OIL | JB72 GEN PANEL
KA4100 | 1061979-1 | RELAY, GENERATOR HEATER DISABLED | JB72 GEN PANEL
KA7610 | 1061979-1 | RELAY, VAR CNTL RDY | JB72 GEN PANEL
PEG0140 | 232941-110 | BUS BAR, DRIVEN - POWER EARTH GROUNDING | JB72 GEN PANEL
XT0120 | 1066730-7,1066730-8,1067996-4 | TERMINAL BLOCK, SPRING, 4 CONDUCTOR,30-12 AWG (0.05-3.31 MM2),NON-IS | JB72 GEN PANEL
XT0335 | 1066730-7,1066730-8,1067996-4 | TERMINAL BLOCK, SPRING, 4 CONDUCTOR,30-12 AWG (0.05-3.31 MM2),NON-IS | JB72 GEN PANEL
XT0336 | 1066730-7,1066730-8,1067996-4 | TERMINAL BLOCK, SPRING, 4 CONDUCTOR,30-12 AWG (0.05-3.31 MM2),NON-IS | JB72 GEN PANEL
XT0337 | 1066730-7,1066730-8,1067996-4 | TERMINAL BLOCK, SPRING, 4 CONDUCTOR,30-12 AWG (0.05-3.31 MM2),NON-IS | JB72 GEN PANEL
XT0338 | 1066730-7,1066730-8,1067996-4 | TERMINAL BLOCK, SPRING, 4 CONDUCTOR,30-12 AWG (0.05-3.31 MM2),NON-IS | JB72 GEN PANEL
XT0339 | 1066730-7,1066730-8,1067996-4 | TERMINAL BLOCK, SPRING, 4 CONDUCTOR,30-12 AWG (0.05-3.31 MM2),NON-IS | JB72 GEN PANEL
XT0350 | 1066730-16,1066730-17,1066730-18 | TERMINAL STRIP, 2 CONDUCTOR | JB72 GEN PANEL
XT0351 | 1066730-7,1066730-8,1067996-4 | TERMINAL BLOCK, SPRING, 4 CONDUCTOR,30-12 AWG (0.05-3.31 MM2),NON-IS | JB72 GEN PANEL
XT0352 | 1066730-16,1066730-17,1066730-18 | TERMINAL STRIP, 2 CONDUCTOR | JB72 GEN PANEL
XT0353 | 1066730-7,1066730-8,1067996-4 | TERMINAL BLOCK, SPRING, 4 CONDUCTOR,30-12 AWG (0.05-3.31 MM2),NON-IS | JB72 GEN PANEL
XT0354 | 1066730-7,1066730-8,1067996-4 | TERMINAL BLOCK, SPRING, 4 CONDUCTOR,30-12 AWG (0.05-3.31 MM2),NON-IS | JB72 GEN PANEL
XT0525 | 1066730-7,1066730-8,1067996-4 | TERMINAL BLOCK, SPRING, 4 CONDUCTOR,30-12 AWG (0.05-3.31 MM2),NON-IS | JB72 GEN PANEL
AF0181 | 2684693-17,2684693-25 | 5094-OB8XT, 8 DISCRETE OUTPUT | JB72 LEFT RAIL
AF0182 | 2684693-17,2684693-23 | 5094-IB16XT, 16 DISCRETE INPUT | JB72 LEFT RAIL
AF0183 | 2684693-18,2684693-28 | 5094-IB16SXT, 16 DISCRETE INPUT, S | JB72 LEFT RAIL
AF0184 | 2684693-19,2684693-33 | 5094-IY8XT, 8 ANALOG INPUT, TC/RTD/ I&V | JB72 LEFT RAIL
AF0185 | 2684693-18,2684693-27 | 5094-OF8IHXT, 8 ANALOG OUTPUT, ISOLATED | JB72 LEFT RAIL
AU0180 | 2684693-22 | 5094-AENTRXT, FLEX 5000 I/O | JB72 LEFT RAIL
BA0120 | 1271449-1 | MEDIA CONVERTER, ETHERNET-FIBER OPTIC | JB72 LEFT RAIL
BA0121 | 1271449-1 | MEDIA CONVERTER, ETHERNET-FIBER OPTIC | JB72 LEFT RAIL
FU0133 | 1043265-1,1043265-3 | FUSE, 2A | JB72 LEFT RAIL
FU0134 | 1043265-1,1043265-3 | FUSE, 2A | JB72 LEFT RAIL
FU0180 | 1043265-1,1043265-5 | FUSE, 10A | JB72 LEFT RAIL
FU0181 | 1043265-1,1043265-5 | FUSE, 10A | JB72 LEFT RAIL
FU0182 | 1043265-1,1043265-6 | FUSE, 15A | JB72 LEFT RAIL
GR0241 | 903849C1 | RAIL GROUND, DIN RAIL GROUNDING | JB72 LEFT RAIL
KA0180 | 1061979-1 | RELAY, 90% SPEED | JB72 LEFT RAIL
KA0181 | 1061979-1 | RELAY, TURBINE RUNNING STATUS | JB72 LEFT RAIL
KA0182 | 1061979-1 | RELAY, WHRS PURGE FLOW ESTABLISHED | JB72 LEFT RAIL
KA0183 | 1061979-1 | RELAY, WASTE HEAT READY | JB72 LEFT RAIL
KA0185 | 1061979-1 | RELAY, PERMISSIVE CLOSE CIRCUIT BREAKER | JB72 LEFT RAIL
XT0180 | 1066730-7,1066730-8,1067996-4 | TERMINAL BLOCK, SPRING, 4 CONDUCTOR,30-12 AWG (0.05-3.31 MM2),NON-IS | JB72 LEFT RAIL
XT0181 | 1066730-7,1066730-8,1067996-4 | TERMINAL BLOCK, SPRING, 4 CONDUCTOR,30-12 AWG (0.05-3.31 MM2),NON-IS | JB72 LEFT RAIL
XT1207 | 1066730-7,1066730-8,1067996-4 | TERMINAL BLOCK, SPRING, 4 CONDUCTOR,30-12 AWG (0.05-3.31 MM2),NON-IS | JB72 LEFT RAIL
GR0141 | 903849C1 | RAIL GROUND, DIN RAIL GROUNDING | JB72 RIGHT RAIL
AF0500 | 1322418-31,1322418-40,1322418-72,1322418-73 | 1444-TSCX02-02RB, 2-CH TACHOMETER INPUT^DYNAMIX 1444 VIBRATION | JB72 VIB PANEL
AF0510 | 1322418-11,1322418-20,1322418-70,1322418-71 | 1444-DYN04-01RA, 4-CH VIBRATION INPUT^DYNAMIX 1444 VIBRATION | JB72 VIB PANEL
FU0510 | 1043265-1,1043265-4 | FUSE, 5A | JB72 VIB PANEL
XT0500 | 1066730-1,1066730-2,1067996-4 | TERMINAL STRIP, 4 CONDUCTOR | JB72 VIB PANEL
XT0501 | 1066730-7,1066730-8,1067996-4 | TERMINAL BLOCK, SPRING, 4 CONDUCTOR,30-12 AWG (0.05-3.31 MM2),NON-IS | JB72 VIB PANEL
AF0111 | 2684693-17,2684693-24 | 5094-OB16XT, 16 DISCRETE OUTPUT | MCC RAIL
AF0112 | 2684693-17,2684693-23 | 5094-IB16XT, 16 DISCRETE INPUT | MCC RAIL
AF0113 | 2684693-17,2684693-23 | 5094-IB16XT, 16 DISCRETE INPUT | MCC RAIL
AF0114 | 2684693-19,2684693-33 | 5094-IY8XT, 8 ANALOG INPUT,TC/RTD/I&V | MCC RAIL
AU0110 | 2684693-22 | 5094-AENTRXT, FLEX 5000 I/O | MCC RAIL
BA0110 | 1271449-1 | MEDIA CONVERTER, ETHERNET-FIBER OPTIC | MCC RAIL
BA0111 | 1271449-1 | MEDIA CONVERTER, ETHERNET-FIBER OPTIC | MCC RAIL
BA0112 | 1271449-1 | MEDIA CONVERTER, ETHERNET-FIBER OPTIC | MCC RAIL
FU0110 | 1043265-1,1043265-5 | FUSE, 10A | MCC RAIL
FU0111 | 1043265-1,1043265-5 | FUSE, 10A | MCC RAIL
FU1110 | 1043265-1,1043265-3 | FUSE, 2A | MCC RAIL
FU1111 | 1043265-1,1043265-3 | FUSE, 2A | MCC RAIL
FU1112 | 1043265-1,1043265-3 | FUSE, 2A | MCC RAIL
GR0257 | 903849C1 | RAIL GROUND, DIN RAIL GROUNDING | MCC RAIL
IEG0110 | 1054025-101 | BUS BAR, INSTRUMENT EARTH (SHIELDING) | MCC RAIL
IEG0257 | 232941-200 | BUS BAR, SYSTEM FUNCTION (USE) | MCC RAIL
KA7000 | 1061979-1 | RELAY, RESET TO NORMAL | MCC RAIL
KA7001 | 1061979-1 | RELAY, ENABLE VAR/PF | MCC RAIL
KA7002 | 1061979-1 | RELAY, VOLTAGE RAISE | MCC RAIL
KA7003 | 1061979-1 | RELAY, VOLTAGE LOWER | MCC RAIL
KA7004 | 1061979-1 | RELAY, AVR | MCC RAIL
KA7005 | 1061979-1 | RELAY, FCR | MCC RAIL
KA7006 | 1061979-1 | RELAY, START | MCC RAIL
KA7007 | 1061979-1 | RELAY, STOP | MCC RAIL
KA7008 | 1061979-1 | RELAY, NO EMERGENCY SHUTDOWN SUMMARY | MCC RAIL
KA7009 | 1061979-1 | RELAY, OFF-LINE OPERATION | MCC RAIL
KA7010 | 1061979-1 | RELAY, EXCITER PSS ENABLE | MCC RAIL
KA7011 | 1061979-1 | RELAY, SPARE | MCC RAIL
KA7012 | 1061979-1 | RELAY, SPARE | MCC RAIL
KA7013 | 1061979-1 | RELAY, SPARE | MCC RAIL
XT0100 | 1066730-7,1066730-8,1067996-4 | TERMINAL BLOCK, SPRING, 4 CONDUCTOR,30-12 AWG (0.05-3.31 MM2),NON-IS | MCC RAIL
XT1124 | 1066730-7,1066730-8,1067996-4 | TERMINAL BLOCK, SPRING, 4 CONDUCTOR,30-12 AWG (0.05-3.31 MM2),NON-IS | MCC RAIL
CCBA0014 | CUSTOMER DEFINED | CUSTOMER CONNECTION, 4M081 MEDIA CONVERTER | PANEL
XTFG1 | FRAME_GROUND | GROUND, FRAME/CHASSIS GROUNDING | PANEL