## Blue Labels
(SHT 1) RECMPR 2X7 BOX | (SHT 2) RECMPR 2X7
PEG0141 | AR0600
BA1101 | AP0606
FU1102 | AP0605
FU1320 | AP0604
KA1261 | AP0602
KA1262 | AP0601
KA1263 | AT0600
KA1264 | UV0600
UJ1100 | AP0603
GR1305 | FU1301
AT1101 | FU1302
HL7776 | FU1303
HL7778 | FU1305
SB7771 | FU1306
SA7774 | FU1307
HL7777 | KT1325
HL7779 | XT1302
SB7770 | XT1303
SB7540 | XT1304
HA0454 | XT1305
HL7775 | XT1310
SB7773 | XT1311
SB7772 | XT1312
SH0455 | XT1354
IEG0141 | XT1355
XT1385
FU7763
FU7701
FU7702
KA0351
KA0352
KA0353
KA0354
KA0355
KA0356
KA0357
KA0358
KA0359
KA0360
KA0361
KA0362
KA0363
KA0364
KA0365
KA1344
KA1345
KA7701
KA7702
KA7703
KA7705
KA7760
KA7768
KA7770
GR1303
AT0681
BA0009
FU0681
FU0009
XT0681
XT0009
AU1300
AF1301
AF1302
AF1303
AF1304
AF1305
AF1306
GR1304
AF1326
AF1325
AF1324
AF1323
AF1322
AF1321
AU1320
FU1321
FU1322
FU1323
XT1320
GR1301
FU0131
XT1301
XTFGA
GR1302
UJ0131

## White Labels
(SHT 2) RECMPR 2X7 | (SHT 2) RECMPR 2X7 - (SHT 1) RECMPR 2X7 BOX | (SHT 1) RECMPR 2X7 BOX
AF1301G | GR1301 | AT1101G
AF1324G | GR1304 | GR1305
AF1325G | IEG01415
AU1300G | IEG01416
AU1320G | IEG01417
UV0600G

## RECMPR 2X7
RECMPR 2X7
Project # | 4M839
Project Name | Enbridge Gas
Revision | B
Controls DE | K. BOLIN
Phone:
Controls ME | S. LOZA
Phone:
From | [5 empty] | To
Device ID | Cable (W) Conductor (SC) Jumper Clip (JC) | Wire No. | Wire ID | Gauge/Size | Page/Zone | Device ID | Location | Page/Zone
XT1302:1 | JC | 0V | CLIP | --- | 5.D5 | XT1302:2 | RECMPR 2X7 | 5.D5
XT1302:2 | JC | 0V | CLIP | --- | 5.D5 | XT1302:3 | RECMPR 2X7 | 5.D5
XT1302:3 | JC | 0V | CLIP | --- | 5.D5 | XT1302:4 | RECMPR 2X7 | 5.D5
XT1302:4 | JC | 0V | CLIP | --- | 5.D5 | XT1302:5 | RECMPR 2X7 | 5.D5
XT1303:1 | JC | FU1301 | CLIP | --- | 5.C5 | XT1303:2 | RECMPR 2X7 | 5.C5
XT1303:2 | JC | FU1301 | CLIP | --- | 5.C5 | XT1303:3 | RECMPR 2X7 | 5.C5
XT1303:3 | JC | FU1301 | CLIP | --- | 5.C5 | XT1303:4 | RECMPR 2X7 | 5.C5
XT1303:4 | JC | FU1301 | CLIP | --- | 5.C5 | XT1303:5 | RECMPR 2X7 | 5.C5
XT1304:1 | JC | FU1303 | CLIP | --- | 8.A6 | XT1304:2 | RECMPR 2X7 | 8.A6
XT1305:1 | JC | 0V | CLIP | --- | 7.B1 | XT1305:2 | RECMPR 2X7 | 7.B1
XT1305:2 | JC | 0V | CLIP | --- | 7.B1 | XT1305:3 | RECMPR 2X7 | 7.B1
XT1320:1 | JC | 0V | CLIP | --- | 2.B1 | XT1320:2 | RECMPR 2X7 | 2.B1
XT1320:2 | JC | 0V | CLIP | --- | 2.B1 | XT1320:3 | RECMPR 2X7 | 2.C1
AF1301:02 | SC | UJ0131VIN | WHT | 20 | 5.A7 | UJ0131:VIN | RECMPR 2X7 | 5.B4
AF1301:03 | SC | 0V | WHT | 14 | 5.A7 | XT1302:2 | RECMPR 2X7 | 5.D5
AF1301:04 | SC | UJ0131IOUT | WHT | 20 | 5.B7 | UJ0131:IOUT | RECMPR 2X7 | 5.B4
AF1301:05 | SC | 0V | WHT | 20 | 5.B7 | XT1302:5 | RECMPR 2X7 | 5.D5
AF1301:COM | SC | AF1303N | WHT | 14 | 7.B2 | AF1303:COM | RECMPR 2X7 | 7.B3
AF1301:COM | SC | AF1301N | WHT | 16 | 7.B2 | AU1300:COM | RECMPR 2X7 | 7.A2
AF1301:SH | SC | AF1301G | GRN | 14 | 7.B2 | AF1306:SH | RECMPR 2X7 | 7.B6
AF1301:SH | SC | AU1300G | GRN | 14 | 7.B2 | AU1300:GND | RECMPR 2X7 | 7.A2
AF1301:V+ | SC | AF1303P | WHT | 14 | 7.B2 | AF1303:V+ | RECMPR 2X7 | 7.B3
AF1301:V+ | SC | AF1301P | WHT | 14 | 7.B2 | AU1300:V+ | RECMPR 2X7 | 7.A2
AF1302:03 | SC | 130203 | WHT | 20 | 9.A6 | XT1355:1 T2 | RECMPR 2X7 | 9.A5
AF1302:35 | SC | 130235 | WHT | 20 | 9.A6 | KA0354:12 | RECMPR 2X7 | 9.A6
AF1302:COM | SC | 0V | WHT | 14 | 7.B3 | XT1305:2 | RECMPR 2X7 | 7.B1
AF1302:V+ | SC | FU1306 | WHT | 14 | 7.B3 | FU1306:LD | RECMPR 2X7 | 7.B1
AF1303:00 | SC | 130300 | WHT | 20 | 8.C6 | KA1344:11 | RECMPR 2X7 | 8.C6
AF1303:02 | SC | UJ0131OK2 | WHT | 20 | 5.B7 | UJ0131:OK2 | RECMPR 2X7 | 5.B4
AF1303:32 | SC | 130332 | WHT | 20 | 8.C6 | KA1344:14 | RECMPR 2X7 | 8.C6
AF1303:34 | SC | UJ0131OK1 | WHT | 20 | 5.B7 | UJ0131:OK1 | RECMPR 2X7 | 5.B4
AF1303:COM | SC | AF1304N | WHT | 14 | 7.B3 | AF1304:COM | RECMPR 2X7 | 7.A5
AF1303:V+ | SC | AF1304P | WHT | 14 | 7.B3 | AF1304:V+ | RECMPR 2X7 | 7.A5
AF1304:00 | SC | 130400 | WHT | 20 | 8.B6 | KA0353:24 | RECMPR 2X7 | 8.B6
AF1304:32 | SC | 130432 | WHT | 20 | 8.B6 | KA0353:21 | RECMPR 2X7 | 8.B6
AF1304:03 | SC | JP2 | VIO | 20 | 9.C6 | AF1304:35 | RECMPR 2X7 | 9.C6
AF1304:COM | SC | AF1306N | WHT | 14 | 7.A5 | AF1306:COM | RECMPR 2X7 | 7.B6
AF1304:V+ | SC | AF1306P | WHT | 14 | 7.A5 | AF1306:V+ | RECMPR 2X7 | 7.B6
AF1305:01 | SC | 130501 | WHT | 20 | 16.B6 | KA7701:A1 | RECMPR 2X7 | 16.B6
AF1305:03 | SC | 130503 | WHT | 20 | 17.A6 | KA7703:A1 | RECMPR 2X7 | 17.A6
AF1305:05 | SC | 130505 | WHT | 20 | 19.A6 | KA7705:A1 | RECMPR 2X7 | 19.A6
AF1305:07 | SC | KT1325B1 | WHT | 20 | 8.B6 | KT1325:B1 | RECMPR 2X7 | 8.A6
AF1305:08 | SC | 130508 | WHT | 20 | 8.C6 | KT1325:15 | RECMPR 2X7 | 8.C6
AF1305:09 | SC | 130509 | WHT | 20 | 21.A7 | KA7702:A1 | RECMPR 2X7 | 21.A6
AF1305:17 | SC | 130517 | WHT | 20 | 16.B6 | KA7701:A2 | RECMPR 2X7 | 16.B6
AF1305:19 | SC | 130519 | WHT | 20 | 17.A6 | KA7703:A2 | RECMPR 2X7 | 17.A6
AF1305:21 | SC | 130521 | WHT | 20 | 19.A6 | KA7705:A2 | RECMPR 2X7 | 19.A6
AF1305:23 | SC | KT1325A2 | WHT | 20 | 8.B6 | KT1325:A2 | RECMPR 2X7 | 8.A6
AF1305:25 | SC | 130525 | WHT | 20 | 21.A7 | KA7702:A2 | RECMPR 2X7 | 21.A6
AF1305:COM | SC | 0V | WHT | 14 | 7.A5 | XT1305:3 | RECMPR 2X7 | 7.B1
AF1305:V+ | SC | FU1307 | WHT | 14 | 7.A5 | FU1307:LD | RECMPR 2X7 | 7.B1
AF1306:01 | SC | 130601 | WHT | 20 | 5.A3 | XT1385:2 | RECMPR 2X7 | 5.A2
AF1306:17 | SC | 0V | WHT | 20 | 5.A3 | XT1385:3 | RECMPR 2X7 | 5.A2
AF1321:00 | SC | 132100 | WHT | 20 | 14.A6 | KA0355:14 | RECMPR 2X7 | 14.A6
AF1321:01 | SC | 132101 | WHT | 20 | 14.A6 | KA0355:24 | RECMPR 2X7 | 14.A6
AF1321:02 | SC | 132102 | WHT | 20 | 16.B6 | KA7701:14 | RECMPR 2X7 | 16.B6
AF1321:03 | SC | 132103 | WHT | 20 | 16.C6 | KA0356:24 | RECMPR 2X7 | 16.C5
AF1321:04 | SC | 132104 | WHT | 20 | 17.C6 | KA0357:24 | RECMPR 2X7 | 17.C5
AF1321:05 | SC | 132105 | WHT | 20 | 19.A6 | KA7705:14 | RECMPR 2X7 | 19.B6
AF1321:COM | SC | AF1321N | WHT | 14 | 2.B2 | AU1320:COM | RECMPR 2X7 | 2.A2
AF1321:J | SC | * |  |  | 2.B2 | AF1322:P | RECMPR 2X7 | 2.B3
AF1321:V+ | SC | AF1321P | WHT | 20 | 2.B2 | AU1320:V+ | RECMPR 2X7 | 2.A2
AF1322:05 | SC | 132205 | WHT | 20 | 23.A6 | KA7760:A1 | RECMPR 2X7 | 23.A6
AF1322:06 | SC | 132206 | WHT | 20 | 23.D6 | KA7768:A1 | RECMPR 2X7 | 23.D6
AF1322:07 | SC | 132207 | WHT | 20 | 17.A6 | KA7703:14 | RECMPR 2X7 | 17.A6
AF1322:11 | SC | 132211 | WHT | 20 | 15.A6 | KA0360:14 | RECMPR 2X7 | 15.A6
AF1322:12 | SC | 132212 | WHT | 20 | 15.B6 | KA0360:24 | RECMPR 2X7 | 15.B6
AF1322:13 | SC | 132213 | WHT | 20 | 15.B6 | KA0363:14 | RECMPR 2X7 | 15.B6
AF1322:14 | SC | KA7770A1 | WHT | 20 | 24.B6 | KA7770:A1 | RECMPR 2X7 | 24.B6
AF1322:15 | SC | 132215 | WHT | 20 | 15.C6 | KA0363:24 | RECMPR 2X7 | 15.C6
AF1322:21 | SC | 132221 | WHT | 20 | 23.A6 | KA7760:A2 | RECMPR 2X7 | 23.A6
AF1322:22 | SC | 132222 | WHT | 20 | 23.D6 | KA7768:A2 | RECMPR 2X7 | 23.D6
AF1322:30 | SC | 132230 | WHT | 20 | 24.B6 | KA7770:A2 | RECMPR 2X7 | 24.B6
AF1322:COM | SC | 0V | WHT | 14 | 2.B3 | XT1320:2 | RECMPR 2X7 | 2.B1
AF1322:J | SC | * |  |  | 2.B3 | AF1323:P | RECMPR 2X7 | 2.B3
AF1322:V+ | SC | FU1322 | WHT | 14 | 2.B3 | FU1322:LD | RECMPR 2X7 | 2.B1
AF1323:COM | SC | AF1324N | WHT | 14 | 2.B3 | AF1324:COM | RECMPR 2X7 | 2.B4
AF1323:COM | SC | 0V | WHT | 14 | 2.B3 | XT1320:3 | RECMPR 2X7 | 2.C1
AF1323:J | SC | * |  |  | 2.B3 | AF1324:P | RECMPR 2X7 | 2.B4
AF1323:V+ | SC | AF1324P | WHT | 14 | 2.B3 | AF1324:V+ | RECMPR 2X7 | 2.B4
AF1323:V+ | SC | FU1323 | WHT | 14 | 2.B3 | FU1323:LD | RECMPR 2X7 | 2.B1
AF1324:COM | SC | AF1325N | WHT | 14 | 2.B4 | AF1325:COM | RECMPR 2X7 | 2.B5
AF1324:J | SC | * |  |  | 2.B4 | AF1325:P | RECMPR 2X7 | 2.B5
AF1324:SH | SC | AF1324G | GRN | 14 | 2.B4 | AF1325:SH | RECMPR 2X7 | 2.B5
AF1324:SH | SC | AU1320G | GRN | 14 | 2.B4 | AU1320:GND | RECMPR 2X7 | 2.A2
AF1324:V+ | SC | AF1325P | WHT | 14 | 2.B4 | AF1325:V+ | RECMPR 2X7 | 2.B5
AF1325:COM | SC | AF1326N | WHT | 14 | 2.B5 | AF1326:COM | RECMPR 2X7 | 2.A5
AF1325:J | SC | * |  |  | 2.B5 | AF1326:P | RECMPR 2X7 | 2.A5
AF1325:SH | SC | AF1325G | GRN | 14 | 2.B5 | AF1326:SH | RECMPR 2X7 | 2.A5
AF1325:V+ | SC | AF1326P | WHT | 14 | 2.B5 | AF1326:V+ | RECMPR 2X7 | 2.A5
AR0600:IE1 | SC | UV0600G | GRN | 14 | 6.A2 | UV0600:GND | RECMPR 2X7 | 6.A2
AT0681:NEG | SC | 0V | WHT | 14 | 12.C4 | XT0681:2 | RECMPR 2X7 | 12.C3
AT0681:POS | SC | AT0681P | WHT | 14 | 12.C4 | XT0681:1 | RECMPR 2X7 | 12.C3
AU1300:COM | SC | 0V | WHT | 14 | 7.A2 | XT1305:1 | RECMPR 2X7 | 7.B1
AU1300:V+ | SC | FU1305 | WHT | 14 | 7.A2 | FU1305:LD | RECMPR 2X7 | 7.B1
AU1320:COM | SC | 0V | WHT | 14 | 2.A2 | XT1320:1 | RECMPR 2X7 | 2.B1
AU1320:V+ | SC | FU1321 | WHT | 14 | 2.A2 | FU1321:LD | RECMPR 2X7 | 2.B1
BA0009:V1(-) | SC | 0V | WHT | 16 | 12.B4 | XT0009:2 | RECMPR 2X7 | 12.C3
BA0009:V1(+) | SC | BA0009P | WHT | 16 | 12.B4 | XT0009:1 | RECMPR 2X7 | 12.C3
FU0009:LD | SC | BA0009P | WHT | 16 | 12.C2 | XT0009:1 | RECMPR 2X7 | 12.C3
FU0009:LI | SC | FU1301 | WHT | 16 | 12.C2 | XT1303:2 | RECMPR 2X7 | 5.C5
FU0131:LD | SC | UJ0131P | WHT | 12 | 5.B3 | UJ0131:+ | RECMPR 2X7 | 5.B4
FU0681:LD | SC | AT0681P | WHT | 14 | 12.C2 | XT0681:1 | RECMPR 2X7 | 12.C3
FU0681:LI | SC | FU1301 | WHT | 16 | 12.C2 | XT1303:1 | RECMPR 2X7 | 5.C5
FU1301:LD | SC | FU1301 | WHT | 12 | 5.C5 | XT1303:1 | RECMPR 2X7 | 5.C5
FU1301:LI | SC | 24V | WHT | 10 | 5.C5 | UJ0131:OUT(+) | RECMPR 2X7 | 5.B4
FU1302:LD | SC | FU1302 | WHT | 14 | 5.C6 | UV0600:(+) | RECMPR 2X7 | 6.A2
FU1302:LI | SC | FU1301 | WHT | 14 | 5.C6 | XT1303:4 | RECMPR 2X7 | 5.C5
FU1303:LD | SC | FU1303 | WHT | 14 | 5.C6 | XT1304:1 | RECMPR 2X7 | 8.A6
FU1303:LI | SC | FU1301 | WHT | 14 | 5.C6 | XT1354:1 | RECMPR 2X7 | 5.C6
FU1305:LI | SC | FU1301 | WHT | 14 | 7.B1 | FU1306:LI | RECMPR 2X7 | 7.B1
FU1305:LI | SC | FU1301 | WHT | 14 | 7.B1 | XT1303:1 | RECMPR 2X7 | 5.C5
FU1306:LI | SC | FU1301 | WHT | 14 | 7.B1 | FU1307:LI | RECMPR 2X7 | 7.B1
FU1321:LI | SC | FU1301 | WHT | 14 | 2.B1 | XT1303:3 | RECMPR 2X7 | 5.C5
FU1321:LI | SC | FU1301 | WHT | 14 | 2.B1 | FU1322:LI | RECMPR 2X7 | 2.B1
FU1322:LI | SC | FU1301 | WHT | 14 | 2.B1 | FU1323:LI | RECMPR 2X7 | 2.B1
FU7701:LI | SC | FU1301 | WHT | 14 | 5.C5 | XT1303:4 | RECMPR 2X7 | 5.C5
FU7702:LI | SC | FU1301 | WHT | 14 | 25.B5 | XT1303:3 | RECMPR 2X7 | 5.C5
FU7763:LI | SC | FU1301 | WHT | 14 | 22.A5 | XT1303:5 | RECMPR 2X7 | 5.C5
GR1302: | SC | GR1302 | GRN/YEL | 14 | 4.A4 | FRAME | RECMPR 2X7 | 4.A3
GR1303: | SC | GR1303 | GRN/YEL | 14 | 4.A4 | FRAME | RECMPR 2X7 | 4.A3
KA0351:11 | SC | FU1303 | WHT | 20 | 8.A5 | XT1304:1 | RECMPR 2X7 | 8.A6
KA0351:11 | SC | FU1303 | WHT | 20 | 8.A5 | KA0353:11 | RECMPR 2X7 | 8.A5
KA0351:14 | SC | KA035114 | WHT | 20 | 8.A5 | KA0353:14 | RECMPR 2X7 | 8.A5
KA0351:14 | SC | KA035114 | WHT | 20 | 8.A5 | KA1345:11 | RECMPR 2X7 | 8.A4
KA0351:24 | SC | 130401 | WHT | 20 | 8.B6 | AF1304:01 | RECMPR 2X7 | 8.B6
KA0351:24 | SC | 130401 | WHT | 20 | 8.B6 | KA1344:24 | RECMPR 2X7 | 8.C6
KA0351:A1 | SC | SH045514 | WHT | 20 | 8.A2 | XT1354:5 | RECMPR 2X7 | 9.B5
KA0351:A1 | SC | SH045514 | WHT | 20 | 8.A2 | KA0352:A1 | RECMPR 2X7 | 8.A2
KA0351:A2 | SC | 0V | WHT | 20 | 8.A2 | KA0352:A2 | RECMPR 2X7 | 8.A2
KA0352:11 | SC | FU1303 | WHT | 20 | 8.A7 | KA1345:21 | RECMPR 2X7 | 8.A7
KA0352:11 | SC | FU1303 | WHT | 20 | 8.A7 | XT1304:2 | RECMPR 2X7 | 8.A6
KA0352:14 | SC | KT1325A1 | WHT | 20 | 8.A7 | KA1345:24 | RECMPR 2X7 | 8.A7
KA0352:A2 | SC | 0V | WHT | 20 | 8.A2 | KA0353:A2 | RECMPR 2X7 | 8.B2
KA0353:A1 | SC | ESTOPD | WHT | 20 | 8.B2 | XT1354:9 | RECMPR 2X7 | 8.B3
KA0353:A1 | SC | ESTOPD | WHT | 20 | 8.B2 | KA0354:A1 | RECMPR 2X7 | 8.B2
KA0353:A2 | SC | 0V | WHT | 20 | 8.B2 | KA0354:A2 | RECMPR 2X7 | 8.B2
KA0354:11 | SC | KA035411 | WHT | 20 | 9.A6 | XT1355:1 B2 | RECMPR 2X7 | 9.A5
KA0354:A1 | SC | ESTOPD | WHT | 20 | 8.B2 | KA0355:A1 | RECMPR 2X7 | 8.B2
KA0354:A2 | SC | 0V | WHT | 20 | 8.B2 | KA0355:A2 | RECMPR 2X7 | 8.B2
KA0355:11 | SC | SV77011 | WHT | 20 | 14.A6 | XT1312:1 | RECMPR 2X7 | 14.A5
KA0355:21 | SC | SV77021 | WHT | 20 | 14.A6 | XT1312:2 | RECMPR 2X7 | 14.A5
KA0355:A1 | SC | ESTOPD | WHT | 20 | 8.B2 | KA0356:A1 | RECMPR 2X7 | 8.B2
KA0355:A2 | SC | 0V | WHT | 20 | 8.B2 | KA0356:A2 | RECMPR 2X7 | 8.B2
KA0356:11 | SC | SV77501 | WHT | 20 | 16.B5 | XT1312:3 | RECMPR 2X7 | 16.B5
KA0356:14 | SC | KA770111 | WHT | 20 | 16.B5 | KA7701:11 | RECMPR 2X7 | 16.B6
KA0356:21 | SC | SV77511 | WHT | 20 | 16.C5 | XT1312:4 | RECMPR 2X7 | 16.C5
KA0356:A1 | SC | ESTOPD | WHT | 20 | 8.B2 | KA0357:A1 | RECMPR 2X7 | 8.B2
KA0356:A2 | SC | 0V | WHT | 20 | 8.B2 | KA0357:A2 | RECMPR 2X7 | 8.B2
KA0357:11 | SC | SV77521 | WHT | 20 | 17.A5 | XT1312:5 | RECMPR 2X7 | 17.A5
KA0357:14 | SC | KA770311 | WHT | 20 | 17.A5 | KA7703:11 | RECMPR 2X7 | 17.A6
KA0357:21 | SC | SV77601 | WHT | 20 | 17.C5 | XT1312:6 | RECMPR 2X7 | 17.C5
KA0357:A1 | SC | ESTOPD | WHT | 20 | 8.B2 | KA0358:A1 | RECMPR 2X7 | 8.C2
KA0357:A2 | SC | 0V | WHT | 20 | 8.B2 | KA0358:A2 | RECMPR 2X7 | 8.C2
KA0358:11 | SC | SV77701 | WHT | 20 | 19.B5 | XT1312:7 | RECMPR 2X7 | 19.B5
KA0358:14 | SC | KA770511 | WHT | 20 | 19.B5 | KA7705:11 | RECMPR 2X7 | 19.B6
KA0358:21 | SC | KA035821 |  | 20 | 21.A6 | KA7702:14 | RECMPR 2X7 | 21.A6
KA0358:A1 | SC | ESTOPD | WHT | 20 | 8.C2 | KA0359:A1 | RECMPR 2X7 | 8.C2
KA0358:A2 | SC | 0V | WHT | 20 | 8.C2 | KA0359:A2 | RECMPR 2X7 | 8.C2
KA0359:A1 | SC | ESTOPD | WHT | 20 | 8.C2 | KA0360:A1 | RECMPR 2X7 | 8.C2
KA0359:A2 | SC | 0V | WHT | 20 | 8.C2 | KA0360:A2 | RECMPR 2X7 | 8.C2
KA0360:11 | SC | SV76511 | WHT | 20 | 15.A6 | XT1312:8 | RECMPR 2X7 | 15.A5
KA0360:21 | SC | SV76521 | WHT | 20 | 15.B6 | XT1312:9 | RECMPR 2X7 | 15.B5
KA0360:A1 | SC | ESTOPD | WHT | 20 | 8.C2 | KA0361:A1 | RECMPR 2X7 | 8.C2
KA0360:A2 | SC | 0V | WHT | 20 | 8.C2 | KA0361:A2 | RECMPR 2X7 | 8.C2
KA0361:A1 | SC | ESTOPD | WHT | 20 | 8.C2 | KA0362:A1 | RECMPR 2X7 | 8.C2
KA0361:A2 | SC | 0V | WHT | 20 | 8.C2 | KA0362:A2 | RECMPR 2X7 | 8.C2
KA0362:A1 | SC | ESTOPD | WHT | 20 | 8.C2 | KA0363:A1 | RECMPR 2X7 | 8.D2
KA0362:A2 | SC | 0V | WHT | 20 | 8.C2 | KA0363:A2 | RECMPR 2X7 | 8.D2
KA0363:11 | SC | SV76531 | WHT | 20 | 15.B6 | XT1312:10 | RECMPR 2X7 | 15.B5
KA0363:21 | SC | SV76541 | WHT | 20 | 15.C6 | XT1312:11 | RECMPR 2X7 | 15.C5
KA0363:A1 | SC | ESTOPD | WHT | 20 | 8.D2 | KA0364:A1 | RECMPR 2X7 | 8.D2
KA0363:A2 | SC | 0V | WHT | 20 | 8.D2 | KA0364:A2 | RECMPR 2X7 | 8.D2
KA0364:A1 | SC | ESTOPD | WHT | 20 | 8.D2 | KA0365:A1 | RECMPR 2X7 | 8.D2
KA0364:A2 | SC | 0V | WHT | 20 | 8.D2 | KA0365:A2 | RECMPR 2X7 | 8.D2
KA0365:A2 | SC | 0V | WHT | 20 | 8.D2 | XT1302:2 | RECMPR 2X7 | 5.D5
KA1344:21 | SC | KA035121 | WHT | 20 | 8.C6 | KA0351:21 | RECMPR 2X7 | 8.B6
KA1344:21 | SC | KA035121 | WHT | 20 | 8.C6 | KA1344:A1 | RECMPR 2X7 | 8.C6
KA1344:24 | SC | 130401 | WHT | 20 | 8.C6 | KT1325:18 | RECMPR 2X7 | 8.C6
KA1344:A1 | SC | KA035121 | WHT | 20 | 8.C6 | KA1345:A1 | RECMPR 2X7 | 8.C6
KA1344:A2 | SC | 130524 | WHT | 20 | 8.C6 | AF1305:24 | RECMPR 2X7 | 8.C6
KA1344:A2 | SC | 130524 | WHT | 20 | 8.C6 | KA1345:A2 | RECMPR 2X7 | 8.C6
KA1345:14 | SC | ESTOPA | WHT | 20 | 8.A4 | XT1311:1 | RECMPR 2X7 | 9.C5
KA1345:24 | SC | KT1325A1 | WHT | 20 | 8.A7 | KT1325:A1 | RECMPR 2X7 | 8.A6
RR3041: -3.01K OHM | SC | FU1301 | LEAD | --- | 5.A2 | XT1385:1 | RECMPR 2X7 | 5.A2
RR3041: -3.01K OHM | SC | 130601 | LEAD | --- | 5.A2 | XT1385:2 | RECMPR 2X7 | 5.A2
RR3042: -1.0K OHM | SC | 0V | LEAD | --- | 5.A2 | XT1385:3 | RECMPR 2X7 | 5.A2
RR3042: -1.0K OHM | SC | 130601 | LEAD | --- | 5.A2 | XT1385:2 | RECMPR 2X7 | 5.A2
UJ0131:- | SC | CC0131N | WHT | 12 | 5.B4 | XT1301:1 | RECMPR 2X7 | 5.B3
UJ0131:G | SC | UJ0131G | GRN/YEL | 14 | 5.B4 | FRAME | RECMPR 2X7 | 5.B3
UJ0131:OUT(-) | SC | 0V | WHT | 14 | 5.B4 | XT1302:1 | RECMPR 2X7 | 5.D5
UV0600:(-) | SC | 0V | WHT | 14 | 6.A2 | XT1302:4 | RECMPR 2X7 | 5.D5
XT1302:1 | SC | 0V | WHT | 12 | 5.D5 | XT0681:2 | RECMPR 2X7 | 12.C3
XT1302:1 | SC | 0V | WHT | 14 | 5.D5 | XT1305:1 | RECMPR 2X7 | 7.B1
XT1302:2 | SC | 0V | WHT | 16 | 5.D5 | XT0009:2 | RECMPR 2X7 | 12.C3
XT1302:4 | SC | 0V | WHT | 14 | 5.D5 | XT1354:3 | RECMPR 2X7 | 9.B5
XT1303:2 | SC | FU1301 | WHT | 20 | 5.C5 | XT1354:4 | RECMPR 2X7 | 9.B5
XT1303:4 | SC | FU1301 | WHT | 14 | 5.C5 | XT1354:1 | RECMPR 2X7 | 5.C6
XT1311:2 | SC | ESTOPB | WHT | 20 | 9.C5 | XT1311:3 | RECMPR 2X7 | 10.A5
XT1320:1 | SC | 0V | WHT | 14 | 2.B1 | XT1302:3 | RECMPR 2X7 | 5.D5
XT1385:1 | SC | FU1301 | WHT | 20 | 5.A2 | XT1303:5 | RECMPR 2X7 | 5.C5
XT1385:3 | SC | 0V | WHT | 20 | 5.A2 | XT1302:5 | RECMPR 2X7 | 5.D5
AP0602:L2 | WC0001 | AP0602L2 | ENET | CABLE | 3.A1 | AP0603:L1 | RECMPR 2X7 | 3.A2
AP0603:L2 | WC0002 | AP0603L2 | ENET | CABLE | 3.A2 | AU1300:L1 | RECMPR 2X7 | 3.A3
AT0681:LAN2 | WC0009 | AT0681LAN2 | ENET | CABLE | 12.A2 | BA0009:RJ45 | RECMPR 2X7 | 12.A3
AP0604:L1 | WC0681 | AT0681LAN1 | ENET | CABLE | 12.A2 | AT0681:LAN1 | RECMPR 2X7 | 12.A2
AU1300:L2 | WC9014 | AU1300L2 | ENET | CABLE | 3.A3 | AU1320:L1 | RECMPR 2X7 | 3.A5
XT1302:4 | SC | 0V | 2-PR2 |  | 5.D5 | XT0773:21 | JB773 | 13.A4
XT1303:3 | SC | FU1301 | WHT | 16 | 5.C5 | FU1320:LI | JB72 | 6.D4
AF1302:00 | SC | HL7778X2 | WHT | 20 | 11.B6 | HL7778:X2 | RECMPR 2X7 BOX | 11.C1
AF1302:01 | SC | HL7779X2 | WHT | 20 | 11.C6 | HL7779:X2 | RECMPR 2X7 BOX | 11.C1
AF1302:02 | SC | HL7775X2 | WHT | 20 | 11.A6 | HL7775:X2 | RECMPR 2X7 BOX | 11.A1
AF1302:05 | SC | HL7776X2 | WHT | 20 | 11.A6 | HL7776:X2 | RECMPR 2X7 BOX | 11.A1
AF1302:06 | SC | HL7777X2 | WHT | 20 | 11.B6 | HL7777:X2 | RECMPR 2X7 BOX | 11.B1
AF1302:16 | SC | HL7778X1 | WHT | 20 | 11.B6 | HL7778:X1 | RECMPR 2X7 BOX | 11.C1
AF1302:17 | SC | HL7779X1 | WHT | 20 | 11.C6 | HL7779:X1 | RECMPR 2X7 BOX | 11.C1
AF1302:18 | SC | HL7775X1 | WHT | 20 | 11.A6 | HL7775:X1 | RECMPR 2X7 BOX | 11.A1
AF1302:21 | SC | HL7776X1 | WHT | 20 | 11.A6 | HL7776:X1 | RECMPR 2X7 BOX | 11.A1
AF1302:22 | SC | HL7777X1 | WHT | 20 | 11.B6 | HL7777:X1 | RECMPR 2X7 BOX | 11.B1
AF1303:03 | SC | SB777014 | WHT | 20 | 10.A6 | SB7770:14 | RECMPR 2X7 BOX | 10.A1
AF1303:04 | SC | SB777114 | WHT | 20 | 10.B6 | SB7771:14 | RECMPR 2X7 BOX | 10.B1
AF1303:05 | SC | SB777214 | WHT | 20 | 10.C6 | SB7772:14 | RECMPR 2X7 BOX | 10.C1
AF1303:06 | SC | SB777314 | WHT | 20 | 10.C6 | SB7773:14 | RECMPR 2X7 BOX | 10.C1
AF1303:07 | SC | SA777412 | WHT | 20 | 10.D6 | SA7774:12 | RECMPR 2X7 BOX | 10.D1
AF1303:08 | SC | SA777414 | WHT | 20 | 10.D6 | SA7774:14 | RECMPR 2X7 BOX | 10.D1
AF1303:35 | SC | SB777013 | WHT | 20 | 10.A6 | SB7770:13 | RECMPR 2X7 BOX | 10.A1
AF1303:36 | SC | SB777113 | WHT | 20 | 10.B6 | SB7771:13 | RECMPR 2X7 BOX | 10.B1
AF1303:37 | SC | SB777213 | WHT | 20 | 10.C6 | SB7772:13 | RECMPR 2X7 BOX | 10.C1
AF1303:38 | SC | SB777313 | WHT | 20 | 10.C6 | SB7773:13 | RECMPR 2X7 BOX | 10.C1
AF1303:39 | SC | SA777411 | WHT | 20 | 10.D6 | SA7774:11 | RECMPR 2X7 BOX | 10.D1
AF1303:40 | SC | SA777413 | WHT | 20 | 10.D6 | SA7774:13 | RECMPR 2X7 BOX | 10.D1
AF1304:02 | SC | SB7540B212 | WHT | 20 | 10.A6 | SB7540:B2-12 | RECMPR 2X7 BOX | 10.A1
AF1304:34 | SC | SB7540B211 | WHT | 20 | 10.A6 | SB7540:B2-11 | RECMPR 2X7 BOX | 10.A1
AF1306:SH | SC | IEG01417 | GRN | 14 | 7.B6 | IEG0141:7 | RECMPR 2X7 BOX | 7.B6
AF1321:08 | SC | 132108 | WHT | 20 | 27.D6 | KA1264:A1 | RECMPR 2X7 BOX | 27.D6
AF1321:24 | SC | 132124 | WHT | 20 | 27.D6 | KA1264:A2 | RECMPR 2X7 BOX | 27.D6
AF1322:08 | SC | 132208 | WHT | 20 | 27.A6 | KA1261:A1 | RECMPR 2X7 BOX | 27.A6
AF1322:09 | SC | 132209 | WHT | 20 | 27.B6 | KA1262:A1 | RECMPR 2X7 BOX | 27.B6
AF1322:10 | SC | 132210 | WHT | 20 | 27.C6 | KA1263:A1 | RECMPR 2X7 BOX | 27.C6
AF1322:24 | SC | 132224 | WHT | 20 | 27.A6 | KA1261:A2 | RECMPR 2X7 BOX | 27.A6
AF1322:25 | SC | 132225 | WHT | 20 | 27.B6 | KA1262:A2 | RECMPR 2X7 BOX | 27.B6
AF1322:26 | SC | 132226 | WHT | 20 | 27.C6 | KA1263:A2 | RECMPR 2X7 BOX | 27.C6
AF1326:SH | SC | IEG01416 | GRN | 14 | 2.A5 | IEG0141:6 | RECMPR 2X7 BOX | 2.C6
AR0600:IE2 | SC | IEG01415 | GRN | 12 | 6.A2 | IEG0141:5 | RECMPR 2X7 BOX | 6.B5
GR1301: | SC | GR1301 | GRN | 14 | 4.A4 | IEG0141:1 | RECMPR 2X7 BOX | 4.A3
GR1304: | SC | GR1304 | GRN | 14 | 4.A4 | IEG0141:3 | RECMPR 2X7 BOX | 4.A3
XT1302:3 | SC | 0V | WHT | 14 | 5.D5 | AT1101:NEG | RECMPR 2X7 BOX | 6.D3
XT1302:3 | SC | 0V | WHT | 16 | 5.D5 | UJ1100:24V(-) | RECMPR 2X7 BOX | 6.C3
XT1303:3 | SC | FU1301 | WHT | 16 | 5.C5 | FU1102:LI | RECMPR 2X7 BOX | 6.C4
XT1311:3 | SC | ESTOPB | WHT | 20 | 10.A5 | SB7540:B1-11 | RECMPR 2X7 BOX | 10.A1
XT1311:4 | SC | ESTOPC | WHT | 20 | 10.A5 | SB7540:B1-12 | RECMPR 2X7 BOX | 10.A1
XT1354:3 | SC | 0V | WHT | 20 | 9.B5 | SH0455:X1 | RECMPR 2X7 BOX | 9.A1
XT1354:4 | SC | FU1301 | WHT | 20 | 9.B5 | SH0455:13 | RECMPR 2X7 BOX | 9.B1
XT1354:5 | SC | SH045514 | WHT | 20 | 9.B5 | SH0455:14 | RECMPR 2X7 BOX | 9.B1
XT1354:6 | SC | SH045511 | WHT | 20 | 9.B5 | SH0455:11 | RECMPR 2X7 BOX | 9.B1
XT1354:7 | SC | SH045512 | WHT | 20 | 9.B5 | SH0455:12 | RECMPR 2X7 BOX | 9.B1
XT1355:1 B1 | SC | SH0455X2 | WHT | 20 | 9.A5 | SH0455:X2 | RECMPR 2X7 BOX | 9.A1
AF1302:04 | WC0454 | HA0454BLK2 | 1 | 18 | 9.A6 | HA0454:BLK-2 | RECMPR 2X7 BOX | 9.A1
AF1302:20 | WC0454 | HA0454BLK1 | 2 | 18 | 9.A6 | HA0454:BLK-1 | RECMPR 2X7 BOX | 9.A1
AU1320:L2 | WC9016 | AU1320L2 | ENET | CABLE | 3.A5 | BA1101:L1 | RECMPR 2X7 BOX | 3.A6
SolarTools ver. 24.0.84.24712 (Jul 31, 2025)
Report date: 4/23/2026 10:52 AM

## RECMPR 2X7 BOX
RECMPR 2X7 BOX
Project # | 4M839
Project Name | Enbridge Gas
Revision | B
Controls DE | K. BOLIN
Phone:
Controls ME | S. LOZA
Phone:
From | [5 empty] | To
Device ID | Cable (W) Conductor (SC) Jumper Clip (JC) | Wire No. | Wire ID | Gauge/Size | Page/Zone | Device ID | Location | Page/Zone
AT1101:GND | SC | AT1101G | GRN/YEL | 14 | 6.D3 | PEG0141:1 | RECMPR 2X7 BOX | 6.D5
BA1101:NEG | SC | BA1101N | WHT | 16 | 6.D2 | UJ1100:OUT1(-) | RECMPR 2X7 BOX | 6.C3
BA1101:POS | SC | BA1101P | WHT | 16 | 6.D2 | UJ1100:OUT1(+) | RECMPR 2X7 BOX | 6.C3
FU1102:LD | SC | FU1102 | WHT | 16 | 6.C4 | UJ1100:24V(+) | RECMPR 2X7 BOX | 6.C3
GR1305: | SC | GR1305 | GRN | 14 | 4.A4 | IEG0141:4 | RECMPR 2X7 BOX | 4.A3
AT1101:L1 | WC0101 | BA1101DEVICE | ENET | CABLE | 6.D3 | BA1101:DEVICE | RECMPR 2X7 BOX | 6.D2
AT1101:POS | SC | FU1320 | WHT | 14 | 6.D3 | FU1320:LD | JB72 | 6.D4
AT1101:NEG | SC | 0V | WHT | 14 | 6.D3 | XT1302:3 | RECMPR 2X7 | 5.D5
FU1102:LI | SC | FU1301 | WHT | 16 | 6.C4 | XT1303:3 | RECMPR 2X7 | 5.C5
HL7775:X1 | SC | HL7775X1 | WHT | 20 | 11.A1 | AF1302:18 | RECMPR 2X7 | 11.A6
HL7775:X2 | SC | HL7775X2 | WHT | 20 | 11.A1 | AF1302:02 | RECMPR 2X7 | 11.A6
HL7776:X1 | SC | HL7776X1 | WHT | 20 | 11.A1 | AF1302:21 | RECMPR 2X7 | 11.A6
HL7776:X2 | SC | HL7776X2 | WHT | 20 | 11.A1 | AF1302:05 | RECMPR 2X7 | 11.A6
HL7777:X1 | SC | HL7777X1 | WHT | 20 | 11.B1 | AF1302:22 | RECMPR 2X7 | 11.B6
HL7777:X2 | SC | HL7777X2 | WHT | 20 | 11.B1 | AF1302:06 | RECMPR 2X7 | 11.B6
HL7778:X1 | SC | HL7778X1 | WHT | 20 | 11.C1 | AF1302:16 | RECMPR 2X7 | 11.B6
HL7778:X2 | SC | HL7778X2 | WHT | 20 | 11.C1 | AF1302:00 | RECMPR 2X7 | 11.B6
HL7779:X1 | SC | HL7779X1 | WHT | 20 | 11.C1 | AF1302:17 | RECMPR 2X7 | 11.C6
HL7779:X2 | SC | HL7779X2 | WHT | 20 | 11.C1 | AF1302:01 | RECMPR 2X7 | 11.C6
IEG0141:1 | SC | GR1301 | GRN | 14 | 4.A3 | GR1301: | RECMPR 2X7 | 4.A4
IEG0141:3 | SC | GR1304 | GRN | 14 | 4.A3 | GR1304: | RECMPR 2X7 | 4.A4
IEG0141:5 | SC | IEG01415 | GRN | 12 | 6.B5 | AR0600:IE2 | RECMPR 2X7 | 6.A2
IEG0141:6 | SC | IEG01416 | GRN | 14 | 2.C6 | AF1326:SH | RECMPR 2X7 | 2.A5
IEG0141:7 | SC | IEG01417 | GRN | 14 | 7.B6 | AF1306:SH | RECMPR 2X7 | 7.B6
KA1261:A1 | SC | 132208 | WHT | 20 | 27.A6 | AF1322:08 | RECMPR 2X7 | 27.A6
KA1261:A2 | SC | 132224 | WHT | 20 | 27.A6 | AF1322:24 | RECMPR 2X7 | 27.A6
KA1262:A1 | SC | 132209 | WHT | 20 | 27.B6 | AF1322:09 | RECMPR 2X7 | 27.B6
KA1262:A2 | SC | 132225 | WHT | 20 | 27.B6 | AF1322:25 | RECMPR 2X7 | 27.B6
KA1263:A1 | SC | 132210 | WHT | 20 | 27.C6 | AF1322:10 | RECMPR 2X7 | 27.C6
KA1263:A2 | SC | 132226 | WHT | 20 | 27.C6 | AF1322:26 | RECMPR 2X7 | 27.C6
KA1264:A1 | SC | 132108 | WHT | 20 | 27.D6 | AF1321:08 | RECMPR 2X7 | 27.D6
KA1264:A2 | SC | 132124 | WHT | 20 | 27.D6 | AF1321:24 | RECMPR 2X7 | 27.D6
SA7774:11 | SC | SA777411 | WHT | 20 | 10.D1 | AF1303:39 | RECMPR 2X7 | 10.D6
SA7774:12 | SC | SA777412 | WHT | 20 | 10.D1 | AF1303:07 | RECMPR 2X7 | 10.D6
SA7774:13 | SC | SA777413 | WHT | 20 | 10.D1 | AF1303:40 | RECMPR 2X7 | 10.D6
SA7774:14 | SC | SA777414 | WHT | 20 | 10.D1 | AF1303:08 | RECMPR 2X7 | 10.D6
SB7540:B1-11 | SC | ESTOPB | WHT | 20 | 10.A1 | XT1311:3 | RECMPR 2X7 | 10.A5
SB7540:B1-12 | SC | ESTOPC | WHT | 20 | 10.A1 | XT1311:4 | RECMPR 2X7 | 10.A5
SB7540:B2-11 | SC | SB7540B211 | WHT | 20 | 10.A1 | AF1304:34 | RECMPR 2X7 | 10.A6
SB7540:B2-12 | SC | SB7540B212 | WHT | 20 | 10.A1 | AF1304:02 | RECMPR 2X7 | 10.A6
SB7770:13 | SC | SB777013 | WHT | 20 | 10.A1 | AF1303:35 | RECMPR 2X7 | 10.A6
SB7770:14 | SC | SB777014 | WHT | 20 | 10.A1 | AF1303:03 | RECMPR 2X7 | 10.A6
SB7771:13 | SC | SB777113 | WHT | 20 | 10.B1 | AF1303:36 | RECMPR 2X7 | 10.B6
SB7771:14 | SC | SB777114 | WHT | 20 | 10.B1 | AF1303:04 | RECMPR 2X7 | 10.B6
SB7772:13 | SC | SB777213 | WHT | 20 | 10.C1 | AF1303:37 | RECMPR 2X7 | 10.C6
SB7772:14 | SC | SB777214 | WHT | 20 | 10.C1 | AF1303:05 | RECMPR 2X7 | 10.C6
SB7773:13 | SC | SB777313 | WHT | 20 | 10.C1 | AF1303:38 | RECMPR 2X7 | 10.C6
SB7773:14 | SC | SB777314 | WHT | 20 | 10.C1 | AF1303:06 | RECMPR 2X7 | 10.C6
SH0455:11 | SC | SH045511 | WHT | 20 | 9.B1 | XT1354:6 | RECMPR 2X7 | 9.B5
SH0455:12 | SC | SH045512 | WHT | 20 | 9.B1 | XT1354:7 | RECMPR 2X7 | 9.B5
SH0455:13 | SC | FU1301 | WHT | 20 | 9.B1 | XT1354:4 | RECMPR 2X7 | 9.B5
SH0455:14 | SC | SH045514 | WHT | 20 | 9.B1 | XT1354:5 | RECMPR 2X7 | 9.B5
SH0455:X1 | SC | 0V | WHT | 20 | 9.A1 | XT1354:3 | RECMPR 2X7 | 9.B5
SH0455:X2 | SC | SH0455X2 | WHT | 20 | 9.A1 | XT1355:1 B1 | RECMPR 2X7 | 9.A5
UJ1100:24V(-) | SC | 0V | WHT | 16 | 6.C3 | XT1302:3 | RECMPR 2X7 | 5.D5
HA0454:BLK-2 | WC0454 | HA0454BLK2 | 1 | 18 | 9.A1 | AF1302:04 | RECMPR 2X7 | 9.A6
HA0454:BLK-1 | WC0454 | HA0454BLK1 | 2 | 18 | 9.A1 | AF1302:20 | RECMPR 2X7 | 9.A6
BA1101:L1 | WC9016 | AU1320L2 | ENET | CABLE | 3.A6 | AU1320:L2 | RECMPR 2X7 | 3.A5
SolarTools ver. 24.0.84.24712 (Jul 31, 2025)
Report date: 4/23/2026 10:52 AM

## Panel Errors
Panel Errors
Project # | 4M839
Project Name | Enbridge Gas
Revision | B
Controls DE | K. BOLIN
Phone:
Controls ME | S. LOZA
Phone:
From | [6 empty] | To
Device ID | Location | Cable (W) Conductor (SC) Jumper Clip (JC) | Wire ID | Wire No. | Gauge/Size | Page/Zone | Device ID | Location | Page/Zone
KA1260_U4:11 | PANEL | SC |  | U4_READY_LOAD2 |  | 27.D1 | AF1323:13 | RECMPR 2X7 | 27.D6
SolarTools ver. 24.0.84.24712 (Jul 31, 2025)
Report date: 4/23/2026 10:52 AM

## Cable Part Numbers
Cable Part Numbers |  |  | SolarTools ver. 24.0.84.24712 (Jul 31, 2025)
Project # | 4M839
Report date: 4/23/2026 10:52 AM
Project Name | Enbridge Gas
Revision | B
Controls DE | K. BOLIN
Phone:
Controls ME | S. LOZA
Phone:
Device ID |  | Part Number |  | Description
WC0101 |  | 1302073-36 |  | CABLE, COMMUNICATION CABLE - 36 INCHES
WC0001 |  | 1302073-36 |  | CABLE, ETHERNET - 36 INCHES
WC0002 |  | 1302073-36 |  | CABLE, ETHERNET - 36 INCHES
WC0009 |  | 1302073-36 |  | CABLE, ETHERNET - 36 INCHES
WC0454 |  | PART OF 1103208-1 |  | CABLE, 2 CONDUCTOR UNSHIELDED PART OF HORN
WC0681 |  | 1302073-36 |  | CABLE
WC9014 |  | 1302073-36 |  | CABLE, ETHERNET - 36 INCHES
WC9016 |  | 1302073-36 |  | CABLE, ETHERNET - 36 INCHES

## Part Number List
Part Number List |  | SolarTools ver. 24.0.84.24712 (Jul 31, 2025)
Project # | 4M839
Report date: 4/23/2026 10:52 AM
Project Name | Enbridge Gas
Revision | B
Controls DE | K. BOLIN
Phone:
Controls ME | S. LOZA
Phone:
Device ID | Part Number | Description | Location
FU1320 | 1043265-1,1043265-3 | FUSE, 2A | JB72
XT0771 | DRIVEN COMMON | TERMINAL STRIP, SYSTEM FUNCTION (USE) | JB771
XT0772 | DRIVEN COMMON | TERMINAL STRIP, SYSTEM FUNCTION (USE) | JB771
XT0774 | DRIVEN COMMON | TERMINAL STRIP, SYSTEM FUNCTION (USE) | JB771
XT0773 | DRIVEN COMMON | TERMINAL STRIP, SYSTEM FUNCTION (USE) | JB773
UAI7763 | PART OF JB7763 | ISOLATOR, LUBE OIL TEMPERATURE | JB7763
CCDTG7760_FLT | CUSTOMER DEFINED | CUSTOMER CONNECTION, DSR ENCLOSURE^GAS DETECTOR FAULT | PANEL
CCDTG7760_H | CUSTOMER DEFINED | CUSTOMER CONNECTION, DSR ENCLOSURE^GAS DETECTOR HIGH ALARM | PANEL
CCDTG7760_L | CUSTOMER DEFINED | CUSTOMER CONNECTION, DSR ENCLOSURE^GAS DETECTOR LOW ALARM | PANEL
KA1260_U1 | CUSTOMER CONNECTION | CUSTOMER CONNECTION, U1_DRY SEAL RECOMPRESSOR ENABLE | PANEL
KA1260_U2 | CUSTOMER CONNECTION | CUSTOMER CONNECTION, U2_DRY SEAL RECOMPRESSOR ENABLE | PANEL
KA1260_U3 | CUSTOMER CONNECTION | CUSTOMER CONNECTION, U3_DRY SEAL RECOMPRESSION ENABLE | PANEL
KA1260_U4 | CUSTOMER CONNECTION | CUSTOMER CONNECTION, U4_DRY SEAL RECOMPRESSION ENABLE | PANEL
U1_DSR_ALARM | CUSTOMER DEFINED | SOLAR CS CONNECTION, DRY SEAL GAS^RECOMPRESSION SYSTEM READY TO RUN | PANEL
U2_DSR_ALARM | CUSTOMER DEFINED | SOLAR CS CONNECTION, DRY SEAL GAS^RECOMPRESSION SYSTEM READY TO RUN | PANEL
U3_DSR_ALARM | CUSTOMER DEFINED | SOLAR CS CONNECTION, DRY SEAL GAS^RECOMPRESSION SYSTEM READY TO RUN | PANEL
U4_DSR_ALARM | CUSTOMER DEFINED | SOLAR CS CONNECTION, DRY SEAL GAS^RECOMPRESSION SYSTEM READY TO RUN | PANEL
AF1301 | 2684693-19,2684693-33 | 5094-IY8XT, 8 ANALOG INPUT, TC/RTD/ I&V | RECMPR 2X7
AF1302 | 2684693-17,2684693-24 | 5094-OB16XT, 16 DISCRETE OUTPUT | RECMPR 2X7
AF1303 | 2684693-48,2684693-51 | 5094-IB32XT, 32 DISCRETE INPUT | RECMPR 2X7
AF1304 | 2684693-18,2684693-28 | 5094-IB16SXT, 16 DISCRETE INPUT, S | RECMPR 2X7
AF1305 | 2684693-18,2684693-55 | 5094-OB16SXT, 16 DISCRETE OUTPUT, S | RECMPR 2X7
AF1306 | 2684693-18,2684693-56 | 5094-IF8IHXT, 8 ANALOG INPUT, ISOLATED | RECMPR 2X7
AF1321 | 2684693-17,2684693-24 | 5094-OB16XT, 16 DISCRETE OUTPUT | RECMPR 2X7
AF1322 | 2684693-17,2684693-24 | 5094-OB16XT, 16 DISCRETE OUTPUT | RECMPR 2X7
AF1323 | 2684693-17,2684693-23 | 5094-IB16XT, 16 DISCRETE INPUT | RECMPR 2X7
AF1324 | 2684693-18,2684693-56 | 5094-IF8IHXT, 8 ANALOG INPUT, ISOLATED | RECMPR 2X7
AF1325 | 2684693-19,2684693-33 | 5094-IY8XT, 8 ANALOG INPUT, TC/RTD/ I&V | RECMPR 2X7
AF1326 | 2684693-18,2684693-30 | 5094-IF4IHSXT, 4 ANALOG INPUT, S | RECMPR 2X7
AP0601 | 1089241-20 | MODULE, BLANK FILLER | RECMPR 2X7
AP0602 | 1089241-40 | 1756-EN2TRXT, ETHERNET | RECMPR 2X7
AP0603 | 1089241-40 | 1756-EN2TRXT, ETHERNET | RECMPR 2X7
AP0604 | 1089241-40 | 1756-EN2TRXT, ETHERNET | RECMPR 2X7
AP0605 | 1089241-20 | MODULE, BLANK FILLER | RECMPR 2X7
AP0606 | 1089241-36 | 1756-EN2TXT, ETHERNET | RECMPR 2X7
AR0600 | 1089241-29 | RACK CHASSIS, 1756-A7XT (7 SLOT) | RECMPR 2X7
AT0600 | 1089241-43 | 1756-L83EXTS, CONTROLLER^GUARDLOGIX | RECMPR 2X7
AT0681 | 1634974-100 | GATEWAY MODULE, TURBOTRONIC GATEWAY | RECMPR 2X7
AU1300 | 2684693-22 | 5094-AENTRXT, FLEX 5000 I/O | RECMPR 2X7
AU1320 | 2684693-22 | 5094-AENTRXT, FLEX 5000 I/O | RECMPR 2X7
BA0009 | 1271449-4 | MEDIA CONVERTER, ETHERNET-FIBER OPTIC | RECMPR 2X7
FU0009 | 1043265-1,1043265-3 | FUSE, 2A | RECMPR 2X7
FU0131 | 1043265-1,1043265-5 | FUSE, 10A | RECMPR 2X7
FU0681 | 1043265-1,1043265-4 | FUSE, 5A | RECMPR 2X7
FU1301 | 1043265-1,1043265-7 | FUSE, 20A | RECMPR 2X7
FU1302 | 1043265-1,1043265-7 | FUSE, 20A | RECMPR 2X7
FU1303 | 1043265-1,1043265-5 | FUSE, 10A | RECMPR 2X7
FU1305 | 1043265-1,1043265-5 | FUSE, 10A | RECMPR 2X7
FU1306 | 1043265-1,1043265-5 | FUSE, 10A | RECMPR 2X7
FU1307 | 1043265-1,1043265-5 | FUSE, 10A | RECMPR 2X7
FU1321 | 1043265-1,1043265-5 | FUSE, 10A | RECMPR 2X7
FU1322 | 1043265-1,1043265-5 | FUSE, 10A | RECMPR 2X7
FU1323 | 1043265-1,1043265-5 | FUSE, 10A | RECMPR 2X7
FU7701 | 1043265-1,1043265-5 | FUSE, 10A | RECMPR 2X7
FU7702 | 1043265-1,1043265-5 | FUSE, 10A | RECMPR 2X7
FU7763 | 1043265-1,1043265-3 | FUSE, 2A | RECMPR 2X7
GR1301 | 903849C1 | RAIL GROUND, DIN RAIL GROUNDING | RECMPR 2X7
GR1302 | 903849C1 | RAIL GROUND, DIN RAIL GROUNDING | RECMPR 2X7
GR1303 | 903849C1 | RAIL GROUND, DIN RAIL GROUNDING | RECMPR 2X7
GR1304 | 903849C1 | RAIL GROUND, DIN RAIL GROUNDING | RECMPR 2X7
KA0351 | 1061979-1 | RELAY, BACKUP SYSTEM RESET | RECMPR 2X7
KA0352 | 1061979-1 | RELAY, BACKUP SYSTEM RESET | RECMPR 2X7
KA0353 | 1061979-1 | RELAY, NO EMERGENCY SHUTDOWN SUMMARY | RECMPR 2X7
KA0354 | 1061979-1 | RELAY, NO EMERGENCY SHUTDOWN SUMMARY | RECMPR 2X7
KA0355 | 1061979-1 | RELAY, NO EMERGENCY SHUTDOWN SUMMARY | RECMPR 2X7
KA0356 | 1061979-1 | RELAY, NO EMERGENCY SHUTDOWN SUMMARY | RECMPR 2X7
KA0357 | 1061979-1 | RELAY, NO EMERGENCY SHUTDOWN SUMMARY | RECMPR 2X7
KA0358 | 1061979-1 | RELAY, NO EMERGENCY SHUTDOWDN SUMMARY | RECMPR 2X7
KA0359 | 1061979-1 | RELAY, NO EMERGENCY SHUTDOWN SUMMARY | RECMPR 2X7
KA0360 | 1061979-1 | RELAY, NO EMERGENCY SHUTDOWN SUMMARY | RECMPR 2X7
KA0361 | 1061979-1 | RELAY, NO EMERGENCY SHUTDOWN SUMMARY | RECMPR 2X7
KA0362 | 1061979-1 | RELAY, NO EMERGENCY SHUTDOWN SUMMARY | RECMPR 2X7
KA0363 | 1061979-1 | RELAY, NO EMERGENCY SHUTDOWN SUMMARY | RECMPR 2X7
KA0364 | 1061979-1 | RELAY, NO EMERGENCY SHUTDOWN SUMMARY | RECMPR 2X7
KA0365 | 1061979-1 | RELAY, NO EMERGENCY SHUTDOWN SUMMARY | RECMPR 2X7
KA1344 | 1061979-1 | RELAY, CONTROLLER ACTIVE | RECMPR 2X7
KA1345 | 1061979-1 | RELAY, CONTROLLER ACTIVE | RECMPR 2X7
KA7701 | 1061979-1 | RELAY, RECOMPRESSOR INLET SHUTOFF | RECMPR 2X7
KA7702 | 1061979-1 | RELAY, RECOMPRESSOR ENABLE | RECMPR 2X7
KA7703 | 1061979-1 | RELAY, RECOMPRESSOR VENT VALVE | RECMPR 2X7
KA7705 | 1061979-1 | RELAY, RECOMPRESSOR OUTLET SHUTOFF | RECMPR 2X7
KA7760 | 1061979-1 | RELAY, LUBE OIL HEATER | RECMPR 2X7
KA7768 | 1061979-1 | RELAY, DSR ENCLOSURE HEATER | RECMPR 2X7
KA7770 | 1061979-1 | RELAY, COMPRESSOR DISCHARGE GAS | RECMPR 2X7
KT1325 | 2651077-3 | TIMER RELAY, WATCHDOG | RECMPR 2X7
RR3041 | 981090C1 | RESISTOR, 3.01K OHM | RECMPR 2X7
RR3042 | 981089C1 | RESISTOR, 1.0K OHM | RECMPR 2X7
UJ0131 | 1286570-1 | POWER CONVERTER, AC/DC INPUT TO 28V DC OUTPUT | RECMPR 2X7
UV0600 | 1089241-28 | POWER SUPPLY, RSLOGIX CHASSIS | RECMPR 2X7
XT0009 | 1066730-7,1066730-8,1067996-4 | TERMINAL BLOCK, SPRING, 4 CONDUCTOR,30-12 AWG (0.05-3.31 MM2),NON-IS | RECMPR 2X7
XT0681 | 1066730-7,1066730-8,1067996-4 | TERMINAL BLOCK, SPRING, 4 CONDUCTOR,30-12 AWG (0.05-3.31 MM2),NON-IS | RECMPR 2X7
XT1301 | 1066730-16 | TERMINAL STRIP, 2 CONDUCTOR | RECMPR 2X7
XT1302 | 1066730-7,1066730-8,1067996-4 | TERMINAL BLOCK, SPRING, 4 CONDUCTOR,30-12 AWG (0.05-3.31 MM2),NON-IS | RECMPR 2X7
XT1303 | 1066730-7,1066730-8,1067996-4 | TERMINAL BLOCK, SPRING, 4 CONDUCTOR,30-12 AWG (0.05-3.31 MM2),NON-IS | RECMPR 2X7
XT1304 | 1066730-7,1066730-8,1067996-4 | TERMINAL BLOCK, SPRING, 4 CONDUCTOR,30-12 AWG (0.05-3.31 MM2),NON-IS | RECMPR 2X7
XT1305 | 1066730-7,1066730-8,1067996-4 | TERMINAL BLOCK, SPRING, 4 CONDUCTOR,30-12 AWG (0.05-3.31 MM2),NON-IS | RECMPR 2X7
XT1311 | 1066730-7,1066730-8,1067996-4 | TERMINAL BLOCK, SPRING, 4 CONDUCTOR,30-12 AWG (0.05-3.31 MM2),NON-IS | RECMPR 2X7
XT1312 | 1066730-7,1066730-8,1067996-4 | TERMINAL BLOCK, SPRING, 4 CONDUCTOR,30-12 AWG (0.05-3.31 MM2),NON-IS | RECMPR 2X7
XT1320 | 1066730-7,1066730-8,1067996-4 | TERMINAL BLOCK, SPRING, 4 CONDUCTOR,30-12 AWG (0.05-3.31 MM2),NON-IS | RECMPR 2X7
XT1354 | 1066730-7,1066730-8,1067996-4 | TERMINAL BLOCK, SPRING, 4 CONDUCTOR,30-12 AWG (0.05-3.31 MM2),NON-IS | RECMPR 2X7
XT1355 | 1066730-9 | DIODE TERMINAL STRIP, 4 CONDUCTOR | RECMPR 2X7
XT1385 | 1066730-7,1066730-8,1067996-4 | TERMINAL BLOCK, SPRING, 4 CONDUCTOR,30-12 AWG (0.05-3.31 MM2),NON-IS | RECMPR 2X7
XTFGA | 1066730-1 | TERMINAL STRIP, 4 CONDUCTOR | RECMPR 2X7
AT1101 | 1577354-4503 | WORKSTATION, VERSA VIEW 1200H | RECMPR 2X7 BOX
BA1101 | 1337728-1 | SWITCH, ETAP, DLR INTERFACE | RECMPR 2X7 BOX
FU1102 | 1043265-1,1043265-5 | FUSE, 10A | RECMPR 2X7 BOX
GR1305 | 903849C1 | RAIL GROUND, DIN RAIL GROUNDING | RECMPR 2X7 BOX
HA0454 | 1103208-101 | HORN, AUDIBLE ALARM | RECMPR 2X7 BOX
HL7775 | 2380746-7 | LIGHT, ALARM SUMMARY, AMBER | RECMPR 2X7 BOX
HL7776 | 2380746-7 | LIGHT, STOPPED, RED | RECMPR 2X7 BOX
HL7777 | 2380746-7 | LIGHT, RUNNING, GREEN | RECMPR 2X7 BOX
HL7778 | 2380746-7 | LIGHT, SYSTEM DISABLED, RED | RECMPR 2X7 BOX
HL7779 | 2380746-7 | LIGHT, SYSTEM ENABLED, GREEN | RECMPR 2X7 BOX
IEG0141 | 232941-110 | BUS BAR, INSTRUMENT EARTH GROUNDING | RECMPR 2X7 BOX
KA1261 | 1061979-1 | RELAY, U1_DSR_ALARM | RECMPR 2X7 BOX
KA1262 | 1061979-1 | RELAY, U2_DSR_ALARM | RECMPR 2X7 BOX
KA1263 | 1061979-1 | RELAY, U3_DSR_ALARM | RECMPR 2X7 BOX
KA1264 | 1061979-1 | RELAY, U4_DSR_ALARM | RECMPR 2X7 BOX
PEG0141 | 232941-200 | BUS BAR, POWER EARTH GROUNDING | RECMPR 2X7 BOX
SA7774 | 2380746-5 | SELECTOR SWITCH, OFF / LOCAL / REMOTE | RECMPR 2X7 BOX
SB7540 | 2380746-4 | PUSHBUTTON SWITCH, EMERGENCY STOP | RECMPR 2X7 BOX
SB7770 | 2380746-1 | PUSHBUTTON SWITCH, SYSTEM RESET | RECMPR 2X7 BOX
SB7771 | 2380746-1 | PUSHBUTTON SWITCH, ACKNOWLEDGE | RECMPR 2X7 BOX
SB7772 | 2380746-1 | PUSHBUTTON SWITCH, HORN SILENCE | RECMPR 2X7 BOX
SB7773 | 2380746-1 | PUSHBUTTON SWITCH, LAMP TEST | RECMPR 2X7 BOX
SH0455 | 2380746-3 | LIGHTED SWITCH, BACKUP SYSTEM ACTIVE/RESET, AMBER | RECMPR 2X7 BOX
UJ1100 | 1088442-4 | POWER CONVERTER, DC/DC INPUT TO 24V DC OUTPUT | RECMPR 2X7 BOX