## Blue Labels
(SHT 1) TURBINE BOX^DOOR^JB70 | (SHT 10) LOOSESHIP DOOR PANEL | (SHT 2) TURBINE BOX^LEFT RAIL^JB70 | (SHT 3) TURBINE BOX^RIGHT RAIL^JB70 | (SHT 4) TURBINE PANEL A JB70 | (SHT 5) TURBINE PANEL B JB70 | (SHT 6) RIGHT RAIL^JB73 | (SHT 7) HP COMPRESSOR^JB73 ONSKID PANEL | (SHT 8) BOP PANEL^JB74 | (SHT 9) LOOSESHIP PANEL
AT1100 | SB0400 | PC0470 | GR1100 | UJ0131 | AT0680 | GR0125 | IEG0130 | FU0180 | XT0561
SB0471 |  | BA1100 |  | XT0014 | XT0680 |  | KA0120 | FU0181 | XT0562
SB0473 |  | FU1101 |  | XT0138 | GR0680 |  | KA4401 | FU0184 | FU0560
SB0474 |  | FU1100 |  | XT0134 | FU0680 |  | XT0121 | XT0180 | FU0200
SA0471 |  | UV0291 |  | FU0137 | AF0400 |  | XT0520 | AF0185 | FU0201
SA0473 |  | FU0291 |  | FU0136 | AF0410 |  | FU0130 | AF0184 | FU0273
SH0470 |  | XT0291 |  | GR0131 | AF0420 |  | FU0131 | AF0183 | XT0200
SB0472 |  | XT0292 |  | FU0011 | AF0430 |  | XT0845 | AF0182 | AU0200
SA0474 |  | XT0137 |  | FU0020 | AF0450 |  | GR0845 | AF0181 | AF0201
SH0471 |  | GR1101 |  | FU0012 | XT0400 |  | AF0510 | AU0180 | AF0202
SH0472 |  |  |  | FU0013 | XT0110 |  | AF0520 | BA1212 | XT7112
HA0472 |  |  |  | FU0014 | FU0110 |  | XT0500 | XT0141 | XT3150
|  |  |  | FU0015 | FU0113 |  | XT0130 | GR0180 | KA3104
|  |  |  | XT0011 | IEG0230 |  | FU0120 | XT0570 | KA3103
|  |  |  | FU0021 | XT0136 |  | FU0121 | FU0570 | KA3220
|  |  |  | FU0022 | XT0233 |  | FU0122 | FU0140 | GR0200
|  |  |  | GR0132 | XT0235 |  | AF1212 | FU0141 | IEG0200
|  |  |  | AT0600 | XT0236 |  | AF1211 | FU0142
|  |  |  | UV0600 | XT0237 |  | AF1210 | FU0143
|  |  |  | AP0601 | XT0240 |  | AF1209 | XT0140
|  |  |  | AP0602 | FU0123 |  | AF1208 | KA0531
|  |  |  | AP0603 | FU0210 |  | AF1207 | KA0532
|  |  |  | AP0604 | FU0212 |  | GR0124 | KA0533
|  |  |  | AP0605 | FU0213 |  | AU1200 | KA0534
|  |  |  | AP0606 | KA0130 |  | AF1201 | KA0535
|  |  |  | AR0600 | KA0131 |  | AF1202 | KA0536
|  |  |  | FU0010 | KA0132 |  | AF1203 | KA0537
|  |  |  | FU0139 | KA0141 |  | AF1204 | KA0540
|  |  |  | FU0211 | KA0133 |  | AF1205 | KA0541
|  |  |  | XT0139 | KA0134 |  | AF1206 | KA0550
|  |  |  | XT0135 | KA0136 |  | GR0120 | KA0551
|  |  |  | UA1520 | KA0137 |  | WC8058 | KA0552
|  |  |  | XT1521 | KA0138 |  |  | KA0553
|  |  |  | XTFGH | KA0144 |  |  | KA0554
|  |  |  | XT0575 | KA0222 |  |  | KT0572
|  |  |  | XT7512 | KA0235 |  |  | KT0573
|  |  |  | KA0221 | KA0236 |  |  | XT0572
|  |  |  | KA0270 | KA0237 |  |  | XT0573
|  |  |  | KA2160 | KA0238 |  |  | FU1212
|  |  |  | KA2161 | KA0239 |  |  | GR0257
|  |  |  | KA0224 | KA0240 |  |  | IEG0257
|  |  |  | KA0135 | KA0248 |  |  | AU0140
|  |  |  | XT0150 | KA0250 |  |  | AF0141
|  |  |  | GR0135 | KA0241 |  |  | AF0142
|  |  |  | PEG0130 | KA0242 |  |  | AF0143
|  |  |  | FU0090 | KA0243 |  |  | AF0144
|  |  |  | FU0091 | KA0244 |  |  | AF0145
|  |  |  | FU0092 | KA0246 |  |  | AF0146
|  |  |  | FU0093 | KA0247 |  |  | GR0140
|  |  |  | XT0090 | KA0245
|  |  |  | AU0090 | KA0249
|  |  |  | AF0091 | KA0231
|  |  |  | AF0092 | KA0232
|  |  |  | AF0093 | KA0233
|  |  |  | AF0094 | KA0234
|  |  |  | AF0095 | KA0230
|  |  |  | AF0096 | KT0140
|  |  |  | GR0133 | KT0141
|  |  |  | FU0080 | KT0142
|  |  |  | FU0081 | KT0143
|  |  |  | FU0082 | KT0144
|  |  |  | XT0080 | KT0145
|  |  |  | XT0085 | KT0146
|  |  |  | AU0080 | GR0231
|  |  |  | AF0081 | AF0068
|  |  |  | AF0082 | AF0067
|  |  |  | AF0083 | AF0066
|  |  |  | AF0084 | AF0065
|  |  |  | AF0085 | AF0064
|  |  |  | AF0086 | AF0063
|  |  |  | AF0087 | AF0062
|  |  |  | XT0050 | AF0061
|  |  |  | GR0134 | AU0060
FU0060
FU0061
FU0062
FU0063
XT0060
GR0232
FU0070
FU0071
XT0070
AU0070
AF0071
AF0072
AF0073
AF0074
AF0075
AF0076
AF0077
KA1020
GR0233
UA1200

## White Labels
(SHT 8) BOP PANEL^JB74 | (SHT 7) HP COMPRESSOR^JB73 ONSKID PANEL | (SHT 9) LOOSESHIP PANEL | (SHT 1) TURBINE BOX^DOOR^JB70 - (SHT 4) TURBINE PANEL A JB70 | (SHT 3) TURBINE BOX^RIGHT RAIL^JB70 - (SHT 5) TURBINE PANEL B JB70 | (SHT 4) TURBINE PANEL A JB70 | (SHT 4) TURBINE PANEL A JB70 - (SHT 5) TURBINE PANEL B JB70 | (SHT 5) TURBINE PANEL B JB70
AF0143G | AF1203G | AU0200G | PEG01304 | IEG023014 | AF0083G | IEG02301 | AF0064G
AF0144G | AF1204G | IEG02001 |  |  | AF0084G | IEG023011 | AF0065G
AU0140G | AF1205G | IEG02002 |  |  | AF0085G | IEG02302 | AF0066G
AU0180G | AF1206G |  |  |  | AF0094G | IEG02303 | AF0071G
IEG02571 | AF1208G |  |  |  | AU0080G | IEG02306 | AF0072G
IEG02572 | AF1209G |  |  |  | AU0090G | IEG02307 | AF0073G
IEG02573 | AF1210G |  |  |  | UV0600G |  | AF0074G
IEG02574 | AF1211G | [5 empty] | AF0075G
IEG02575 | AU1200G | [5 empty] | AU0060G
| IEG01301 | [5 empty] | AU0070G
| IEG01303 | [5 empty] | IEG023010
| IEG01304 | [5 empty] | IEG023012
| IEG01307 | [5 empty] | IEG023013
| XT05001 | [5 empty] | IEG02304
IEG02305
IEG02308
IEG02309
XT04001
XT04002

## Heat Shrink Labels
(SHT 4) TURBINE PANEL A JB70 | (SHT 4) TURBINE PANEL A JB70 - (SHT 5) TURBINE PANEL B JB70 | (SHT 5) TURBINE PANEL B JB70
WC4563 | WC4749 | WC4193
WC4524

## BOP PANEL^JB74
BOP PANEL^JB74
Project # | J0630
Project Name | TC TUSCARORA SHOETREE CR
Revision | A.3
Controls DE | G.JP
Phone:
Controls ME
Phone:
From | [5 empty] | To
Device ID | Cable (W) Conductor (SC) Jumper Clip (JC) | Wire No. | Wire ID | Gauge/Size | Page/Zone | Device ID | Location | Page/Zone
XT0140:3 | JC | 0V | CLIP | --- | 19.A5 | XT0140:2 | BOP PANEL^JB74 | 19.A5
XT0140:4 | JC | 0V | CLIP | --- | 19.A5 | XT0140:3 | BOP PANEL^JB74 | 19.A5
XT0180:1 | JC | 0V | CLIP | --- | 19.D1 | XT0180:2 | BOP PANEL^JB74 | 19.D1
AF0141:00 | SC | KA053121 | WHT | 20 | 81.A7 | KA0531:21 | BOP PANEL^JB74 | 81.A6
AF0141:02 | SC | 014102 | WHT | 20 | 81.B7 | KA0552:11 | BOP PANEL^JB74 | 81.B6
AF0141:04 | SC | KA053211 | WHT | 20 | 82.A7 | KA0532:11 | BOP PANEL^JB74 | 82.A6
AF0141:06 | SC | 014106 | WHT | 20 | 82.B7 | KA0553:11 | BOP PANEL^JB74 | 82.B6
AF0141:12 | SC | 014112 | WHT | 20 | 83.B7 | KA0554:11 | BOP PANEL^JB74 | 83.B6
AF0141:14 | SC | KA053111 | WHT | 20 | 80.A7 | KA0531:11 | BOP PANEL^JB74 | 80.A5
AF0141:16 | SC | KA7621X2 | WHT | 20 | 81.A7 | XT0572:4 | BOP PANEL^JB74 | 81.A5
AF0141:20 | SC | KA7641X2 | WHT | 20 | 82.A7 | XT0572:5 | BOP PANEL^JB74 | 82.A5
AF0141:32 | SC | KA055011 | WHT | 20 | 81.A7 | KA0550:11 | BOP PANEL^JB74 | 81.A6
AF0141:36 | SC | 014136 | WHT | 20 | 82.A7 | KA0551:11 | BOP PANEL^JB74 | 82.A6
AF0141:COM | SC | 0V | WHT | 12 | 19.B2 | XT0140:3 | BOP PANEL^JB74 | 19.A5
AF0141:V+ | SC | FU0141 | WHT | 16 | 19.B2 | FU0141:LD | BOP PANEL^JB74 | 19.C1
AF0142:COM | SC | AF0142N | WHT | 16 | 19.B3 | AF0143:COM | BOP PANEL^JB74 | 19.B3
AF0142:COM | SC | AU0140N | WHT | 16 | 19.B3 | AU0140:COM | BOP PANEL^JB74 | 19.B1
AF0142:V+ | SC | AF0142P | WHT | 16 | 19.B3 | AF0143:V+ | BOP PANEL^JB74 | 19.B3
AF0142:V+ | SC | AU0140P | WHT | 16 | 19.B3 | AU0140:V+ | BOP PANEL^JB74 | 19.B1
AF0143:COM | SC | AF0143N | WHT | 16 | 19.B3 | AF0144:COM | BOP PANEL^JB74 | 19.B4
AF0143:SH | SC | AF0143G | GRN | 14 | 19.B3 | AF0144:SH | BOP PANEL^JB74 | 19.B4
AF0143:SH | SC | AU0140G | GRN | 14 | 19.B3 | AU0140:GND | BOP PANEL^JB74 | 19.B1
AF0143:V+ | SC | AF0143P | WHT | 16 | 19.B3 | AF0144:V+ | BOP PANEL^JB74 | 19.B4
AF0144:COM | SC | AF0144N | WHT | 16 | 19.B4 | AF0145:COM | BOP PANEL^JB74 | 19.B5
AF0144:SH | SC | AF0144G | GRN | 14 | 19.B4 | AF0145:SH | BOP PANEL^JB74 | 19.B5
AF0144:V+ | SC | AF0144P | WHT | 16 | 19.B4 | AF0145:V+ | BOP PANEL^JB74 | 19.B5
AF0145:SH | SC | IEG02571 | GRN | 14 | 19.B5 | IEG0257:1 | BOP PANEL^JB74 | 19.C5
AF0146:COM | SC | 0V | WHT | 14 | 19.B5 | XT0140:3 | BOP PANEL^JB74 | 19.A5
AF0146:V+ | SC | FU0142 | WHT | 14 | 19.B5 | FU0142:LD | BOP PANEL^JB74 | 19.C1
AF0181:COM | SC | 0V | WHT | 12 | 19.D2 | XT0180:2 | BOP PANEL^JB74 | 19.D1
AF0181:V+ | SC | FU0181 | WHT | 16 | 19.D2 | FU0181:LD | BOP PANEL^JB74 | 19.D1
AF0182:00 | SC | JP4 | VIO | 20 | 26.B7 | AF0182:32 | BOP PANEL^JB74 | 26.B7
AF0182:COM | SC | AF0182N | WHT | 16 | 19.D3 | AF0183:COM | BOP PANEL^JB74 | 19.C3
AF0182:COM | SC | AU0180N | WHT | 16 | 19.D3 | AU0180:COM | BOP PANEL^JB74 | 19.C1
AF0182:V+ | SC | AF0182P | WHT | 16 | 19.D3 | AF0183:V+ | BOP PANEL^JB74 | 19.C3
AF0182:V+ | SC | AU0180P | WHT | 16 | 19.D3 | AU0180:V+ | BOP PANEL^JB74 | 19.C1
AF0183:04 | SC | ZSC76212 | WHT | 20 | 81.B7 | XT0572:2 | BOP PANEL^JB74 | 81.B5
AF0183:05 | SC | ZSC76412 | WHT | 20 | 82.B7 | XT0572:3 | BOP PANEL^JB74 | 82.B5
AF0183:20 | SC | KT0572A2 | WHT | 20 | 81.B7 | KT0572:A2 | BOP PANEL^JB74 | 81.B6
AF0183:21 | SC | KT0573A2 | WHT | 20 | 82.B7 | KT0573:A2 | BOP PANEL^JB74 | 82.B6
AF0183:COM | SC | AF0183N | WHT | 16 | 19.C3 | AF0185:COM | BOP PANEL^JB74 | 19.D5
AF0183:V+ | SC | AF0183P | WHT | 16 | 19.C3 | AF0185:V+ | BOP PANEL^JB74 | 19.D5
AF0184:00 | SC | 018400 | WHT | 20 | 81.D7 | KA0550:A1 | BOP PANEL^JB74 | 81.D6
AF0184:01 | SC | 018401 | WHT | 20 | 81.D7 | KA0552:A1 | BOP PANEL^JB74 | 81.D6
AF0184:02 | SC | 018402 | WHT | 20 | 82.C7 | KA0551:A1 | BOP PANEL^JB74 | 82.C5
AF0184:03 | SC | 018403 | WHT | 20 | 82.C7 | KA0553:A1 | BOP PANEL^JB74 | 82.C5
AF0184:04 | SC | 018404 | WHT | 20 | 83.C7 | KA0554:A1 | BOP PANEL^JB74 | 83.C5
AF0184:16 | SC | 018416 | WHT | 20 | 81.D7 | KA0550:A2 | BOP PANEL^JB74 | 81.D6
AF0184:17 | SC | 018417 | WHT | 20 | 81.D7 | KA0552:A2 | BOP PANEL^JB74 | 81.D6
AF0184:18 | SC | 018418 | WHT | 20 | 82.C7 | KA0551:A2 | BOP PANEL^JB74 | 82.C5
AF0184:19 | SC | 018419 | WHT | 20 | 82.C7 | KA0553:A2 | BOP PANEL^JB74 | 82.C5
AF0184:20 | SC | 018420 | WHT | 20 | 83.C7 | KA0554:A2 | BOP PANEL^JB74 | 83.C5
AF0184:COM | SC | 0V | WHT | 16 | 19.C4 | XT0180:1 | BOP PANEL^JB74 | 19.D1
AF0184:V+ | SC | FU0184 | WHT | 16 | 19.C4 | FU0184:LD | BOP PANEL^JB74 | 19.D1
AF0185:SH | SC | IEG02572 | GRN | 14 | 19.D5 | IEG0257:2 | BOP PANEL^JB74 | 19.D5
AF0185:SH | SC | AU0180G | GRN | 14 | 19.D5 | AU0180:GND | BOP PANEL^JB74 | 19.C1
AU0140:COM | SC | 0V | WHT | 16 | 19.B1 | XT0140:2 | BOP PANEL^JB74 | 19.A5
AU0140:V+ | SC | FU0140 | WHT | 16 | 19.B1 | FU0140:LD | BOP PANEL^JB74 | 19.B1
AU0180:COM | SC | 0V | WHT | 12 | 19.C1 | XT0180:1 | BOP PANEL^JB74 | 19.D1
AU0180:V+ | SC | FU0180 | WHT | 16 | 19.C1 | FU0180:LD | BOP PANEL^JB74 | 19.D1
BA1212:NEG | SC | UV0291N | WHT | 16 | 8.A2 | XT0141:2 | BOP PANEL^JB74 | 8.A5
BA1212:POS | SC | FU1212LD | WHT | 16 | 8.A2 | FU1212:LD | BOP PANEL^JB74 | 8.A3
FU0140:LI | SC | FU0570 | WHT | 12 | 19.B1 | FU0570:LD | BOP PANEL^JB74 | 19.A4
FU0140:LI | SC | FU0570 | WHT | 14 | 19.B1 | FU0141:LI | BOP PANEL^JB74 | 19.C1
FU0141:LI | SC | FU0570 | WHT | 14 | 19.C1 | FU0142:LI | BOP PANEL^JB74 | 19.C1
FU0142:LI | SC | FU0570 | WHT | 14 | 19.C1 | FU0143:LI | BOP PANEL^JB74 | 19.C1
FU0143:LD | SC | FU0143 | WHT | 14 | 19.C1 | XT0140:7 | BOP PANEL^JB74 | 21.C1
FU0143:LI | SC | FU0570 | WHT | 14 | 19.C1 | FU0180:LI | BOP PANEL^JB74 | 19.D1
FU0180:LI | SC | FU0570 | WHT | 14 | 19.D1 | FU0181:LI | BOP PANEL^JB74 | 19.D1
FU0181:LI | SC | FU0570 | WHT | 14 | 19.D1 | FU0184:LI | BOP PANEL^JB74 | 19.D1
FU0570:LI | SC | FU0136 | WHT | 12 | 19.A4 | XT0140:1 | BOP PANEL^JB74 | 19.A5
FU1212:LI | SC | UV0291P | WHT | 16 | 8.A3 | XT0141:1 | BOP PANEL^JB74 | 8.A5
GR0140: | SC | IEG02573 | GRN | 14 | 4.A4 | IEG0257:3 | BOP PANEL^JB74 | 4.A3
GR0180: | SC | IEG02575 | GRN | 14 | 4.A3 | IEG0257:5 | BOP PANEL^JB74 | 4.A3
GR0257: | SC | IEG02574 | GRN | 14 | 4.A3 | IEG0257:4 | BOP PANEL^JB74 | 4.A3
KA0531:24 | SC | KA053124 | WHT | 20 | 81.A6 | KA0540:A1 | BOP PANEL^JB74 | 81.A5
KA0531:A1 | SC | ESTOP | WHT | 20 | 21.A3 | KA0532:A1 | BOP PANEL^JB74 | 21.A3
KA0531:A1 | SC | ESTOP | WHT | 20 | 21.A3 | XT0140:6 | BOP PANEL^JB74 | 21.A2
KA0531:A2 | SC | 0V | WHT | 20 | 21.A3 | KA0532:A2 | BOP PANEL^JB74 | 21.A3
KA0531:A2 | SC | 0V | WHT | 20 | 21.A3 | KA0536:A2 | BOP PANEL^JB74 | 21.A3
KA0532:14 | SC | KA053214 | WHT | 20 | 82.A6 | KA0541:A1 | BOP PANEL^JB74 | 82.A5
KA0532:A1 | SC | ESTOP | WHT | 20 | 21.A3 | KA0533:A1 | BOP PANEL^JB74 | 21.B3
KA0532:A2 | SC | 0V | WHT | 20 | 21.A3 | KA0533:A2 | BOP PANEL^JB74 | 21.B3
KA0533:11 | SC | FU0143 | WHT | 14 | 21.C2 | XT0140:7 | BOP PANEL^JB74 | 21.C1
KA0533:A1 | SC | ESTOP | WHT | 20 | 21.B3 | KA0534:A1 | BOP PANEL^JB74 | 21.B3
KA0533:A2 | SC | 0V | WHT | 20 | 21.B3 | KA0534:A2 | BOP PANEL^JB74 | 21.B3
KA0534:A1 | SC | ESTOP | WHT | 20 | 21.B3 | KA0537:A1 | BOP PANEL^JB74 | 21.B3
KA0534:A2 | SC | 0V | WHT | 20 | 21.B3 | KA0537:A2 | BOP PANEL^JB74 | 21.B3
KA0535:11 | SC | KA053511 | WHT | 20 | 83.B6 | KA0554:14 | BOP PANEL^JB74 | 83.B6
KA0535:14 | SC | KA053514 | WHT | 20 | 83.B6 | XT0573:1 B2 | BOP PANEL^JB74 | 83.B5
KA0535:A1 | SC | KA0231A1 | WHT | 20 | 21.A3 | KA0536:A1 | BOP PANEL^JB74 | 21.A3
KA0535:A1 | SC | KA0231A1 | WHT | 20 | 21.A3 | XT0140:5 | BOP PANEL^JB74 | 21.A2
KA0535:A2 | SC | 0V | WHT | 20 | 21.A3 | KA0536:A2 | BOP PANEL^JB74 | 21.A3
KA0535:A2 | SC | 0V | WHT | 20 | 21.A3 | XT0140:4 | BOP PANEL^JB74 | 19.A5
KA0536:11 | SC | XT05732B1 | WHT | 20 | 83.B5 | XT0573:2 B1 | BOP PANEL^JB74 | 83.B5
KA0536:12 | SC | KA053612 | WHT | 20 | 83.B5 | XT0573:1 T1 | BOP PANEL^JB74 | 83.B5
KA0540:11 | SC | KA054011 | WHT | 20 | 81.A5 | KA0550:14 | BOP PANEL^JB74 | 81.A6
KA0540:21 | SC | ZSC76212 | WHT | 20 | 81.B5 | XT0572:2 | BOP PANEL^JB74 | 81.B5
KA0540:22 | SC | KA054012 | WHT | 20 | 81.B5 | KT0572:A1 | BOP PANEL^JB74 | 81.B6
KA0540:A2 | SC | KA7621X2 | WHT | 20 | 81.A5 | XT0572:4 | BOP PANEL^JB74 | 81.A5
KA0541:11 | SC | KA054111 | WHT | 20 | 82.A5 | KA0551:14 | BOP PANEL^JB74 | 82.A6
KA0541:21 | SC | ZSC76412 | WHT | 20 | 82.B5 | XT0572:3 | BOP PANEL^JB74 | 82.B5
KA0541:22 | SC | KA054112 | WHT | 20 | 82.B5 | KT0573:A1 | BOP PANEL^JB74 | 82.B6
KA0541:A2 | SC | KA7641X2 | WHT | 20 | 82.A5 | XT0572:5 | BOP PANEL^JB74 | 82.A5
KA0552:14 | SC | KA055214 | WHT | 20 | 81.B6 | XT0573:5 B2 | BOP PANEL^JB74 | 81.B5
KA0553:14 | SC | KA055314 | WHT | 20 | 82.B6 | XT0573:3 B2 | BOP PANEL^JB74 | 82.B5
KT0572:15 | SC | KA053312 | WHT | 20 | 21.C3 | KT0573:15 | BOP PANEL^JB74 | 21.C3
KT0572:16 | SC | KT057216 | WHT | 20 | 21.C3 | XT0573:2 B2 | BOP PANEL^JB74 | 83.B5
KT0572:16 | SC | KT057216 | WHT | 20 | 21.C3 | XT0573:5 T2 | BOP PANEL^JB74 | 81.B5
KT0573:15 | SC | KA053312 | WHT | 20 | 21.C3 | KA0533:12 | BOP PANEL^JB74 | 21.C2
KT0573:16 | SC | KT057316 | WHT | 20 | 21.C3 | XT0573:2 T2 | BOP PANEL^JB74 | 83.B5
KT0573:16 | SC | KT057316 | WHT | 20 | 21.C3 | XT0573:3 T2 | BOP PANEL^JB74 | 82.B5
XT0140:1 | SC | FU0136 | WHT | 16 | 19.A5 | XT0570:1 | BOP PANEL^JB74 | 19.A5
XT0140:2 | SC | 0V | WHT | 12 | 19.A5 | XT0570:2 | BOP PANEL^JB74 | 19.A5
XT0180:1 | SC | 0V | WHT | 16 | 19.D1 | XT0140:4 | BOP PANEL^JB74 | 19.A5
AU0140:L2 | WC0014 | AU0140L2 | ENET | CABLE | 2.B2 | AU0180:L1 | BOP PANEL^JB74 | 2.B3
AU0180:L2 | WC0018 | AU0180L2 | ENET | CABLE | 2.B3 | BA1212:L1 | BOP PANEL^JB74 | 2.B4
SolarTools ver. 24.0.84.24712 (Jul 31, 2025)
Report date: 3/3/2026 11:49 AM

## HP COMPRESSOR^JB73 ONSKID PANEL
HP COMPRESSOR^JB73 ONSKID PANEL
HP COMPRESSOR^JB73^ONSKID PANEL
Project # | J0630
Project Name | TC TUSCARORA SHOETREE CR
Revision | A.3
Controls DE | G.JP
Phone:
Controls ME
Phone:
From | [5 empty] | To
Device ID | Cable (W) Conductor (SC) Jumper Clip (JC) | Wire No. | Wire ID | Gauge/Size | Page/Zone | Device ID | Location | Page/Zone
XT0121:3 | JC | FU0122 | CLIP | --- | 67.A5 | XT0121:4 | HP COMPRESSOR^JB73 ONSKID PANEL | 67.C5
XT0121:4 | JC | FU0122 | CLIP | --- | 67.C5 | XT0121:5 | HP COMPRESSOR^JB73 ONSKID PANEL | 68.A5
XT0121:7 | JC | 0V | CLIP | --- | 67.A5 | XT0121:8 | HP COMPRESSOR^JB73 ONSKID PANEL | 67.C5
XT0121:8 | JC | 0V | CLIP | --- | 67.C5 | XT0121:9 | HP COMPRESSOR^JB73 ONSKID PANEL | 68.A5
XT0130:3 | JC | 0V | CLIP | --- | 18.A5 | XT0130:2 | HP COMPRESSOR^JB73 ONSKID PANEL | 18.A5
XT0130:4 | JC | 0V | CLIP | --- | 18.A5 | XT0130:3 | HP COMPRESSOR^JB73 ONSKID PANEL | 18.A5
AF0510:32 | SC | XT05001 | GRN | 16 | 18.A2 | XT0500:1 | HP COMPRESSOR^JB73 ONSKID PANEL | 18.C2
AF0510:53 | SC | 0V | WHT | 14 | 18.A2 | XT0130:2 | HP COMPRESSOR^JB73 ONSKID PANEL | 18.A5
AF0510:54 | SC | AF0520N | WHT | 16 | 18.A2 | AF0520:53 | HP COMPRESSOR^JB73 ONSKID PANEL | 18.A1
AF0510:55 | SC | FU0131 | WHT | 16 | 18.A2 | FU0131:LD | HP COMPRESSOR^JB73 ONSKID PANEL | 18.C1
AF0510:56 | SC | AF0520P | WHT | 16 | 18.A2 | AF0520:55 | HP COMPRESSOR^JB73 ONSKID PANEL | 18.A1
AF0520:32 | SC | XT05001 | GRN | 16 | 18.A1 | XT0500:1 | HP COMPRESSOR^JB73 ONSKID PANEL | 18.C2
AF1201:COM | SC | 0V | WHT | 14 | 18.D2 | XT0130:3 | HP COMPRESSOR^JB73 ONSKID PANEL | 18.A5
AF1201:J | SC | * |  |  | 18.D2 | AF1202:P | HP COMPRESSOR^JB73 ONSKID PANEL | 18.D3
AF1201:V+ | SC | FU0121 | WHT | 14 | 18.D2 | FU0121:LD | HP COMPRESSOR^JB73 ONSKID PANEL | 18.D1
AF1202:COM | SC | AF1202N | WHT | 20 | 18.D3 | AF1203:COM | HP COMPRESSOR^JB73 ONSKID PANEL | 18.D3
AF1202:COM | SC | AU1200N | WHT | 20 | 18.D3 | AU1200:COM | HP COMPRESSOR^JB73 ONSKID PANEL | 18.C1
AF1202:J | SC | * |  |  | 18.D3 | AF1203:P | HP COMPRESSOR^JB73 ONSKID PANEL | 18.D3
AF1202:V+ | SC | AF1202P | WHT | 20 | 18.D3 | AF1203:V+ | HP COMPRESSOR^JB73 ONSKID PANEL | 18.D3
AF1202:V+ | SC | AU1200P | WHT | 20 | 18.D3 | AU1200:V+ | HP COMPRESSOR^JB73 ONSKID PANEL | 18.C1
AF1203:COM | SC | AF1203N | WHT | 20 | 18.D3 | AF1204:COM | HP COMPRESSOR^JB73 ONSKID PANEL | 18.C4
AF1203:J | SC | * |  |  | 18.D3 | AF1204:P | HP COMPRESSOR^JB73 ONSKID PANEL | 18.C4
AF1203:SH | SC | AF1203G | GRN | 14 | 18.D3 | AF1204:SH | HP COMPRESSOR^JB73 ONSKID PANEL | 18.C4
AF1203:SH | SC | AU1200G | GRN | 14 | 18.D3 | AU1200:GND | HP COMPRESSOR^JB73 ONSKID PANEL | 18.C1
AF1203:V+ | SC | AF1203P | WHT | 20 | 18.D3 | AF1204:V+ | HP COMPRESSOR^JB73 ONSKID PANEL | 18.C4
AF1204:COM | SC | AF1204N | WHT | 20 | 18.C4 | AF1205:COM | HP COMPRESSOR^JB73 ONSKID PANEL | 18.C4
AF1204:J | SC | * |  |  | 18.C4 | AF1205:P | HP COMPRESSOR^JB73 ONSKID PANEL | 18.C4
AF1204:SH | SC | AF1204G | GRN | 14 | 18.C4 | AF1205:SH | HP COMPRESSOR^JB73 ONSKID PANEL | 18.C4
AF1204:V+ | SC | AF1204P | WHT | 20 | 18.C4 | AF1205:V+ | HP COMPRESSOR^JB73 ONSKID PANEL | 18.C4
AF1205:COM | SC | AF1205N | WHT | 20 | 18.C4 | AF1206:COM | HP COMPRESSOR^JB73 ONSKID PANEL | 18.D5
AF1205:J | SC | * |  |  | 18.C4 | AF1206:P | HP COMPRESSOR^JB73 ONSKID PANEL | 18.D5
AF1205:SH | SC | AF1205G | GRN | 14 | 18.C4 | AF1206:SH | HP COMPRESSOR^JB73 ONSKID PANEL | 18.D5
AF1205:V+ | SC | AF1205P | WHT | 20 | 18.C4 | AF1206:V+ | HP COMPRESSOR^JB73 ONSKID PANEL | 18.D5
AF1206:COM | SC | AF1206N | WHT | 20 | 18.D5 | AF1207:COM | HP COMPRESSOR^JB73 ONSKID PANEL | 18.B3
AF1206:SH | SC | AF1206G | GRN | 14 | 18.D5 | AF1208:SH | HP COMPRESSOR^JB73 ONSKID PANEL | 18.C4
AF1206:V+ | SC | AF1206P | WHT | 20 | 18.D5 | AF1207:V+ | HP COMPRESSOR^JB73 ONSKID PANEL | 18.B3
AF1207:02 | SC | 120702 | WHT | 20 | 72.A7 | KA4401:14 | HP COMPRESSOR^JB73 ONSKID PANEL | 72.A6
AF1207:18 | SC | 120718 | WHT | 20 | 72.A7 | KA4401:A2 | HP COMPRESSOR^JB73 ONSKID PANEL | 72.A6
AF1207:34 | SC | PS44012 | WHT | 20 | 72.A7 | KA4401:11 | HP COMPRESSOR^JB73 ONSKID PANEL | 72.A6
AF1207:COM | SC | AF1207N | WHT | 20 | 18.B3 | AF1208:COM | HP COMPRESSOR^JB73 ONSKID PANEL | 18.C4
AF1207:J | SC | * |  |  | 18.B3 | AF1208:P | HP COMPRESSOR^JB73 ONSKID PANEL | 18.C4
AF1207:V+ | SC | AF1207P | WHT | 20 | 18.B3 | AF1208:V+ | HP COMPRESSOR^JB73 ONSKID PANEL | 18.C4
AF1208:07 | SC | TE44381 | WHT | 20 | 64.A7 | AF1208:23 | HP COMPRESSOR^JB73 ONSKID PANEL | 64.A7
AF1208:09 | SC | TE44371 | WHT | 20 | 64.B7 | AF1208:25 | HP COMPRESSOR^JB73 ONSKID PANEL | 64.B7
AF1208:11 | SC | TE44181 | WHT | 20 | 64.C7 | AF1208:27 | HP COMPRESSOR^JB73 ONSKID PANEL | 64.C7
AF1208:13 | SC | TE44171 | WHT | 20 | 64.C7 | AF1208:29 | HP COMPRESSOR^JB73 ONSKID PANEL | 64.C7
AF1208:COM | SC | AF1208N | WHT | 20 | 18.C4 | AF1209:COM | HP COMPRESSOR^JB73 ONSKID PANEL | 18.C4
AF1208:SH | SC | AF1208G | GRN | 14 | 18.C4 | AF1209:SH | HP COMPRESSOR^JB73 ONSKID PANEL | 18.C4
AF1208:V+ | SC | AF1208P | WHT | 20 | 18.C4 | AF1209:V+ | HP COMPRESSOR^JB73 ONSKID PANEL | 18.C4
AF1209:07 | SC | TE44141 | WHT | 20 | 63.A7 | AF1209:23 | HP COMPRESSOR^JB73 ONSKID PANEL | 63.A7
AF1209:09 | SC | TE44131 | WHT | 20 | 63.B7 | AF1209:25 | HP COMPRESSOR^JB73 ONSKID PANEL | 63.B7
AF1209:11 | SC | TE44331 | WHT | 20 | 63.C7 | AF1209:27 | HP COMPRESSOR^JB73 ONSKID PANEL | 63.C7
AF1209:13 | SC | TE44341 | WHT | 20 | 63.D7 | AF1209:29 | HP COMPRESSOR^JB73 ONSKID PANEL | 63.D7
AF1209:COM | SC | AF1209N | WHT | 20 | 18.C4 | AF1210:COM | HP COMPRESSOR^JB73 ONSKID PANEL | 18.C5
AF1209:SH | SC | AF1209G | GRN | 14 | 18.C4 | AF1210:SH | HP COMPRESSOR^JB73 ONSKID PANEL | 18.C5
AF1209:V+ | SC | AF1209P | WHT | 20 | 18.C4 | AF1210:V+ | HP COMPRESSOR^JB73 ONSKID PANEL | 18.C5
AF1210:COM | SC | AF1210N | WHT | 20 | 18.C5 | AF1211:COM | HP COMPRESSOR^JB73 ONSKID PANEL | 18.C6
AF1210:SH | SC | AF1210G | GRN | 14 | 18.C5 | AF1211:SH | HP COMPRESSOR^JB73 ONSKID PANEL | 18.C6
AF1210:V+ | SC | AF1210P | WHT | 20 | 18.C5 | AF1211:V+ | HP COMPRESSOR^JB73 ONSKID PANEL | 18.C6
AF1211:COM | SC | AF1211N | WHT | 20 | 18.C6 | AF1212:COM | HP COMPRESSOR^JB73 ONSKID PANEL | 18.C6
AF1211:SH | SC | AF1211G | GRN | 14 | 18.C6 | AF1212:SH | HP COMPRESSOR^JB73 ONSKID PANEL | 18.C6
AF1211:V+ | SC | AF1211P | WHT | 20 | 18.C6 | AF1212:V+ | HP COMPRESSOR^JB73 ONSKID PANEL | 18.C6
AF1212:SH | SC | IEG01303 | GRN | 14 | 18.C6 | IEG0130:3 | HP COMPRESSOR^JB73 ONSKID PANEL | 18.C7
AU1200:COM | SC | 0V | WHT | 14 | 18.C1 | XT0130:4 | HP COMPRESSOR^JB73 ONSKID PANEL | 18.A5
AU1200:V+ | SC | FU0120 | WHT | 14 | 18.C1 | FU0120:LD | HP COMPRESSOR^JB73 ONSKID PANEL | 18.D1
FU0120:LI | SC | FU0130 | WHT | 14 | 18.D1 | FU0131:LI | HP COMPRESSOR^JB73 ONSKID PANEL | 18.C1
FU0120:LI | SC | FU0130 | WHT | 14 | 18.D1 | FU0121:LI | HP COMPRESSOR^JB73 ONSKID PANEL | 18.D1
FU0121:LI | SC | FU0130 | WHT | 14 | 18.D1 | FU0122:LI | HP COMPRESSOR^JB73 ONSKID PANEL | 18.D1
FU0122:LD | SC | FU0122 | WHT | 16 | 18.D1 | XT0121:3 | HP COMPRESSOR^JB73 ONSKID PANEL | 67.A5
FU0130:LD | SC | FU0130 | WHT | 14 | 18.A4 | FU0131:LI | HP COMPRESSOR^JB73 ONSKID PANEL | 18.C1
FU0130:LI | SC | FU0136 | WHT | 14 | 18.A4 | XT0130:1 | HP COMPRESSOR^JB73 ONSKID PANEL | 18.A5
GR0120: | SC | IEG01301 | GRN | 14 | 4.A3 | IEG0130:1 | HP COMPRESSOR^JB73 ONSKID PANEL | 4.A3
GR0124: | SC | IEG01307 | GRN | 14 | 4.A4 | IEG0130:7 | HP COMPRESSOR^JB73 ONSKID PANEL | 4.A3
GR0845: | SC | GR0845 | GRN/YEL | 14 | 4.A3 | FRAME | HP COMPRESSOR^JB73 ONSKID PANEL | 4.A3
IEG0130:4 | SC | IEG01304 | GRN | 14 | 18.C2 | XT0500:2 | HP COMPRESSOR^JB73 ONSKID PANEL | 18.C2
KA0120:A1 | SC | KA0231A1 | WHT | 20 | 18.B5 | XT0130:6 | HP COMPRESSOR^JB73 ONSKID PANEL | 18.B5
KA0120:A2 | SC | 0V | WHT | 14 | 18.B5 | XT0130:7 | HP COMPRESSOR^JB73 ONSKID PANEL | 18.B5
KA4401:11 | SC | PS44012 | WHT | 20 | 72.A6 | XT0121:1 | HP COMPRESSOR^JB73 ONSKID PANEL | 72.A5
KA4401:A1 | SC | PS44013 | WHT | 20 | 72.A6 | XT0121:2 | HP COMPRESSOR^JB73 ONSKID PANEL | 72.A5
XT0121:7 | SC | 0V | WHT | 14 | 67.A5 | XT0130:3 | HP COMPRESSOR^JB73 ONSKID PANEL | 18.A5
XT0130:1 | SC | FU0136 | WHT | 16 | 18.A5 | XT0520:1 | HP COMPRESSOR^JB73 ONSKID PANEL | 18.A5
XT0130:3 | SC | 0V | WHT | 20 | 18.A5 | XT0130:7 | HP COMPRESSOR^JB73 ONSKID PANEL | 18.B5
XT0130:4 | SC | 0V | WHT | 14 | 18.A5 | XT0520:2 | HP COMPRESSOR^JB73 ONSKID PANEL | 18.A5
XT0130:5 | SC | KA0231A1 | WHT | 14 | 18.A5 | XT0130:6 | HP COMPRESSOR^JB73 ONSKID PANEL | 18.B5
XT0520:3 | SC | KA0231A1 | WHT | 14 | 18.A5 | XT0130:5 | HP COMPRESSOR^JB73 ONSKID PANEL | 18.A5
AF0510:L2 | WC0051 | AF0510L2 | ENET | CABLE | 2.B4 | AF0520:L1 | HP COMPRESSOR^JB73 ONSKID PANEL | 2.B5
AF0520:L2 | WC0052 | AF0520L2 | ENET | CABLE | 2.B5 | AU1200:L1 | HP COMPRESSOR^JB73 ONSKID PANEL | 2.B6
AF0510:LBUS | WC8051 | AF0520RBUS | BUS | CABLE | 18.A2 | AF0520:RBUS | HP COMPRESSOR^JB73 ONSKID PANEL | 18.A1
AF1206:J | WC8058 | AF1206J | CABLE | CABLE | 18.D5 | AF1207:P | HP COMPRESSOR^JB73 ONSKID PANEL | 18.B3
AF1202:11 | SC | PS44103 | WHT | 16 | 74.A6 | XT4875:9 | JB75 | 74.A2
AF1202:12 | SC | PS44303 | WHT | 16 | 74.B6 | XT4875:15 | JB75 | 74.B2
AF1202:43 | SC | PS44102 | WHT | 16 | 74.A6 | XT4875:8 | JB75 | 74.A2
AF1202:44 | SC | PS44302 | WHT | 16 | 74.B6 | XT4875:14 | JB75 | 74.B2
XT0121:1 | SC | PS44012 | WHT | 18 | 72.A5 | XT4875:2 | JB75 | 72.A2
XT0121:2 | SC | PS44013 | WHT | 18 | 72.A5 | XT4875:3 | JB75 | 72.A2
XT0130:1 | SC | FU0136 | WHT | 14 | 18.A5 | XT0110:1 | TURBINE PANEL B JB70 | 17.A5
XT0130:2 | SC | 0V | WHT | 14 | 18.A5 | XT0110:2 | TURBINE PANEL B JB70 | 17.A5
XT0130:5 | SC | KA0231A1 | WHT | 20 | 18.A5 | XT0110:3 | TURBINE PANEL B JB70 | 17.B5
AF0510:L1 | WC0045 | AF0450L2 | ENET | CABLE | 2.B4 | AF0450:L2 | TURBINE PANEL B JB70 | 2.A5
SolarTools ver. 24.0.84.24712 (Jul 31, 2025)
Report date: 3/3/2026 11:49 AM

## LOOSESHIP PANEL
LOOSESHIP PANEL
Project # | J0630
Project Name | TC TUSCARORA SHOETREE CR
Revision | A.3
Controls DE | G.JP
Phone:
Controls ME
Phone:
From | [5 empty] | To
Device ID | Cable (W) Conductor (SC) Jumper Clip (JC) | Wire No. | Wire ID | Gauge/Size | Page/Zone | Device ID | Location | Page/Zone
XT0562:1 | JC | 0V | CLIP | --- | 20.B2 | XT0562:2 | LOOSESHIP PANEL | 20.C2
AF0201:COM | SC | AU0200N | WHT | 16 | 20.A4 | AU0200:COM | LOOSESHIP PANEL | 20.A3
AF0201:J | SC | * |  |  | 20.A4 | AF0202:P | LOOSESHIP PANEL | 20.A5
AF0201:SHLD | SC | AF0201V+L | WHT | 20 | 20.C5 | AF0201:V+L | LOOSESHIP PANEL | 20.C5
AF0201:V+ | SC | AU0200P | WHT | 16 | 20.A4 | AU0200:V+ | LOOSESHIP PANEL | 20.A3
AF0202:00 | SC | 020200 | WHT | 20 | 59.A7 | KA3103:A1 | LOOSESHIP PANEL | 59.A5
AF0202:01 | SC | 020201 | WHT | 20 | 59.C7 | KA3104:A1 | LOOSESHIP PANEL | 59.C5
AF0202:02 | SC | KA32201 | WHT | 20 | 57.C7 | KA3220:A1 | LOOSESHIP PANEL | 57.C5
AF0202:32 | SC | 020232 | WHT | 20 | 59.A7 | KA3103:A2 | LOOSESHIP PANEL | 59.A5
AF0202:33 | SC | 020233 | WHT | 20 | 59.C7 | KA3104:A2 | LOOSESHIP PANEL | 59.C5
AF0202:34 | SC | KA32202 | WHT | 20 | 57.C7 | KA3220:A2 | LOOSESHIP PANEL | 57.C5
AF0202:COM | SC | 0V | WHT | 14 | 20.A5 | XT0562:1 | LOOSESHIP PANEL | 20.B2
AF0202:COML | SC | AF0202COML | WHT | 20 | 20.C6 | AF0202:SHLD | LOOSESHIP PANEL | 20.C6
AF0202:V+ | SC | FU0201 | WHT | 14 | 20.A5 | FU0201:LD | LOOSESHIP PANEL | 20.B3
AU0200:COM | SC | 0V | WHT | 14 | 20.A3 | XT0562:1 | LOOSESHIP PANEL | 20.B2
AU0200:GND | SC | AU0200G | GRN | 14 | 20.A3 | XT0200:1 | LOOSESHIP PANEL | 20.B4
AU0200:V+ | SC | FU0200 | WHT | 14 | 20.A3 | FU0200:LD | LOOSESHIP PANEL | 20.A3
FU0200:LI | SC | FU0560LD | WHT | 12 | 20.A3 | XT0561:1 | LOOSESHIP PANEL | 20.A2
FU0200:LI | SC | FU0560LD | WHT | 14 | 20.A3 | FU0201:LI | LOOSESHIP PANEL | 20.B3
FU0201:LI | SC | FU0560LD | WHT | 14 | 20.B3 | FU0273:LI | LOOSESHIP PANEL | 20.C3
FU0560:LD | SC | FU0560LD | WHT | 12 | 20.B2 | XT0561:1 | LOOSESHIP PANEL | 20.A2
GR0200: | SC | IEG02002 | GRN | 14 | 4.B3 | IEG0200:2 | LOOSESHIP PANEL | 4.B3
IEG0200:1 | SC | IEG02001 | GRN | 14 | 20.B5 | XT0200:2 | LOOSESHIP PANEL | 20.B4
SolarTools ver. 24.0.84.24712 (Jul 31, 2025)
Report date: 3/3/2026 11:49 AM

## TURBINE BOX^DOOR^JB70
TURBINE BOX^DOOR^JB70
Project # | J0630
Project Name | TC TUSCARORA SHOETREE CR
Revision | A.3
Controls DE | G.JP
Phone:
Controls ME
Phone:
From | [5 empty] | To
Device ID | Cable (W) Conductor (SC) Jumper Clip (JC) | Wire No. | Wire ID | Gauge/Size | Page/Zone | Device ID | Location | Page/Zone
AT1100:POS | SC | FU1100 | WHT | 14 | 24.D3 | FU1100:LD | TURBINE BOX^LEFT RAIL^JB70 | 24.D3
AT1100:L1 | WC0101 | BA1100DEVICE | ENET | CABLE | 24.D3 | BA1100:DEVICE | TURBINE BOX^LEFT RAIL^JB70 | 24.D1
AT1100:GND | SC | PEG01304 | GRN/YEL | 14 | 24.D3 | PEG0130:4 | TURBINE PANEL A JB70 | 24.D6
AT1100:NEG | SC | 0V | WHT | 16 | 24.D3 | XT0134:3 | TURBINE PANEL A JB70 | 12.B3
SA0473:B-B1 | SC | SA0473B-B1 | WHT | 20 | 23.D1 | AF0087:06 | TURBINE PANEL A JB70 | 23.D7
SA0473:B-B2 | SC | SA0473B-B2 | WHT | 20 | 23.D1 | AF0087:38 | TURBINE PANEL A JB70 | 23.D7
SA0473:W-B1 | SC | SA0473W-B1 | WHT | 20 | 23.C1 | AF0087:05 | TURBINE PANEL A JB70 | 23.C7
SA0473:W-B2 | SC | SA0473W-B2 | WHT | 20 | 23.C1 | AF0087:37 | TURBINE PANEL A JB70 | 23.C7
SA0474:B1-13 | SC | SA0474B113 | WHT | 20 | 23.C1 | AF0087:45 | TURBINE PANEL A JB70 | 23.C7
SA0474:B1-14 | SC | SA0474B114 | WHT | 20 | 23.C1 | AF0087:13 | TURBINE PANEL A JB70 | 23.C7
SA0474:B2-13 | SC | SA0474B213 | WHT | 20 | 23.C1 | AF0087:44 | TURBINE PANEL A JB70 | 23.C7
SA0474:B2-14 | SC | SA0474B214 | WHT | 20 | 23.C1 | AF0087:12 | TURBINE PANEL A JB70 | 23.C7
HA0472:BLK-1 | WC5072 | HA04721 | 1 | 18 | 22.C1 | AF0092:28 | TURBINE PANEL A JB70 | 22.C7
HA0472:BLK-2 | WC5072 | HA04722 | 2 | 18 | 22.C1 | AF0092:12 | TURBINE PANEL A JB70 | 22.C7
SA0473:B-A3 | SC | SA0473B-A3 | WHT | 20 | 23.D1 | AF0063:08 | TURBINE PANEL B JB70 | 23.D7
SA0473:B-A4 | SC | SA0473B-A4 | WHT | 20 | 23.D1 | AF0063:40 | TURBINE PANEL B JB70 | 23.D7
Report date: 3/3/2026 11:49 AM |  |  |  |  | SolarTools ver. 24.0.84.24712 (Jul 31, 2025)

## TURBINE BOX^LEFT RAIL^JB70
TURBINE BOX^LEFT RAIL^JB70
Project # | J0630
Project Name | TC TUSCARORA SHOETREE CR
Revision | A.3
Controls DE | G.JP
Phone:
Controls ME
Phone:
From | [5 empty] | To
Device ID | Cable (W) Conductor (SC) Jumper Clip (JC) | Wire No. | Wire ID | Gauge/Size | Page/Zone | Device ID | Location | Page/Zone
BA1100:POS | SC | FU1101LD | WHT | 16 | 24.D1 | FU1101:LD | TURBINE BOX^LEFT RAIL^JB70 | 24.C2
FU0291:LD | SC | FU0291 | WHT | 16 | 24.C4 | UV0291:24V(+) | TURBINE BOX^LEFT RAIL^JB70 | 24.C5
GR1101: | SC | GR1101 | GRN/YEL | 14 | 3.A6 | FRAME | TURBINE BOX^LEFT RAIL^JB70 | 3.A5
PC0470:INP_A | SC | 009312 | WHT | 20 | 24.B5 | PC0470:INP_B | TURBINE BOX^LEFT RAIL^JB70 | 24.B5
UV0291:OUT1(-) | SC | UV0291N | WHT | 16 | 24.C5 | XT0292:1 | TURBINE BOX^LEFT RAIL^JB70 | 24.C6
UV0291:OUT1(+) | SC | UV0291P | WHT | 16 | 24.C5 | XT0291:1 | TURBINE BOX^LEFT RAIL^JB70 | 24.C6
XT0137:1 | SC | ESTOPA | WHT | 20 | 23.B5 | SB0472:B1-11 | JB70 | 23.B1
XT0137:2 | SC | ESTOP | WHT | 20 | 23.B5 | SB0472:B1-12 | JB70 | 23.B1
XT0137:3 | SC | SH047111 | WHT | 20 | 22.A5 | SH0471:11 | JB70 | 22.A1
XT0137:4 | SC | SH047112 | WHT | 20 | 22.A5 | SH0471:12 | JB70 | 22.A1
XT0137:5 | SC | SH047013 | WHT | 20 | 22.B5 | SH0470:13 | JB70 | 22.B1
XT0137:6 | SC | SH047014 | WHT | 20 | 22.B5 | SH0470:14 | JB70 | 22.B1
FU1100:LD | SC | FU1100 | WHT | 14 | 24.D3 | AT1100:POS | TURBINE BOX^DOOR^JB70 | 24.D3
BA1100:DEVICE | WC0101 | BA1100DEVICE | ENET | CABLE | 24.D1 | AT1100:L1 | TURBINE BOX^DOOR^JB70 | 24.D3
FU0291:LI | SC | FU0136 | WHT | 14 | 24.C4 | XT0138:3 | TURBINE PANEL A JB70 | 12.A3
FU1100:LI | SC | FU0136 | WHT | 16 | 24.D3 | XT0138:3 | TURBINE PANEL A JB70 | 12.A3
PC0470:+PWR | SC | 009344 | WHT | 20 | 24.B5 | AF0093:44 | TURBINE PANEL A JB70 | 24.B7
PC0470:INP_A | SC | 009312 | WHT | 20 | 24.B5 | AF0093:12 | TURBINE PANEL A JB70 | 24.B7
PC0470:-PWR | SC | 009328 | WHT | 20 | 24.B5 | AF0093:28 | TURBINE PANEL A JB70 | 24.B7
UV0291:24V(-) | SC | 0V | WHT | 16 | 24.C5 | XT0134:3 | TURBINE PANEL A JB70 | 12.B3
XT0137:1 | SC | ESTOPA | WHT | 20 | 23.B5 | XT0240:3 | TURBINE PANEL B JB70 | 14.A3
XT0137:2 | SC | ESTOP | WHT | 20 | 23.B5 | XT0240:4 | TURBINE PANEL B JB70 | 14.A3
SolarTools ver. 24.0.84.24712 (Jul 31, 2025)
Report date: 3/3/2026 11:49 AM

## TURBINE BOX^RIGHT RAIL^JB70
TURBINE BOX^RIGHT RAIL^JB70
Project # | J0630
Project Name | TC TUSCARORA SHOETREE CR
Revision | A.3
Controls DE | G.JP
Phone:
Controls ME
Phone:
From | [5 empty] | To
Device ID | Cable (W) Conductor (SC) Jumper Clip (JC) | Wire No. | Wire ID | Gauge/Size | Page/Zone | Device ID | Location | Page/Zone
GR1100: | SC | IEG023014 | GRN | 14 | 3.A5 | IEG0230:14 | TURBINE PANEL B JB70 | 3.A4
Report date: 3/3/2026 11:49 AM |  |  |  |  | SolarTools ver. 24.0.84.24712 (Jul 31, 2025)

## TURBINE PANEL A JB70
TURBINE PANEL A JB70
TURBINE PANEL A^JB70
Project # | J0630
Project Name | TC TUSCARORA SHOETREE CR
Revision | A.3
Controls DE | G.JP
Phone:
Controls ME
Phone:
From | [5 empty] | To
Device ID | Cable (W) Conductor (SC) Jumper Clip (JC) | Wire No. | Wire ID | Gauge/Size | Page/Zone | Device ID | Location | Page/Zone
XT0011:3 | JC | FU0022 | CLIP | --- | 11.C3 | XT0011:2 | TURBINE PANEL A JB70 | 11.C3
XT0080:1 | JC | 0V | CLIP | --- | 9.D1 | XT0080:2 | TURBINE PANEL A JB70 | 9.D1
XT0080:2 | JC | 0V | CLIP | --- | 9.D1 | XT0080:3 | TURBINE PANEL A JB70 | 9.D1
XT0090:1 | JC | 0V | CLIP | --- | 9.B1 | XT0090:2 | TURBINE PANEL A JB70 | 9.B1
XT0134:1 | JC | 0V | CLIP | --- | 12.B3 | XT0134:2 | TURBINE PANEL A JB70 | 12.B3
XT0134:2 | JC | 0V | CLIP | --- | 12.B3 | XT0134:3 | TURBINE PANEL A JB70 | 12.B3
XT0134:3 | JC | 0V | CLIP | --- | 12.B3 | XT0134:4 | TURBINE PANEL A JB70 | 12.B3
XT0135:1 | JC | 0V | CLIP | --- | 12.B4 | XT0135:2 | TURBINE PANEL A JB70 | 12.B4
XT0135:2 | JC | 0V | CLIP | --- | 12.B4 | XT0135:3 | TURBINE PANEL A JB70 | 12.B4
XT0138:1 | JC | FU0136 | CLIP | --- | 12.A3 | XT0138:2 | TURBINE PANEL A JB70 | 12.A3
XT0138:2 | JC | FU0136 | CLIP | --- | 12.A3 | XT0138:3 | TURBINE PANEL A JB70 | 12.A3
XT0138:3 | JC | FU0136 | CLIP | --- | 12.A3 | XT0138:4 | TURBINE PANEL A JB70 | 12.B3
XT0139:1 | JC | FU0137 | CLIP | --- | 12.A4 | XT0139:2 | TURBINE PANEL A JB70 | 12.A4
XT0139:2 | JC | FU0137 | CLIP | --- | 12.A4 | XT0139:3 | TURBINE PANEL A JB70 | 12.B4
AF0081:07 | SC | ESDR124 | WHT | 20 | 25.C7 | XT7512:2 | TURBINE PANEL A JB70 | 25.C6
AF0081:10 | SC | S112-BNC2 | WHT | 20 | 25.B7 | XT7512:4 | TURBINE PANEL A JB70 | 25.B6
AF0081:39 | SC | ESDR121 | WHT | 20 | 25.C7 | XT7512:1 | TURBINE PANEL A JB70 | 25.C6
AF0081:42 | SC | S112-BC2 | WHT | 20 | 25.B7 | XT7512:3 | TURBINE PANEL A JB70 | 25.B6
AF0081:COM | SC | AU0080N | WHT | 20 | 9.C2 | AU0080:COM | TURBINE PANEL A JB70 | 9.C2
AF0081:V+ | SC | AU0080P | WHT | 20 | 9.C2 | AU0080:V+ | TURBINE PANEL A JB70 | 9.C2
AF0082:COM | SC | AF0082N | WHT | 16 | 9.D3 | AF0083:COM | TURBINE PANEL A JB70 | 9.D3
AF0082:COM | SC | 0V | WHT | 16 | 9.D3 | XT0080:2 | TURBINE PANEL A JB70 | 9.D1
AF0082:V+ | SC | FU0081 | WHT | 14 | 9.D3 | FU0081:LD | TURBINE PANEL A JB70 | 9.D1
AF0082:V+ | SC | AF0082P | WHT | 16 | 9.D3 | AF0083:V+ | TURBINE PANEL A JB70 | 9.D3
AF0083:01 | SC | TE12701 | WHT | 20 | 48.C7 | AF0083:17 | TURBINE PANEL A JB70 | 48.C7
AF0083:03 | SC | TE12601 | WHT | 20 | 48.B7 | AF0083:19 | TURBINE PANEL A JB70 | 48.B7
AF0083:COM | SC | AF0083N | WHT | 16 | 9.D3 | AF0084:COM | TURBINE PANEL A JB70 | 9.D4
AF0083:SH | SC | AF0083G | GRN | 14 | 9.D3 | AF0084:SH | TURBINE PANEL A JB70 | 9.D4
AF0083:SH | SC | AU0080G | GRN | 14 | 9.D3 | AU0080:GND | TURBINE PANEL A JB70 | 9.C2
AF0083:V+ | SC | AF0083P | WHT | 16 | 9.D3 | AF0084:V+ | TURBINE PANEL A JB70 | 9.D4
AF0084:COM | SC | AF0084N | WHT | 20 | 9.D4 | AF0085:COM | TURBINE PANEL A JB70 | 9.D5
AF0084:SH | SC | AF0084G | GRN | 14 | 9.D4 | AF0085:SH | TURBINE PANEL A JB70 | 9.D5
AF0084:V+ | SC | AF0084P | WHT | 20 | 9.D4 | AF0085:V+ | TURBINE PANEL A JB70 | 9.D5
AF0085:COM | SC | AF0085N | WHT | 20 | 9.D5 | AF0086:COM | TURBINE PANEL A JB70 | 9.D5
AF0085:SH | SC | AF0085G | GRN | 14 | 9.D5 | AF0086:SH | TURBINE PANEL A JB70 | 9.D5
AF0085:V+ | SC | AF0085P | WHT | 20 | 9.D5 | AF0086:V+ | TURBINE PANEL A JB70 | 9.D5
AF0086:COM | SC | AF0086N | WHT | 20 | 9.D5 | AF0087:COM | TURBINE PANEL A JB70 | 9.D6
AF0086:V+ | SC | AF0086P | WHT | 20 | 9.D5 | AF0087:V+ | TURBINE PANEL A JB70 | 9.D6
AF0091:09 | SC | UJ0131OK2 | WHT | 20 | 11.B7 | UJ0131:OK2 | TURBINE PANEL A JB70 | 11.B4
AF0091:41 | SC | UJ0131OK1 | WHT | 20 | 11.B7 | UJ0131:OK1 | TURBINE PANEL A JB70 | 11.B4
AF0091:COM | SC | AF0091N | WHT | 14 | 9.B2 | AF0094:COM | TURBINE PANEL A JB70 | 9.B4
AF0091:COM | SC | AU0090N | WHT | 20 | 9.B2 | AU0090:COM | TURBINE PANEL A JB70 | 9.A2
AF0091:V+ | SC | AF0091P | WHT | 20 | 9.B2 | AF0094:V+ | TURBINE PANEL A JB70 | 9.B4
AF0091:V+ | SC | AU0090P | WHT | 20 | 9.B2 | AU0090:V+ | TURBINE PANEL A JB70 | 9.A2
AF0092:00 | SC | AF009200 | WHT | 20 | 32.D7 | KA0270:A1 | TURBINE PANEL A JB70 | 32.D6
AF0092:04 | SC | 009204 | WHT | 20 | 27.A6 | KA2160:A1 | TURBINE PANEL A JB70 | 27.A5
AF0092:07 | SC | 009207 | WHT | 20 | 27.A6 | KA2161:A1 | TURBINE PANEL A JB70 | 27.B5
AF0092:16 | SC | AF009216 | WHT | 20 | 32.D7 | KA0270:A2 | TURBINE PANEL A JB70 | 32.D6
AF0092:20 | SC | 009220 | WHT | 20 | 27.A6 | KA2160:A2 | TURBINE PANEL A JB70 | 27.A5
AF0092:23 | SC | 009223 | WHT | 20 | 27.A6 | KA2161:A2 | TURBINE PANEL A JB70 | 27.B5
AF0092:COM | SC | 0V | WHT | 16 | 9.B3 | XT0090:2 | TURBINE PANEL A JB70 | 9.B1
AF0092:V+ | SC | FU0091 | WHT | 14 | 9.B3 | FU0091:LD | TURBINE PANEL A JB70 | 9.B1
AF0093:COM | SC | 0V | WHT | 14 | 9.B3 | XT0090:2 | TURBINE PANEL A JB70 | 9.B1
AF0093:V+ | SC | FU0092 | WHT | 14 | 9.B3 | FU0092:LD | TURBINE PANEL A JB70 | 9.B1
AF0094:00 | SC | 009400 | WHT | 20 | 11.C7 | XT0085:2 | TURBINE PANEL A JB70 | 11.C6
AF0094:01 | SC | 0V | WHT | 20 | 11.C7 | XT0085:3 | TURBINE PANEL A JB70 | 11.C6
AF0094:04 | SC | UJ0131VIN | WHT | 14 | 11.A7 | UJ0131:VIN | TURBINE PANEL A JB70 | 11.B4
AF0094:05 | SC | 0V | WHT | 16 | 11.A7 | XT0135:3 | TURBINE PANEL A JB70 | 12.B4
AF0094:06 | SC | UJ0131IOUT | WHT | 14 | 11.B7 | UJ0131:IOUT | TURBINE PANEL A JB70 | 11.B4
AF0094:07 | SC | 0V | WHT | 16 | 11.B7 | XT0135:3 | TURBINE PANEL A JB70 | 12.B4
AF0094:COM | SC | AF0094N | WHT | 14 | 9.B4 | AF0096:COM | TURBINE PANEL A JB70 | 9.B5
AF0094:SH | SC | AF0094G | GRN | 14 | 9.B4 | AF0096:SH | TURBINE PANEL A JB70 | 9.B5
AF0094:SH | SC | AU0090G | GRN | 14 | 9.B4 | AU0090:GND | TURBINE PANEL A JB70 | 9.A2
AF0094:V+ | SC | AF0094P | WHT | 20 | 9.B4 | AF0096:V+ | TURBINE PANEL A JB70 | 9.B5
AF0095:02 | SC | 009502 | WHT | 20 | 44.A7 | KA0221:14 | TURBINE PANEL A JB70 | 44.A6
AF0095:COM | SC | 0V | WHT | 14 | 9.B5 | XT0090:2 | TURBINE PANEL A JB70 | 9.B1
AF0095:V+ | SC | FU0093 | WHT | 14 | 9.B5 | FU0093:LD | TURBINE PANEL A JB70 | 9.B1
XT7512:2 | SC | JP2 | VIO | 20 | 25.C6 | XT7512:1 | TURBINE PANEL A JB70 | 25.C6
XT7512:4 | SC | JP6 | VIO | 20 | 25.B6 | XT7512:3 | TURBINE PANEL A JB70 | 25.B6
AR0600:IE1 | SC | UV0600G | GRN | 14 | 7.A1 | UV0600:GND | TURBINE PANEL A JB70 | 7.B2
AU0080:COM | SC | 0V | WHT | 16 | 9.C2 | XT0080:1 | TURBINE PANEL A JB70 | 9.D1
AU0080:V+ | SC | FU0080 | WHT | 14 | 9.C2 | FU0080:LD | TURBINE PANEL A JB70 | 9.D1
AU0090:COM | SC | 0V | WHT | 16 | 9.A2 | XT0090:1 | TURBINE PANEL A JB70 | 9.B1
AU0090:V+ | SC | FU0090 | WHT | 14 | 9.A2 | FU0090:LD | TURBINE PANEL A JB70 | 9.B1
FU0010:LD | SC | FU0010 | WHT | 14 | 12.A5 | UV0600:(+) | TURBINE PANEL A JB70 | 7.B2
FU0010:LI | SC | FU0137 | WHT | 14 | 12.A5 | XT0139:1 | TURBINE PANEL A JB70 | 12.A4
FU0011:LD | SC | UJ0131P | WHT | 12 | 11.B3 | UJ0131:+ | TURBINE PANEL A JB70 | 11.B4
FU0012:LI | SC | FU0021 | --- | BUS | 11.B3 | FU0013:LI | TURBINE PANEL A JB70 | 11.B3
FU0012:LI | SC | FU0021 | --- | BUS | 11.B3 | XT0014:1 | TURBINE PANEL A JB70 | 11.B2
FU0013:LI | SC | FU0021 | --- | BUS | 11.B3 | FU0014:LI | TURBINE PANEL A JB70 | 11.C3
FU0014:LI | SC | FU0021 | --- | BUS | 11.C3 | FU0015:LI | TURBINE PANEL A JB70 | 11.C3
FU0020:LD | SC | UJ0131N | WHT | 12 | 11.B3 | UJ0131:- | TURBINE PANEL A JB70 | 11.B4
FU0021:LD | SC | FU0021 | WHT | 14 | 11.B2 | XT0014:1 | TURBINE PANEL A JB70 | 11.B2
FU0022:LD | SC | FU0022 | WHT | 14 | 11.B2 | XT0011:3 | TURBINE PANEL A JB70 | 11.C3
FU0080:LI | SC | FU0137 | WHT | 14 | 9.D1 | FU0081:LI | TURBINE PANEL A JB70 | 9.D1
FU0080:LI | SC | FU0137 | WHT | 14 | 9.D1 | XT0139:2 | TURBINE PANEL A JB70 | 12.A4
FU0081:LI | SC | FU0137 | WHT | 14 | 9.D1 | FU0082:LI | TURBINE PANEL A JB70 | 9.D1
FU0090:LI | SC | FU0137 | WHT | 14 | 9.B1 | XT0139:2 | TURBINE PANEL A JB70 | 12.A4
FU0090:LI | SC | FU0137 | WHT | 14 | 9.B1 | FU0091:LI | TURBINE PANEL A JB70 | 9.B1
FU0091:LI | SC | FU0137 | WHT | 14 | 9.B1 | FU0092:LI | TURBINE PANEL A JB70 | 9.B1
FU0092:LI | SC | FU0137 | WHT | 14 | 9.B1 | FU0093:LI | TURBINE PANEL A JB70 | 9.B1
FU0136:LD | SC | FU0136 | WHT | 10 | 12.A3 | XT0138:1 | TURBINE PANEL A JB70 | 12.A3
FU0136:LI | SC | 24V | WHT | 12 | 12.A3 | UJ0131:OUT(+) | TURBINE PANEL A JB70 | 11.B4
FU0137:LD | SC | FU0137 | WHT | 14 | 12.A4 | XT0139:1 | TURBINE PANEL A JB70 | 12.A4
FU0137:LI | SC | FU0136 | WHT | 16 | 12.A4 | XT0138:1 | TURBINE PANEL A JB70 | 12.A3
FU0139:LI | SC | FU0137 | WHT | 14 | 12.A5 | XT0139:1 | TURBINE PANEL A JB70 | 12.A4
FU0211:LI | SC | FU0137 | WHT | 12 | 12.B4 | XT0139:3 | TURBINE PANEL A JB70 | 12.B4
GR0131: | SC | GR0131 | GRN/YEL | 14 | 3.A3 | FRAME | TURBINE PANEL A JB70 | 3.A3
GR0132: | SC | GR0132 | GRN/YEL | 14 | 3.A3 | FRAME | TURBINE PANEL A JB70 | 3.A3
KA0135:11 | SC | KM3150EN | RED | 16 | 54.A6 | XT0150:2 | TURBINE PANEL A JB70 | 54.A6
KA0135:12 | SC | KM3150EP | RED | 16 | 54.A6 | XT0150:1 | TURBINE PANEL A JB70 | 54.A6
UJ0131:G | SC | UJ0131G | GRN/YEL | 12 | 11.B4 | FRAME | TURBINE PANEL A JB70 | 11.B4
UJ0131:OUT(-) | SC | 0V | WHT | 12 | 11.B4 | XT0134:1 | TURBINE PANEL A JB70 | 12.B3
UV0600:(-) | SC | 0V | WHT | 14 | 7.B2 | XT0135:1 | TURBINE PANEL A JB70 | 12.B4
XT0085:1 | SC | FU0137 | WHT | 14 | 11.C6 | XT0139:3 | TURBINE PANEL A JB70 | 12.B4
XT0085:3 | SC | 0V | WHT | 16 | 11.C6 | XT0135:3 | TURBINE PANEL A JB70 | 12.B4
XT0090:1 | SC | 0V | WHT | 16 | 9.B1 | XT0135:2 | TURBINE PANEL A JB70 | 12.B4
XT0135:1 | SC | 0V | WHT | 16 | 12.B4 | XT0134:1 | TURBINE PANEL A JB70 | 12.B3
XT0135:2 | SC | 0V | WHT | 16 | 12.B4 | XT0080:1 | TURBINE PANEL A JB70 | 9.D1
AP0602:L2 | WC0001 | AP0602L2 | ENET | CABLE | 2.A2 | AP0603:L1 | TURBINE PANEL A JB70 | 2.A3
AP0603:L2 | WC0003 | AP0603L2 | ENET | CABLE | 2.A3 | AU0090:L1 | TURBINE PANEL A JB70 | 2.A4
AU0080:L1 | WC0009 | AU0090L2 | ENET | CABLE | 2.A4 | AU0090:L2 | TURBINE PANEL A JB70 | 2.A4
AF0086:12 | WC4563 | FT21082 | BLK | 20 | 46.C7 | XT0050:2 | TURBINE PANEL A JB70 | 46.C5
AF0086:60 | WC4563 | FT2108S | SH | 20 | 46.C7 | XT0050:3 | TURBINE PANEL A JB70 | 46.C5
AF0081:04 | SC | SB047222 | WHT | 20 | 23.B7 | SB0472:B2-12 | JB70 | 23.B1
AF0081:36 | SC | SB047221 | WHT | 20 | 23.B7 | SB0472:B2-11 | JB70 | 23.B1
AF0087:00 | SC | SH047114 | WHT | 20 | 22.A7 | SH0471:14 | JB70 | 22.A1
AF0087:01 | SC | SH047012 | WHT | 20 | 22.B7 | SH0470:12 | JB70 | 22.B1
AF0087:02 | SC | SB047112 | WHT | 20 | 22.D7 | SB0471:12 | JB70 | 22.D1
AF0087:03 | SC | SB047314 | WHT | 20 | 22.D7 | SB0473:14 | JB70 | 22.D1
AF0087:04 | SC | SB047424 | WHT | 20 | 23.A7 | SB0474:14 | JB70 | 23.A1
AF0087:07 | SC | SA047114 | WHT | 20 | 23.A7 | SA0471:B2-14 | JB70 | 23.A1
AF0087:08 | SC | SA047124 | WHT | 20 | 23.B7 | SA0471:B1-14 | JB70 | 23.B1
AF0087:32 | SC | SH047113 | WHT | 20 | 22.A7 | SH0471:13 | JB70 | 22.A1
AF0087:33 | SC | SH047011 | WHT | 20 | 22.B7 | SH0470:11 | JB70 | 22.B1
AF0087:34 | SC | SB047111 | WHT | 20 | 22.D7 | SB0471:11 | JB70 | 22.D1
AF0087:35 | SC | SB047313 | WHT | 20 | 22.D7 | SB0473:13 | JB70 | 22.D1
AF0087:36 | SC | SB047423 | WHT | 20 | 23.A7 | SB0474:13 | JB70 | 23.A1
AF0087:39 | SC | SA047113 | WHT | 20 | 23.A7 | SA0471:B2-13 | JB70 | 23.A1
AF0087:40 | SC | SA047123 | WHT | 20 | 23.B7 | SA0471:B1-13 | JB70 | 23.B1
AF0093:06 | SC | SH0470X2 | WHT | 20 | 22.B7 | SH0470:X2 | JB70 | 22.B1
AF0093:15 | SC | SH0471X2 | WHT | 20 | 22.A7 | SH0471:X2 | JB70 | 22.A1
AF0093:22 | SC | SH0470X1 | WHT | 20 | 22.B7 | SH0470:X1 | JB70 | 22.B1
AF0093:31 | SC | SH0471X1 | WHT | 20 | 22.A7 | SH0471:X1 | JB70 | 22.A1
AF0087:05 | SC | SA0473W-B1 | WHT | 20 | 23.C7 | SA0473:W-B1 | TURBINE BOX^DOOR^JB70 | 23.C1
AF0087:06 | SC | SA0473B-B1 | WHT | 20 | 23.D7 | SA0473:B-B1 | TURBINE BOX^DOOR^JB70 | 23.D1
AF0087:12 | SC | SA0474B214 | WHT | 20 | 23.C7 | SA0474:B2-14 | TURBINE BOX^DOOR^JB70 | 23.C1
AF0087:13 | SC | SA0474B114 | WHT | 20 | 23.C7 | SA0474:B1-14 | TURBINE BOX^DOOR^JB70 | 23.C1
AF0087:37 | SC | SA0473W-B2 | WHT | 20 | 23.C7 | SA0473:W-B2 | TURBINE BOX^DOOR^JB70 | 23.C1
AF0087:38 | SC | SA0473B-B2 | WHT | 20 | 23.D7 | SA0473:B-B2 | TURBINE BOX^DOOR^JB70 | 23.D1
AF0087:44 | SC | SA0474B213 | WHT | 20 | 23.C7 | SA0474:B2-13 | TURBINE BOX^DOOR^JB70 | 23.C1
AF0087:45 | SC | SA0474B113 | WHT | 20 | 23.C7 | SA0474:B1-13 | TURBINE BOX^DOOR^JB70 | 23.C1
PEG0130:4 | SC | PEG01304 | GRN/YEL | 14 | 24.D6 | AT1100:GND | TURBINE BOX^DOOR^JB70 | 24.D3
XT0134:3 | SC | 0V | WHT | 16 | 12.B3 | AT1100:NEG | TURBINE BOX^DOOR^JB70 | 24.D3
AF0092:28 | WC5072 | HA04721 | 1 | 18 | 22.C7 | HA0472:BLK-1 | TURBINE BOX^DOOR^JB70 | 22.C1
AF0092:12 | WC5072 | HA04722 | 2 | 18 | 22.C7 | HA0472:BLK-2 | TURBINE BOX^DOOR^JB70 | 22.C1
AF0093:12 | SC | 009312 | WHT | 20 | 24.B7 | PC0470:INP_A | TURBINE BOX^LEFT RAIL^JB70 | 24.B5
AF0093:28 | SC | 009328 | WHT | 20 | 24.B7 | PC0470:-PWR | TURBINE BOX^LEFT RAIL^JB70 | 24.B5
AF0093:44 | SC | 009344 | WHT | 20 | 24.B7 | PC0470:+PWR | TURBINE BOX^LEFT RAIL^JB70 | 24.B5
XT0134:3 | SC | 0V | WHT | 16 | 12.B3 | UV0291:24V(-) | TURBINE BOX^LEFT RAIL^JB70 | 24.C5
XT0138:3 | SC | FU0136 | WHT | 14 | 12.A3 | FU0291:LI | TURBINE BOX^LEFT RAIL^JB70 | 24.C4
XT0138:3 | SC | FU0136 | WHT | 16 | 12.A3 | FU1100:LI | TURBINE BOX^LEFT RAIL^JB70 | 24.D3
AF0081:00 | SC | UA1200J21 | WHT | 20 | 14.A7 | KA0241:11 | TURBINE PANEL B JB70 | 14.A5
AF0081:01 | SC | KA024314 | WHT | 20 | 14.B7 | KA0243:14 | TURBINE PANEL B JB70 | 14.B6
AF0081:02 | SC | KA024524 | WHT | 20 | 14.B7 | KA0245:24 | TURBINE PANEL B JB70 | 14.B6
AF0081:03 | SC | 008103 | WHT | 20 | 15.C7 | KA0130:14 | TURBINE PANEL B JB70 | 15.D6
AF0081:08 | SC | KA024214 | WHT | 20 | 14.C7 | KA0242:14 | TURBINE PANEL B JB70 | 14.C6
AF0081:09 | SC | KA023924 | WHT | 20 | 14.A7 | KA0239:24 | TURBINE PANEL B JB70 | 14.B6
AF0081:19 | SC | UA1200J27 | WHT | 20 | 15.C7 | UA1200:J2-7 | TURBINE PANEL B JB70 | 15.B3
AF0081:33 | SC | KA024311 | WHT | 20 | 14.B7 | KA0243:11 | TURBINE PANEL B JB70 | 14.B6
AF0081:34 | SC | KA024521 | WHT | 20 | 14.B7 | KA0245:21 | TURBINE PANEL B JB70 | 14.B6
AF0081:35 | SC | 008135 | WHT | 20 | 15.C7 | KA0130:A1 | TURBINE PANEL B JB70 | 15.C5
AF0081:41 | SC | KA023921 | WHT | 20 | 14.A7 | KA0239:21 | TURBINE PANEL B JB70 | 14.B6
AF0086:SH | SC | IEG02302 | GRN | 14 | 9.D5 | IEG0230:2 | TURBINE PANEL B JB70 | 9.D5
AF0087:09 | SC | KA013112 | WHT | 20 | 13.C4 | KA0137:24 | TURBINE PANEL B JB70 | 13.D3
AF0087:11 | SC | KA013624 | WHT | 20 | 13.B4 | KA0136:24 | TURBINE PANEL B JB70 | 13.B3
AF0087:43 | SC | KA013621 | WHT | 20 | 13.B4 | KA0136:21 | TURBINE PANEL B JB70 | 13.B3
AF0091:07 | SC | KA014114 | WHT | 20 | 13.C2 | KA0141:14 | TURBINE PANEL B JB70 | 13.C2
AF0091:12 | SC | KA0134A1 | WHT | 20 | 56.C7 | KA0134:A1 | TURBINE PANEL B JB70 | 13.C6
AF0091:39 | SC | KA014111 | WHT | 20 | 13.C2 | KA0141:11 | TURBINE PANEL B JB70 | 13.C2
AF0092:02 | SC | KA0133A1 | WHT | 20 | 54.B7 | KA0133:A1 | TURBINE PANEL B JB70 | 13.C6
AF0092:06 | SC | KA013114 | WHT | 20 | 54.A7 | KA0131:14 | TURBINE PANEL B JB70 | 13.D4
AF0092:13 | SC | XT02372 | WHT | 20 | 22.C7 | XT0237:2 T2 | TURBINE PANEL B JB70 | 22.C5
AF0095:18 | SC | SV21202 | WHT | 20 | 44.A7 | XT0060:4 | TURBINE PANEL B JB70 | 44.A5
AF0096:SH | SC | IEG023011 | GRN | 14 | 9.B5 | IEG0230:11 | TURBINE PANEL B JB70 | 9.B6
AR0600:IE2 | SC | IEG02301 | GRN | 12 | 7.A1 | IEG0230:1 | TURBINE PANEL B JB70 | 7.B4
FU0139:LD | SC | FU0139 | WHT | 14 | 12.A5 | XT0136:1 | TURBINE PANEL B JB70 | 13.A2
FU0211:LD | SC | FU0211 | WHT | 14 | 12.B4 | KA1020:14 | TURBINE PANEL B JB70 | 29.A5
GR0133: | SC | IEG02303 | GRN | 14 | 3.A3 | IEG0230:3 | TURBINE PANEL B JB70 | 3.A3
GR0134: | SC | IEG02306 | GRN | 14 | 3.A3 | IEG0230:6 | TURBINE PANEL B JB70 | 3.A3
GR0135: | SC | IEG02307 | GRN | 14 | 3.A4 | IEG0230:7 | TURBINE PANEL B JB70 | 3.A4
KA0135:A1 | SC | KA0135A1 | WHT | 20 | 13.D6 | KA0144:A1 | TURBINE PANEL B JB70 | 13.C6
KA0135:A1 | SC | KA0135A1 | WHT | 20 | 13.D6 | KA0131:11 | TURBINE PANEL B JB70 | 13.D4
KA0135:A2 | SC | 0V | WHT | 20 | 13.D6 | KA0136:A2 | TURBINE PANEL B JB70 | 13.D6
KA0135:A2 | SC | 0V | WHT | 20 | 13.D6 | KA0144:A2 | TURBINE PANEL B JB70 | 13.C6
KA0221:11 | SC | 022111 | WHT | 20 | 44.A6 | KA0235:24 | TURBINE PANEL B JB70 | 44.A5
KA0221:A1 | SC | 007602 | WHT | 16 | 44.A6 | AF0076:02 | TURBINE PANEL B JB70 | 44.A7
KA0221:A2 | SC | 007618 | WHT | 20 | 44.A6 | AF0076:18 | TURBINE PANEL B JB70 | 44.A7
KA0224:A1 | SC | 007615 | WHT | 20 | 25.D6 | AF0076:15 | TURBINE PANEL B JB70 | 25.D6
KA0224:A2 | SC | 007631 | WHT | 20 | 25.D6 | AF0076:31 | TURBINE PANEL B JB70 | 25.D6
XT0050:1 | SC | FT21081 | WHT | 16 | 46.C5 | FU0213:LD | TURBINE PANEL B JB70 | 12.C5
XT0134:4 | SC | 0V | WHT | 12 | 12.B3 | XT0235:1 | TURBINE PANEL B JB70 | 12.D4
XT0134:4 | SC | 0V | WHT | 16 | 12.B3 | XT0110:2 | TURBINE PANEL B JB70 | 17.A5
XT0135:1 | SC | 0V | WHT | 14 | 12.B4 | XT0136:3 | TURBINE PANEL B JB70 | 13.A2
XT0135:1 | SC | 0V | WHT | 16 | 12.B4 | KA1020:24 | TURBINE PANEL B JB70 | 29.A5
XT0138:4 | SC | FU0136 | WHT | 14 | 12.B3 | XT0110:1 | TURBINE PANEL B JB70 | 17.A5
XT0138:4 | SC | FU0136 | WHT | 16 | 12.B3 | FU0210:LI | TURBINE PANEL B JB70 | 12.C4
XT0139:4 | SC | KA0231A1 | WHT | 14 | 14.D6 | XT0110:3 | TURBINE PANEL B JB70 | 17.B5
XT0139:4 | SC | KA0231A1 | WHT | 20 | 14.D6 | KA0230:A1 | TURBINE PANEL B JB70 | 14.D6
AU0080:L2 | WC0008 | AU0080L2 | ENET | CABLE | 2.A4 | AU0070:L1 | TURBINE PANEL B JB70 | 2.A5
AP0606:L1 | WC0680 | AP0606L1 | ENET | CABLE | 5.A1 | AT0680:LAN1 | TURBINE PANEL B JB70 | 5.A2
UA1520:+24 | WC4749 | UA15201 | RED | 20 | 36.A5 | AF0450:05 | TURBINE PANEL B JB70 | 36.A7
UA1520:OUT | WC4749 | UA15202 | CLR | 20 | 36.A5 | AF0450:06 | TURBINE PANEL B JB70 | 36.A7
UA1520:COM | WC4749 | UA15203 | BLK | 20 | 36.A5 | AF0450:08 | TURBINE PANEL B JB70 | 36.A7
XT1521:1 | WC4749 | PE1520S | SH | 20 | 36.A5 | AF0450:23 | TURBINE PANEL B JB70 | 36.A7
SolarTools ver. 24.0.84.24712 (Jul 31, 2025)
Report date: 3/3/2026 11:49 AM

## TURBINE PANEL B JB70
TURBINE PANEL B JB70
TURBINE PANEL B^JB70
Project # | J0630
Project Name | TC TUSCARORA SHOETREE CR
Revision | A.3
Controls DE | G.JP
Phone:
Controls ME
Phone:
From | [5 empty] | To
Device ID | Cable (W) Conductor (SC) Jumper Clip (JC) | Wire No. | Wire ID | Gauge/Size | Page/Zone | Device ID | Location | Page/Zone
XT0060:1 | JC | 0V | CLIP | --- | 10.C1 | XT0060:2 | TURBINE PANEL B JB70 | 10.D1
XT0070:1 | JC | 0V | CLIP | --- | 10.B1 | XT0070:2 | TURBINE PANEL B JB70 | 10.B1
XT0136:1 | JC | FU0139 | CLIP | --- | 13.A2 | XT0136:2 | TURBINE PANEL B JB70 | 13.A2
XT0233:1 | JC | FU0210 | CLIP | --- | 12.C4 | XT0233:2 | TURBINE PANEL B JB70 | 12.C4
XT0233:2 | JC | FU0210 | CLIP | --- | 12.C4 | XT0233:3 | TURBINE PANEL B JB70 | 12.C4
XT0235:1 | JC | 0V | CLIP | --- | 12.D4 | XT0235:2 | TURBINE PANEL B JB70 | 12.D4
XT0235:2 | JC | 0V | CLIP | --- | 12.D4 | XT0235:3 | TURBINE PANEL B JB70 | 12.D4
XT0240:11 | JC | FU0139 | CLIP | --- | 14.C4 | XT0240:12 | TURBINE PANEL B JB70 | 14.C4
XT0240:9 | JC | 0V | CLIP | --- | 14.D3 | XT0240:10 | TURBINE PANEL B JB70 | 14.D3
AF0061:COM | SC | 0V | WHT | 14 | 10.C2 | XT0060:2 | TURBINE PANEL B JB70 | 10.D1
AF0061:V+ | SC | FU0061 | WHT | 14 | 10.C2 | FU0061:LD | TURBINE PANEL B JB70 | 10.C1
AF0062:00 | SC | 006200 | WHT | 20 | 44.B7 | KA0222:14 | TURBINE PANEL B JB70 | 44.B6
AF0062:08 | SC | 006208 | WHT | 20 | 30.A7 | KA0233:14 | TURBINE PANEL B JB70 | 30.A5
AF0062:10 | SC | 006210 | WHT | 20 | 30.A7 | KA0233:24 | TURBINE PANEL B JB70 | 30.A6
AF0062:16 | SC | SV21242 | WHT | 20 | 44.B7 | XT0060:6 | TURBINE PANEL B JB70 | 44.C5
AF0062:40 | SC | 006240 | WHT | 20 | 30.A7 | KA0233:12 | TURBINE PANEL B JB70 | 30.A5
AF0062:COM | SC | 0V | WHT | 14 | 10.C3 | XT0060:2 | TURBINE PANEL B JB70 | 10.D1
AF0062:V+ | SC | FU0062 | WHT | 14 | 10.C3 | FU0062:LD | TURBINE PANEL B JB70 | 10.D1
AF0063:COM | SC | AU0060N | WHT | 14 | 10.C3 | AU0060:COM | TURBINE PANEL B JB70 | 10.B2
AF0063:COM | SC | AF0063N | WHT | 20 | 10.C3 | AF0064:COM | TURBINE PANEL B JB70 | 10.B4
AF0063:V+ | SC | AF0063P | WHT | 20 | 10.C3 | AF0064:V+ | TURBINE PANEL B JB70 | 10.B4
AF0063:V+ | SC | AU0060P | WHT | 20 | 10.C3 | AU0060:V+ | TURBINE PANEL B JB70 | 10.B2
AF0064:COM | SC | AF0064N | WHT | 20 | 10.B4 | AF0065:COM | TURBINE PANEL B JB70 | 10.B5
AF0064:SH | SC | AF0064G | GRN | 14 | 10.B4 | AF0065:SH | TURBINE PANEL B JB70 | 10.B5
AF0064:SH | SC | AU0060G | GRN | 14 | 10.B4 | AU0060:GND | TURBINE PANEL B JB70 | 10.B2
AF0064:V+ | SC | AF0064P | WHT | 20 | 10.B4 | AF0065:V+ | TURBINE PANEL B JB70 | 10.B5
AF0065:COM | SC | AF0065N | WHT | 20 | 10.B5 | AF0066:COM | TURBINE PANEL B JB70 | 10.C5
AF0065:SH | SC | AF0065G | GRN | 14 | 10.B5 | AF0066:SH | TURBINE PANEL B JB70 | 10.C5
AF0065:V+ | SC | AF0065P | WHT | 20 | 10.B5 | AF0066:V+ | TURBINE PANEL B JB70 | 10.C5
AF0066:SH | SC | AF0066G | GRN | 14 | 10.C5 | AF0068:SH | TURBINE PANEL B JB70 | 10.C6
AF0067:12 | SC | KA0134A1 | WHT | 20 | 56.D7 | KA0134:A1 | TURBINE PANEL B JB70 | 13.C6
AF0067:COM | SC | 0V | WHT | 14 | 10.C6 | XT0060:2 | TURBINE PANEL B JB70 | 10.D1
AF0067:COM | SC | AF0067N | WHT | 20 | 10.C6 | AF0068:COM | TURBINE PANEL B JB70 | 10.C6
AF0067:V+ | SC | FU0063 | WHT | 14 | 10.C6 | FU0063:LD | TURBINE PANEL B JB70 | 10.D1
AF0067:V+ | SC | AF0067P | WHT | 20 | 10.C6 | AF0068:V+ | TURBINE PANEL B JB70 | 10.C6
AF0068:SH | SC | IEG02304 | GRN | 14 | 10.C6 | IEG0230:4 | TURBINE PANEL B JB70 | 10.C7
AF0071:COM | SC | AF0071N | WHT | 20 | 10.B2 | AF0072:COM | TURBINE PANEL B JB70 | 10.A3
AF0071:COM | SC | AU0070N | WHT | 20 | 10.B2 | AU0070:COM | TURBINE PANEL B JB70 | 10.A2
AF0071:SH | SC | AF0071G | GRN | 14 | 10.B2 | AF0072:SH | TURBINE PANEL B JB70 | 10.A3
AF0071:SH | SC | AU0070G | GRN | 14 | 10.B2 | AU0070:GND | TURBINE PANEL B JB70 | 10.A2
AF0071:V+ | SC | AF0071P | WHT | 20 | 10.B2 | AF0072:V+ | TURBINE PANEL B JB70 | 10.A3
AF0071:V+ | SC | AU0070P | WHT | 20 | 10.B2 | AU0070:V+ | TURBINE PANEL B JB70 | 10.A2
AF0072:COM | SC | AF0072N | WHT | 20 | 10.A3 | AF0073:COM | TURBINE PANEL B JB70 | 10.B3
AF0072:SH | SC | AF0072G | GRN | 14 | 10.A3 | AF0073:SH | TURBINE PANEL B JB70 | 10.B3
AF0072:V+ | SC | AF0072P | WHT | 20 | 10.A3 | AF0073:V+ | TURBINE PANEL B JB70 | 10.B3
AF0073:COM | SC | AF0073N | WHT | 20 | 10.B3 | AF0074:COM | TURBINE PANEL B JB70 | 10.B4
AF0073:SH | SC | AF0073G | GRN | 14 | 10.B3 | AF0074:SH | TURBINE PANEL B JB70 | 10.B4
AF0073:V+ | SC | AF0073P | WHT | 20 | 10.B3 | AF0074:V+ | TURBINE PANEL B JB70 | 10.B4
AF0074:COM | SC | AF0074N | WHT | 20 | 10.B4 | AF0075:COM | TURBINE PANEL B JB70 | 10.A5
AF0074:SH | SC | AF0074G | GRN | 14 | 10.B4 | AF0075:SH | TURBINE PANEL B JB70 | 10.A5
AF0074:V+ | SC | AF0074P | WHT | 20 | 10.B4 | AF0075:V+ | TURBINE PANEL B JB70 | 10.A5
AF0075:COM | SC | AF0075N | WHT | 20 | 10.A5 | AF0077:COM | TURBINE PANEL B JB70 | 10.B6
AF0075:SH | SC | AF0075G | GRN | 14 | 10.A5 | AF0077:SH | TURBINE PANEL B JB70 | 10.B6
AF0075:V+ | SC | AF0075P | WHT | 20 | 10.A5 | AF0077:V+ | TURBINE PANEL B JB70 | 10.B6
AF0076:00 | SC | 007600 | WHT | 20 | 40.B7 | KA0237:14 | TURBINE PANEL B JB70 | 40.B5
AF0076:01 | SC | KA023724 | WHT | 20 | 42.B7 | KA0237:24 | TURBINE PANEL B JB70 | 42.B5
AF0076:04 | SC | 007604 | WHT | 16 | 44.B7 | KA0222:A1 | TURBINE PANEL B JB70 | 44.B6
AF0076:08 | SC | 007608 | WHT | 20 | 24.A7 | KA1020:A1 | TURBINE PANEL B JB70 | 24.A5
AF0076:10 | SC | KT014615 | WHT | 20 | 14.C7 | KT0146:15 | TURBINE PANEL B JB70 | 14.C6
AF0076:11 | SC | UA1200J14 | WHT | 20 | 15.C7 | UA1200:J1-4 | TURBINE PANEL B JB70 | 15.B3
AF0076:12 | SC | 007612 | WHT | 20 | 15.C7 | XT0237:1 B2 | TURBINE PANEL B JB70 | 15.C5
AF0076:13 | SC | KT0146B1 | WHT | 20 | 13.B2 | KT0146:B1 | TURBINE PANEL B JB70 | 13.B2
AF0076:20 | SC | 007620 | WHT | 20 | 44.B7 | KA0222:A2 | TURBINE PANEL B JB70 | 44.B6
AF0076:24 | SC | 007624 | WHT | 20 | 24.A7 | KA1020:A2 | TURBINE PANEL B JB70 | 24.A5
AF0076:26 | SC | KA0231A2 | WHT | 20 | 14.C7 | KA0231:A2 | TURBINE PANEL B JB70 | 14.C6
AF0076:29 | SC | KT0146A2 | WHT | 20 | 13.B2 | KT0146:A2 | TURBINE PANEL B JB70 | 13.B2
AF0076:COM | SC | 0V | WHT | 14 | 10.A5 | XT0070:2 | TURBINE PANEL B JB70 | 10.B1
AF0076:V+ | SC | FU0071 | WHT | 14 | 10.A5 | FU0071:LD | TURBINE PANEL B JB70 | 10.B1
AF0077:SH | SC | IEG02305 | GRN | 14 | 10.B6 | IEG0230:5 | TURBINE PANEL B JB70 | 10.B7
XT0240:3 | SC | JW1 | CLIP | -- | 14.A3 | XT0240:2 | TURBINE PANEL B JB70 | 14.A3
XT0240:2 | SC | JP0 | VIO | 20 | 14.A3 | XT0240:1 | TURBINE PANEL B JB70 | 14.A3
AF0400:12 | SC | XT04001 | GRN | 16 | 17.B6 | XT0400:1 | TURBINE PANEL B JB70 | 17.C6
AF0410:32 | SC | XT04001 | GRN | 16 | 17.B5 | XT0400:1 | TURBINE PANEL B JB70 | 17.C6
AF0410:53 | SC | 0V | WHT | 14 | 17.B5 | XT0110:2 | TURBINE PANEL B JB70 | 17.A5
AF0410:54 | SC | AF0420N | WHT | 14 | 17.B5 | AF0420:53 | TURBINE PANEL B JB70 | 17.B5
AF0410:55 | SC | FU0113 | WHT | 16 | 17.B5 | FU0113:LD | TURBINE PANEL B JB70 | 17.A4
AF0410:56 | SC | AF0420P | WHT | 14 | 17.B5 | AF0420:55 | TURBINE PANEL B JB70 | 17.B5
AF0420:32 | SC | XT04001 | GRN | 16 | 17.B5 | XT0400:1 | TURBINE PANEL B JB70 | 17.C6
AF0420:54 | SC | AF0430N | WHT | 14 | 17.B5 | AF0430:53 | TURBINE PANEL B JB70 | 17.B4
AF0420:56 | SC | AF0430P | WHT | 14 | 17.B5 | AF0430:55 | TURBINE PANEL B JB70 | 17.B4
AF0430:32 | SC | XT04002 | GRN | 16 | 17.B4 | XT0400:2 | TURBINE PANEL B JB70 | 17.C3
AF0430:54 | SC | AF0450N | WHT | 14 | 17.B4 | AF0450:53 | TURBINE PANEL B JB70 | 17.B3
AF0430:56 | SC | AF0450P | WHT | 14 | 17.B4 | AF0450:55 | TURBINE PANEL B JB70 | 17.B3
AF0450:32 | SC | XT04002 | GRN | 16 | 17.B3 | XT0400:2 | TURBINE PANEL B JB70 | 17.C3
AT0680:NEG | SC | 0V | WHT | 16 | 5.C3 | XT0680:2 | TURBINE PANEL B JB70 | 5.D3
AT0680:POS | SC | AT0680POS | WHT | 14 | 5.C3 | XT0680:1 | TURBINE PANEL B JB70 | 5.D3
AU0060:COM | SC | 0V | WHT | 14 | 10.B2 | XT0060:1 | TURBINE PANEL B JB70 | 10.C1
AU0060:V+ | SC | FU0060 | WHT | 14 | 10.B2 | FU0060:LD | TURBINE PANEL B JB70 | 10.C1
AU0070:COM | SC | 0V | WHT | 14 | 10.A2 | XT0070:1 | TURBINE PANEL B JB70 | 10.B1
AU0070:V+ | SC | FU0070 | WHT | 14 | 10.A2 | FU0070:LD | TURBINE PANEL B JB70 | 10.B1
FU0060:LI | SC | FU0210 | WHT | 14 | 10.C1 | XT0233:1 | TURBINE PANEL B JB70 | 12.C4
FU0060:LI | SC | FU0210 | WHT | 14 | 10.C1 | FU0061:LI | TURBINE PANEL B JB70 | 10.C1
FU0061:LI | SC | FU0210 | WHT | 14 | 10.C1 | FU0062:LI | TURBINE PANEL B JB70 | 10.D1
FU0062:LI | SC | FU0210 | WHT | 14 | 10.D1 | FU0063:LI | TURBINE PANEL B JB70 | 10.D1
FU0070:LI | SC | FU0210 | WHT | 14 | 10.B1 | XT0233:2 | TURBINE PANEL B JB70 | 12.C4
FU0070:LI | SC | FU0210 | WHT | 14 | 10.B1 | FU0071:LI | TURBINE PANEL B JB70 | 10.B1
FU0110:LD | SC | FU0110 | WHT | 14 | 17.A4 | FU0113:LI | TURBINE PANEL B JB70 | 17.A4
FU0110:LI | SC | FU0136 | WHT | 14 | 17.A4 | XT0110:1 | TURBINE PANEL B JB70 | 17.A5
FU0123:LI | SC | FU0210 | WHT | 16 | 12.C5 | XT0233:3 | TURBINE PANEL B JB70 | 12.C4
FU0210:LD | SC | FU0210 | WHT | 12 | 12.C4 | XT0233:1 | TURBINE PANEL B JB70 | 12.C4
FU0212:LD | SC | FU0212 | WHT | 16 | 12.C5 | KA0248:21 | TURBINE PANEL B JB70 | 15.C6
FU0212:LD | SC | FU0212 | WHT | 16 | 12.C5 | XT0233:4 | TURBINE PANEL B JB70 | 15.D5
FU0212:LI | SC | FU0210 | WHT | 14 | 12.C5 | XT0233:1 | TURBINE PANEL B JB70 | 12.C4
FU0213:LI | SC | FU0210 | WHT | 14 | 12.C5 | XT0233:2 | TURBINE PANEL B JB70 | 12.C4
FU0680:LD | SC | AT0680POS | WHT | 14 | 5.D2 | XT0680:1 | TURBINE PANEL B JB70 | 5.D3
FU0680:LI | SC | FU0210 | WHT | 14 | 5.D2 | XT0233:3 | TURBINE PANEL B JB70 | 12.C4
GR0231: | SC | IEG02308 | GRN | 14 | 3.A4 | IEG0230:8 | TURBINE PANEL B JB70 | 3.A4
GR0232: | SC | IEG023013 | GRN | 14 | 3.A4 | IEG0230:13 | TURBINE PANEL B JB70 | 3.A4
GR0233: | SC | IEG023012 | GRN | 14 | 3.A4 | IEG0230:12 | TURBINE PANEL B JB70 | 3.A4
GR0680: | SC | GR0680 | GRN/YEL | 14 | 3.A5 | FRAME | TURBINE PANEL B JB70 | 3.A4
IEG0230:10 | SC | IEG023010 | GRN | 14 | 15.D6 | UA1200:J3-4 | TURBINE PANEL B JB70 | 15.B3
IEG0230:9 | SC | IEG02309 | GRN | 14 | 17.C6 | XT0400:3 | TURBINE PANEL B JB70 | 17.C6
KA0130:A1 | SC | 008135 | WHT | 20 | 15.C5 | KA0130:11 | TURBINE PANEL B JB70 | 15.D6
KA0130:A2 | SC | UA1200J26 | WHT | 20 | 15.C5 | UA1200:J2-6 | TURBINE PANEL B JB70 | 15.B3
KA0131:12 | SC | KA013112 | WHT | 20 | 13.D4 | KA0137:24 | TURBINE PANEL B JB70 | 13.D3
KA0131:A1 | SC | KA0231A1 | WHT | 20 | 13.B6 | KA0132:A1 | TURBINE PANEL B JB70 | 13.B6
KA0131:A1 | SC | KA0231A1 | WHT | 20 | 13.B6 | XT0136:10 | TURBINE PANEL B JB70 | 13.B5
KA0131:A2 | SC | 0V | WHT | 20 | 13.B6 | KA0132:A2 | TURBINE PANEL B JB70 | 13.B6
KA0131:A2 | SC | 0V | WHT | 20 | 13.B6 | KT0145:A2 | TURBINE PANEL B JB70 | 13.B6
KA0132:11 | SC | FU0139 | WHT | 20 | 13.A3 | KA0133:11 | TURBINE PANEL B JB70 | 13.A3
KA0132:11 | SC | FU0139 | WHT | 20 | 13.A3 | KT0145:15 | TURBINE PANEL B JB70 | 13.D2
KA0132:12 | SC | KT0141A1 | WHT | 20 | 13.A3 | KT0142:A1 | TURBINE PANEL B JB70 | 13.A6
KA0132:12 | SC | KT0141A1 | WHT | 20 | 13.A3 | KA0133:12 | TURBINE PANEL B JB70 | 13.A3
KA0132:21 | SC | KA0138A1 | WHT | 20 | 13.D4 | KA0138:A1 | TURBINE PANEL B JB70 | 13.D6
KA0132:22 | SC | KA013222 | WHT | 20 | 13.D4 | KA0137:14 | TURBINE PANEL B JB70 | 13.D3
KA0132:22 | SC | KA013222 | WHT | 20 | 13.D4 | KT0141:18 | TURBINE PANEL B JB70 | 13.D2
KA0132:24 | SC | KA013224 | WHT | 20 | 13.D4 | KA0134:14 | TURBINE PANEL B JB70 | 13.D3
KA0132:A1 | SC | KA0231A1 | WHT | 20 | 13.B6 | KA0141:A1 | TURBINE PANEL B JB70 | 13.C6
KA0132:A2 | SC | 0V | WHT | 20 | 13.B6 | KA0141:A2 | TURBINE PANEL B JB70 | 13.C6
KA0133:11 | SC | FU0139 | WHT | 20 | 13.A3 | KA0134:11 | TURBINE PANEL B JB70 | 13.D3
KA0133:A2 | SC | 0V | WHT | 20 | 13.C6 | KA0134:A2 | TURBINE PANEL B JB70 | 13.C6
KA0133:A2 | SC | 0V | WHT | 20 | 13.C6 | KA0141:A2 | TURBINE PANEL B JB70 | 13.C6
KA0134:11 | SC | FU0139 | WHT | 20 | 13.D3 | KA0136:11 | TURBINE PANEL B JB70 | 13.B4
KA0134:A2 | SC | 0V | WHT | 20 | 13.C6 | KA0144:A2 | TURBINE PANEL B JB70 | 13.C6
KA0136:11 | SC | FU0139 | WHT | 20 | 13.B4 | KA0137:21 | TURBINE PANEL B JB70 | 13.D3
KA0136:14 | SC | KA013821 | WHT | 20 | 13.B4 | KA0138:21 | TURBINE PANEL B JB70 | 13.B5
KA0136:A1 | SC | PS32002 | WHT | 20 | 13.D6 | XT0136:5 | TURBINE PANEL B JB70 | 53.D5
KA0136:A2 | SC | 0V | WHT | 20 | 13.D6 | KA0137:A2 | TURBINE PANEL B JB70 | 13.D6
KA0137:11 | SC | FU0139 | WHT | 20 | 13.D3 | KA0137:21 | TURBINE PANEL B JB70 | 13.D3
KA0137:A1 | SC | KA0137A1 | WHT | 20 | 13.D6 | KT0142:18 | TURBINE PANEL B JB70 | 13.D2
KA0137:A2 | SC | 0V | WHT | 20 | 13.D6 | KA0138:A2 | TURBINE PANEL B JB70 | 13.D6
KA0138:11 | SC | KM3170EP | WHT | 20 | 56.C5 | XT0136:13 | TURBINE PANEL B JB70 | 56.C5
KA0138:14 | SC | FU0139 | WHT | 20 | 56.C5 | XT0136:11 | TURBINE PANEL B JB70 | 56.C6
KA0138:24 | SC | KT0144B1 | WHT | 20 | 13.B5 | KT0144:B1 | TURBINE PANEL B JB70 | 13.B6
KA0141:21 | SC | KT0146A1 | WHT | 20 | 13.B2 | KT0146:A1 | TURBINE PANEL B JB70 | 13.B2
KA0141:21 | SC | KT0146A1 | WHT | 20 | 13.B2 | KA0241:21 | TURBINE PANEL B JB70 | 13.B2
KA0141:24 | SC | FU0139 | WHT | 20 | 13.B2 | KA0241:24 | TURBINE PANEL B JB70 | 13.B2
KA0141:24 | SC | FU0139 | WHT | 20 | 13.B2 | XT0136:2 | TURBINE PANEL B JB70 | 13.A2
KA0222:11 | SC | 022211 | WHT | 20 | 44.B6 | KA0236:24 | TURBINE PANEL B JB70 | 44.B5
KA0230:A1 | SC | KA0231A1 | WHT | 20 | 14.D6 | KA0234:A1 | TURBINE PANEL B JB70 | 14.D6
KA0231:11 | SC | KA0231A1 | WHT | 20 | 14.C6 | KA0231:A1 | TURBINE PANEL B JB70 | 14.C6
KA0231:11 | SC | KA0231A1 | WHT | 20 | 14.C6 | KA0242:11 | TURBINE PANEL B JB70 | 14.C6
KA0231:14 | SC | KA024214 | WHT | 20 | 14.C6 | KA0242:14 | TURBINE PANEL B JB70 | 14.C6
KA0231:14 | SC | KA024214 | WHT | 20 | 14.C6 | KT0146:18 | TURBINE PANEL B JB70 | 14.C6
KA0231:21 | SC | KA023121 | WHT | 20 | 14.A4 | KA0245:14 | TURBINE PANEL B JB70 | 14.A4
KA0231:A1 | SC | KA0231A1 | WHT | 20 | 14.C6 | KA0232:A1 | TURBINE PANEL B JB70 | 14.D6
KA0231:A2 | SC | KA0231A2 | WHT | 20 | 14.C6 | KA0232:A2 | TURBINE PANEL B JB70 | 14.D6
KA0232:A1 | SC | KA0231A1 | WHT | 20 | 14.D6 | KA0233:A1 | TURBINE PANEL B JB70 | 14.D6
KA0232:A2 | SC | KA0231A2 | WHT | 20 | 14.D6 | KA0233:A2 | TURBINE PANEL B JB70 | 14.D6
KA0233:A1 | SC | KA0231A1 | WHT | 20 | 14.D6 | KA0234:A1 | TURBINE PANEL B JB70 | 14.D6
KA0233:A2 | SC | KA0231A2 | WHT | 20 | 14.D6 | KA0234:A2 | TURBINE PANEL B JB70 | 14.D6
KA0234:A2 | SC | KA0231A2 | WHT | 20 | 14.D6 | KA0230:A2 | TURBINE PANEL B JB70 | 14.D6
KA0235:11 | SC | UA1200J21 | WHT | 20 | 14.A5 | XT0060:3 | TURBINE PANEL B JB70 | 15.D5
KA0235:11 | SC | UA1200J21 | WHT | 20 | 14.A5 | KA0241:11 | TURBINE PANEL B JB70 | 14.A5
KA0235:14 | SC | KA024114 | WHT | 20 | 14.A5 | KA0241:14 | TURBINE PANEL B JB70 | 14.A5
KA0235:A1 | SC | ESTOP | WHT | 20 | 14.A2 | XT0240:4 | TURBINE PANEL B JB70 | 14.A3
KA0235:A1 | SC | ESTOP | WHT | 20 | 14.A2 | KA0236:A1 | TURBINE PANEL B JB70 | 14.B2
KA0236:11 | SC | FU0139 | WHT | 20 | 14.D4 | KA0244:11 | TURBINE PANEL B JB70 | 14.D4
KA0236:11 | SC | FU0139 | WHT | 20 | 14.D4 | XT0240:12 | TURBINE PANEL B JB70 | 14.C4
KA0236:12 | SC | KA023612 | WHT | 20 | 14.D4 | XT0240:13 | TURBINE PANEL B JB70 | 14.D4
KA0236:A1 | SC | ESTOP | WHT | 20 | 14.B2 | KA0237:A1 | TURBINE PANEL B JB70 | 14.B2
KA0236:A2 | SC | 0V | WHT | 20 | 14.B2 | KA0235:A2 | TURBINE PANEL B JB70 | 14.A2
KA0236:A2 | SC | 0V | WHT | 20 | 14.B2 | KA0237:A2 | TURBINE PANEL B JB70 | 14.B2
KA0237:A1 | SC | ESTOP | WHT | 20 | 14.B2 | KA0238:A1 | TURBINE PANEL B JB70 | 14.B2
KA0237:A2 | SC | 0V | WHT | 20 | 14.B2 | KA0238:A2 | TURBINE PANEL B JB70 | 14.B2
KA0238:A1 | SC | ESTOP | WHT | 20 | 14.B2 | KA0239:A1 | TURBINE PANEL B JB70 | 14.B2
KA0238:A2 | SC | 0V | WHT | 20 | 14.B2 | KA0239:A2 | TURBINE PANEL B JB70 | 14.B2
KA0239:A1 | SC | ESTOP | WHT | 20 | 14.B2 | KA0240:A1 | TURBINE PANEL B JB70 | 14.B2
KA0239:A2 | SC | 0V | WHT | 20 | 14.B2 | KA0240:A2 | TURBINE PANEL B JB70 | 14.B2
KA0240:11 | SC | PS32004 | WHT | 18 | 53.D5 | XT0136:6 | TURBINE PANEL B JB70 | 53.D5
KA0240:14 | SC | UF1300 | WHT | 20 | 53.D5 | XT0136:7 | TURBINE PANEL B JB70 | 53.D6
KA0240:A1 | SC | ESTOP | WHT | 20 | 14.B2 | KA0248:A1 | TURBINE PANEL B JB70 | 14.C2
KA0240:A2 | SC | 0V | WHT | 20 | 14.B2 | KA0248:A2 | TURBINE PANEL B JB70 | 14.C2
KA0241:14 | SC | KA024114 | WHT | 20 | 14.A5 | KA0231:24 | TURBINE PANEL B JB70 | 14.A4
KA0241:A1 | SC | KA0241A1 | WHT | 20 | 14.C2 | KA0242:A1 | TURBINE PANEL B JB70 | 14.C2
KA0241:A1 | SC | KA0241A1 | WHT | 20 | 14.C2 | XT0240:6 | TURBINE PANEL B JB70 | 14.C3
KA0241:A2 | SC | 0V | WHT | 20 | 14.C2 | KA0242:A2 | TURBINE PANEL B JB70 | 14.C2
KA0241:A2 | SC | 0V | WHT | 20 | 14.C2 | KA0250:A2 | TURBINE PANEL B JB70 | 14.C2
KA0242:11 | SC | KA0231A1 | WHT | 20 | 14.C6 | XT0136:10 | TURBINE PANEL B JB70 | 13.B5
KA0242:21 | SC | 024221 | WHT | 20 | 15.C6 | XT0237:1 T2 | TURBINE PANEL B JB70 | 15.C5
KA0242:24 | SC | KA024822 | WHT | 20 | 15.C6 | KA0248:22 | TURBINE PANEL B JB70 | 15.C6
KA0242:A2 | SC | 0V | WHT | 20 | 14.C2 | KA0243:A2 | TURBINE PANEL B JB70 | 14.C2
KA0243:21 | SC | ESTOPC | WHT | 20 | 14.A3 | XT0240:1 | TURBINE PANEL B JB70 | 14.A3
KA0243:24 | SC | KA024511 | WHT | 20 | 14.A3 | KA0245:11 | TURBINE PANEL B JB70 | 14.A4
KA0243:A1 | SC | KA0243A1 | WHT | 20 | 14.C2 | KA0244:A1 | TURBINE PANEL B JB70 | 14.D2
KA0243:A1 | SC | KA0243A1 | WHT | 20 | 14.C2 | XT0240:7 | TURBINE PANEL B JB70 | 14.C3
KA0243:A2 | SC | 0V | WHT | 20 | 14.C2 | KA0244:A2 | TURBINE PANEL B JB70 | 14.D2
KA0244:12 | SC | KA024412 | WHT | 20 | 14.D4 | KT0145:A1 | TURBINE PANEL B JB70 | 13.B6
KA0244:A1 | SC | KA0243A1 | WHT | 20 | 14.D2 | KA0246:A1 | TURBINE PANEL B JB70 | 14.D2
KA0244:A2 | SC | 0V | WHT | 20 | 14.D2 | KA0246:A2 | TURBINE PANEL B JB70 | 14.D2
KA0245:A1 | SC | KA0245A1 | WHT | 20 | 14.D2 | KA0249:A1 | TURBINE PANEL B JB70 | 14.D2
KA0245:A1 | SC | KA0245A1 | WHT | 20 | 14.D2 | XT0240:8 | TURBINE PANEL B JB70 | 14.D3
KA0245:A2 | SC | 0V | WHT | 20 | 14.D2 | KA0249:A2 | TURBINE PANEL B JB70 | 14.D2
KA0245:A2 | SC | 0V | WHT | 20 | 14.D2 | KA0247:A2 | TURBINE PANEL B JB70 | 14.D2
KA0246:A1 | SC | KA0243A1 | WHT | 20 | 14.D2 | KA0247:A1 | TURBINE PANEL B JB70 | 14.D2
KA0246:A2 | SC | 0V | WHT | 20 | 14.D2 | KA0247:A2 | TURBINE PANEL B JB70 | 14.D2
KA0248:A1 | SC | ESTOP | WHT | 20 | 14.C2 | KA0250:A1 | TURBINE PANEL B JB70 | 14.C2
KA0248:A2 | SC | 0V | WHT | 20 | 14.C2 | KA0250:A2 | TURBINE PANEL B JB70 | 14.C2
KA0249:A2 | SC | 0V | WHT | 20 | 14.D2 | XT0240:10 | TURBINE PANEL B JB70 | 14.D3
KT0140:15 | SC | FU0139 | WHT | 20 | 13.D1 | KT0142:15 | TURBINE PANEL B JB70 | 13.D2
KT0140:15 | SC | FU0139 | WHT | 20 | 13.A2 | XT0136:2 | TURBINE PANEL B JB70 | 13.A2
KT0140:16 | SC | KT014115 | WHT | 20 | 13.D1 | KT0141:15 | TURBINE PANEL B JB70 | 13.D2
KT0140:18 | SC | KT0143A1 | WHT | 20 | 13.A2 | KT0143:A1 | TURBINE PANEL B JB70 | 13.A6
KT0140:A1 | SC | KT0140A1 | WHT | 20 | 13.A6 | KT0143:16 | TURBINE PANEL B JB70 | 13.A5
KT0140:A2 | SC | 0V | WHT | 20 | 13.A6 | KT0141:A2 | TURBINE PANEL B JB70 | 13.A6
KT0140:A2 | SC | 0V | WHT | 20 | 13.A6 | XT0136:3 | TURBINE PANEL B JB70 | 13.A2
KT0141:18 | SC | KA013222 | WHT | 20 | 13.D2 | KT0144:18 | TURBINE PANEL B JB70 | 13.D2
KT0141:A1 | SC | KT0141A1 | WHT | 20 | 13.A6 | KT0143:15 | TURBINE PANEL B JB70 | 13.A5
KT0141:A1 | SC | KT0141A1 | WHT | 20 | 13.A6 | KT0142:A1 | TURBINE PANEL B JB70 | 13.A6
KT0141:A2 | SC | 0V | WHT | 20 | 13.A6 | KT0142:A2 | TURBINE PANEL B JB70 | 13.A6
KT0142:15 | SC | FU0139 | WHT | 20 | 13.D2 | KT0144:A1 | TURBINE PANEL B JB70 | 13.B6
KT0142:18 | SC | KA0137A1 | WHT | 20 | 13.D2 | KT0145:18 | TURBINE PANEL B JB70 | 13.D2
KT0142:A2 | SC | 0V | WHT | 20 | 13.A6 | KT0143:A2 | TURBINE PANEL B JB70 | 13.A6
KT0143:A2 | SC | 0V | WHT | 20 | 13.A6 | KT0144:A2 | TURBINE PANEL B JB70 | 13.B6
KT0144:15 | SC | FU0139 | WHT | 20 | 13.D2 | KT0145:15 | TURBINE PANEL B JB70 | 13.D2
KT0144:15 | SC | FU0139 | WHT | 20 | 13.D2 | KT0144:A1 | TURBINE PANEL B JB70 | 13.B6
KT0144:A2 | SC | 0V | WHT | 20 | 13.B6 | KT0145:A2 | TURBINE PANEL B JB70 | 13.B6
UA1200:J1-10 | SC | FU0212 | WHT | 20 | 15.B3 | XT0233:4 | TURBINE PANEL B JB70 | 15.D5
UA1200:J1-5 | SC | UA1200J15 | WHT | 20 | 15.B3 | XT0237:1 B1 | TURBINE PANEL B JB70 | 15.C5
UA1200:J1-8 | SC | UA1200J | WHT | 20 | 47.B6 | UA1200:J3-5 | TURBINE PANEL B JB70 | 47.B6
UA1200:J1-9 | SC | 0V | WHT | 20 | 15.B3 | XT0235:4 | TURBINE PANEL B JB70 | 15.D5
UA1200:J2-1 | SC | UA1200J21 | WHT | 20 | 15.B3 | XT0060:3 | TURBINE PANEL B JB70 | 15.D5
UA1200:J2-2 | SC | FU0212 | WHT | 20 | 15.B3 | XT0233:4 | TURBINE PANEL B JB70 | 15.D5
XT0070:1 | SC | 0V | WHT | 16 | 10.B1 | XT0235:1 | TURBINE PANEL B JB70 | 12.D4
XT0136:1 | SC | FU0139 | WHT | 20 | 13.A2 | XT0136:11 | TURBINE PANEL B JB70 | 56.C6
XT0136:1 | SC | FU0139 | WHT | 20 | 13.A2 | XT0240:12 | TURBINE PANEL B JB70 | 14.C4
XT0136:12 | SC | 0V | WHT | 20 | 56.C6 | XT0136:3 | TURBINE PANEL B JB70 | 13.A2
XT0136:3 | SC | 0V | WHT | 14 | 13.A2 | XT0240:10 | TURBINE PANEL B JB70 | 14.D3
XT0136:4 | SC | FU0139 | WHT | 20 | 53.D5 | XT0136:1 | TURBINE PANEL B JB70 | 13.A2
XT0235:1 | SC | 0V | WHT | 16 | 12.D4 | XT0060:1 | TURBINE PANEL B JB70 | 10.C1
XT0235:2 | SC | 0V | WHT | 16 | 12.D4 | XT0235:4 | TURBINE PANEL B JB70 | 15.D5
XT0240:11 | SC | FU0139 | WHT | 20 | 14.C4 | XT0236:1 | TURBINE PANEL B JB70 | 22.B5
XT0240:13 | SC | KA023612 | WHT | 20 | 14.D4 | XT0237:2 B2 | TURBINE PANEL B JB70 | 22.C5
XT0240:6 | SC | KA0241A1 | WHT | 20 | 14.C3 | XT0236:2 | TURBINE PANEL B JB70 | 22.B5
XT0240:9 | SC | 0V | WHT | 20 | 14.D3 | XT0236:3 | TURBINE PANEL B JB70 | 22.C5
XT0680:2 | SC | 0V | WHT | 14 | 5.D3 | XT0235:3 | TURBINE PANEL B JB70 | 12.D4
AF0410:L1 | WC0006 | AU0060L2 | ENET | CABLE | 2.A2 | AU0060:L2 | TURBINE PANEL B JB70 | 2.A6
AU0060:L1 | WC0007 | AU0070L2 | ENET | CABLE | 2.A6 | AU0070:L2 | TURBINE PANEL B JB70 | 2.A5
AF0410:L2 | WC0041 | AF0410L2 | ENET | CABLE | 2.A2 | AF0420:L1 | TURBINE PANEL B JB70 | 2.A3
AF0420:L2 | WC0042 | AF0420L2 | ENET | CABLE | 2.A3 | AF0430:L1 | TURBINE PANEL B JB70 | 2.A4
AF0430:L2 | WC0043 | AF0430L2 | ENET | CABLE | 2.A4 | AF0450:L1 | TURBINE PANEL B JB70 | 2.A5
AF0066:10 | WC4193 | 006610 | RED | 20 | 31.A7 | KA0234:14 | TURBINE PANEL B JB70 | 31.A5
AF0066:26 | WC4193 | 006626 | BLK | 20 | 31.A7 | KA0234:24 | TURBINE PANEL B JB70 | 31.A5
AF0066:58 | WC4193 | FCE1440S | SH | 20 | 31.A7 | XT0060:5 | TURBINE PANEL B JB70 | 31.A5
AF0065:12 | WC4524 | UA1200J13 | RED | 20 | 15.B7 | UA1200:J1-3 | TURBINE PANEL B JB70 | 15.B3
AF0065:28 | WC4524 | UA1200J11 | BLK | 20 | 15.B7 | UA1200:J1-1 | TURBINE PANEL B JB70 | 15.B3
AF0065:60 | WC4524 | UA1200S | SH | 20 | 15.B7 | FLOATING | TURBINE PANEL B JB70 | 15.B3
AF0400:LBUS | WC8040 | AF0410RBUS | BUS | CABLE | 17.B6 | AF0410:RBUS | TURBINE PANEL B JB70 | 17.B5
AF0410:LBUS | WC8041 | AF0420RBUS | BUS | CABLE | 17.B5 | AF0420:RBUS | TURBINE PANEL B JB70 | 17.B5
AF0420:LBUS | WC8042 | AF0430RBUS | BUS | CABLE | 17.B5 | AF0430:RBUS | TURBINE PANEL B JB70 | 17.B4
AF0430:LBUS | WC8043 | AF0450RBUS | BUS | CABLE | 17.B4 | AF0450:RBUS | TURBINE PANEL B JB70 | 17.B3
XT0236:1 | SC | FU0139 | WHT | 20 | 22.B5 | SH0472:13 | JB70 | 22.B1
XT0236:2 | SC | KA0241A1 | WHT | 20 | 22.B5 | SH0472:14 | JB70 | 22.B1
XT0236:3 | SC | 0V | WHT | 20 | 22.C5 | SH0472:X1 | JB70 | 22.C1
XT0236:4 | SC | SH047211 | WHT | 20 | 22.C5 | SH0472:11 | JB70 | 22.C1
XT0236:5 | SC | SH047212 | WHT | 20 | 22.C5 | SH0472:12 | JB70 | 22.C1
XT0237:2 B1 | SC | SH0472X2 | WHT | 20 | 22.C5 | SH0472:X2 | JB70 | 22.C1
XT0110:1 | SC | FU0136 | WHT | 14 | 17.A5 | XT0130:1 | HP COMPRESSOR^JB73 ONSKID PANEL | 18.A5
XT0110:2 | SC | 0V | WHT | 14 | 17.A5 | XT0130:2 | HP COMPRESSOR^JB73 ONSKID PANEL | 18.A5
XT0110:3 | SC | KA0231A1 | WHT | 20 | 17.B5 | XT0130:5 | HP COMPRESSOR^JB73 ONSKID PANEL | 18.A5
AF0450:L2 | WC0045 | AF0450L2 | ENET | CABLE | 2.A5 | AF0510:L1 | HP COMPRESSOR^JB73 ONSKID PANEL | 2.B4
AF0063:08 | SC | SA0473B-A3 | WHT | 20 | 23.D7 | SA0473:B-A3 | TURBINE BOX^DOOR^JB70 | 23.D1
AF0063:40 | SC | SA0473B-A4 | WHT | 20 | 23.D7 | SA0473:B-A4 | TURBINE BOX^DOOR^JB70 | 23.D1
XT0240:3 | SC | ESTOPA | WHT | 20 | 14.A3 | XT0137:1 | TURBINE BOX^LEFT RAIL^JB70 | 23.B5
XT0240:4 | SC | ESTOP | WHT | 20 | 14.A3 | XT0137:2 | TURBINE BOX^LEFT RAIL^JB70 | 23.B5
IEG0230:14 | SC | IEG023014 | GRN | 14 | 3.A4 | GR1100: | TURBINE BOX^RIGHT RAIL^JB70 | 3.A5
AF0076:02 | SC | 007602 | WHT | 16 | 44.A7 | KA0221:A1 | TURBINE PANEL A JB70 | 44.A6
AF0076:15 | SC | 007615 | WHT | 20 | 25.D6 | KA0224:A1 | TURBINE PANEL A JB70 | 25.D6
AF0076:18 | SC | 007618 | WHT | 20 | 44.A7 | KA0221:A2 | TURBINE PANEL A JB70 | 44.A6
AF0076:31 | SC | 007631 | WHT | 20 | 25.D6 | KA0224:A2 | TURBINE PANEL A JB70 | 25.D6
FU0210:LI | SC | FU0136 | WHT | 16 | 12.C4 | XT0138:4 | TURBINE PANEL A JB70 | 12.B3
FU0213:LD | SC | FT21081 | WHT | 16 | 12.C5 | XT0050:1 | TURBINE PANEL A JB70 | 46.C5
IEG0230:1 | SC | IEG02301 | GRN | 12 | 7.B4 | AR0600:IE2 | TURBINE PANEL A JB70 | 7.A1
IEG0230:11 | SC | IEG023011 | GRN | 14 | 9.B6 | AF0096:SH | TURBINE PANEL A JB70 | 9.B5
IEG0230:2 | SC | IEG02302 | GRN | 14 | 9.D5 | AF0086:SH | TURBINE PANEL A JB70 | 9.D5
IEG0230:3 | SC | IEG02303 | GRN | 14 | 3.A3 | GR0133: | TURBINE PANEL A JB70 | 3.A3
IEG0230:6 | SC | IEG02306 | GRN | 14 | 3.A3 | GR0134: | TURBINE PANEL A JB70 | 3.A3
IEG0230:7 | SC | IEG02307 | GRN | 14 | 3.A4 | GR0135: | TURBINE PANEL A JB70 | 3.A4
KA0130:14 | SC | 008103 | WHT | 20 | 15.D6 | AF0081:03 | TURBINE PANEL A JB70 | 15.C7
KA0130:A1 | SC | 008135 | WHT | 20 | 15.C5 | AF0081:35 | TURBINE PANEL A JB70 | 15.C7
KA0131:11 | SC | KA0135A1 | WHT | 20 | 13.D4 | KA0135:A1 | TURBINE PANEL A JB70 | 13.D6
KA0131:14 | SC | KA013114 | WHT | 20 | 13.D4 | AF0092:06 | TURBINE PANEL A JB70 | 54.A7
KA0133:A1 | SC | KA0133A1 | WHT | 20 | 13.C6 | AF0092:02 | TURBINE PANEL A JB70 | 54.B7
KA0134:A1 | SC | KA0134A1 | WHT | 20 | 13.C6 | AF0091:12 | TURBINE PANEL A JB70 | 56.C7
KA0136:21 | SC | KA013621 | WHT | 20 | 13.B3 | AF0087:43 | TURBINE PANEL A JB70 | 13.B4
KA0136:24 | SC | KA013624 | WHT | 20 | 13.B3 | AF0087:11 | TURBINE PANEL A JB70 | 13.B4
KA0136:A2 | SC | 0V | WHT | 20 | 13.D6 | KA0135:A2 | TURBINE PANEL A JB70 | 13.D6
KA0137:24 | SC | KA013112 | WHT | 20 | 13.D3 | AF0087:09 | TURBINE PANEL A JB70 | 13.C4
KA0141:11 | SC | KA014111 | WHT | 20 | 13.C2 | AF0091:39 | TURBINE PANEL A JB70 | 13.C2
KA0141:14 | SC | KA014114 | WHT | 20 | 13.C2 | AF0091:07 | TURBINE PANEL A JB70 | 13.C2
KA0144:A1 | SC | KA0135A1 | WHT | 20 | 13.C6 | KA0135:A1 | TURBINE PANEL A JB70 | 13.D6
KA0144:A2 | SC | 0V | WHT | 20 | 13.C6 | KA0135:A2 | TURBINE PANEL A JB70 | 13.D6
KA0230:A1 | SC | KA0231A1 | WHT | 20 | 14.D6 | XT0139:4 | TURBINE PANEL A JB70 | 14.D6
KA0235:24 | SC | 022111 | WHT | 20 | 44.A5 | KA0221:11 | TURBINE PANEL A JB70 | 44.A6
KA0239:21 | SC | KA023921 | WHT | 20 | 14.B6 | AF0081:41 | TURBINE PANEL A JB70 | 14.A7
KA0239:24 | SC | KA023924 | WHT | 20 | 14.B6 | AF0081:09 | TURBINE PANEL A JB70 | 14.A7
KA0241:11 | SC | UA1200J21 | WHT | 20 | 14.A5 | AF0081:00 | TURBINE PANEL A JB70 | 14.A7
KA0242:14 | SC | KA024214 | WHT | 20 | 14.C6 | AF0081:08 | TURBINE PANEL A JB70 | 14.C7
KA0243:11 | SC | KA024311 | WHT | 20 | 14.B6 | AF0081:33 | TURBINE PANEL A JB70 | 14.B7
KA0243:14 | SC | KA024314 | WHT | 20 | 14.B6 | AF0081:01 | TURBINE PANEL A JB70 | 14.B7
KA0245:21 | SC | KA024521 | WHT | 20 | 14.B6 | AF0081:34 | TURBINE PANEL A JB70 | 14.B7
KA0245:24 | SC | KA024524 | WHT | 20 | 14.B6 | AF0081:02 | TURBINE PANEL A JB70 | 14.B7
KA1020:14 | SC | FU0211 | WHT | 14 | 29.A5 | FU0211:LD | TURBINE PANEL A JB70 | 12.B4
KA1020:24 | SC | 0V | WHT | 16 | 29.A5 | XT0135:1 | TURBINE PANEL A JB70 | 12.B4
UA1200:J2-7 | SC | UA1200J27 | WHT | 20 | 15.B3 | AF0081:19 | TURBINE PANEL A JB70 | 15.C7
XT0060:4 | SC | SV21202 | WHT | 20 | 44.A5 | AF0095:18 | TURBINE PANEL A JB70 | 44.A7
XT0110:1 | SC | FU0136 | WHT | 14 | 17.A5 | XT0138:4 | TURBINE PANEL A JB70 | 12.B3
XT0110:2 | SC | 0V | WHT | 16 | 17.A5 | XT0134:4 | TURBINE PANEL A JB70 | 12.B3
XT0110:3 | SC | KA0231A1 | WHT | 14 | 17.B5 | XT0139:4 | TURBINE PANEL A JB70 | 14.D6
XT0136:1 | SC | FU0139 | WHT | 14 | 13.A2 | FU0139:LD | TURBINE PANEL A JB70 | 12.A5
XT0136:3 | SC | 0V | WHT | 14 | 13.A2 | XT0135:1 | TURBINE PANEL A JB70 | 12.B4
XT0235:1 | SC | 0V | WHT | 12 | 12.D4 | XT0134:4 | TURBINE PANEL A JB70 | 12.B3
XT0237:2 T2 | SC | XT02372 | WHT | 20 | 22.C5 | AF0092:13 | TURBINE PANEL A JB70 | 22.C7
AU0070:L1 | WC0008 | AU0080L2 | ENET | CABLE | 2.A5 | AU0080:L2 | TURBINE PANEL A JB70 | 2.A4
AT0680:LAN1 | WC0680 | AP0606L1 | ENET | CABLE | 5.A2 | AP0606:L1 | TURBINE PANEL A JB70 | 5.A1
AF0450:05 | WC4749 | UA15201 | RED | 20 | 36.A7 | UA1520:+24 | TURBINE PANEL A JB70 | 36.A5
AF0450:06 | WC4749 | UA15202 | CLR | 20 | 36.A7 | UA1520:OUT | TURBINE PANEL A JB70 | 36.A5
AF0450:08 | WC4749 | UA15203 | BLK | 20 | 36.A7 | UA1520:COM | TURBINE PANEL A JB70 | 36.A5
AF0450:23 | WC4749 | PE1520S | SH | 20 | 36.A7 | XT1521:1 | TURBINE PANEL A JB70 | 36.A5
SolarTools ver. 24.0.84.24712 (Jul 31, 2025)
Report date: 3/3/2026 11:48 AM

## Panel Errors
Panel Errors
Project # | J0630
Project Name | TC TUSCARORA SHOETREE CR
Revision | A.3
Controls DE | G.JP
Phone:
Controls ME
Phone:
From | [6 empty] | To
Device ID | Location | Cable (W) Conductor (SC) Jumper Clip (JC) | Wire ID | Wire No. | Gauge/Size | Page/Zone | Device ID | Location | Page/Zone
EL0273:+ | PANEL | SC | WHT | ZS0273 | 14 | 20.C4 | ZS0273:2 | PANEL | 20.C4
FU0273:LD | LOOSESHIP PANEL | SC | WHT | FU0273 | 14 | 20.C3 | ZS0273:1 | PANEL | 20.C4
XT0085:2 | TURBINE PANEL A JB70 | SC | WHT | 009400 | 20 | 11.C6 | RR0852: -1.0K OHM | PANEL | 11.C6
XT0562:2 | LOOSESHIP PANEL | SC | WHT | 0V | 14 | 20.C2 | EL0273:- | PANEL | 20.C4
XT7112:1 | LOOSESHIP PANEL | SC | WHT | ESTOPB1 | 20 | 25.B5 | ESDR1:11 | PANEL | 25.B5
XT7112:1 | LOOSESHIP PANEL | SC | WHT | ESTOPB1 | 20 | 25.B5 | S112-A:C1 | PANEL | 25.B5
ESDR1:A2 | PANEL | SC | WHT | 0V | 14 | 25.A6 | XT0562:2 | LOOSESHIP PANEL | 20.C2
S112-A:NC1 | PANEL | SC | WHT | ESTOPC | 20 | 25.B5 | XT7112:2 | LOOSESHIP PANEL | 25.B6
S112-B:C2 | PANEL | SC | WHT | S112-BC2 | 20 | 25.B5 | XT7112:3 | LOOSESHIP PANEL | 25.B5
S112-B:NC2 | PANEL | SC | WHT | S112-BNC2 | 20 | 25.B5 | XT7112:4 | LOOSESHIP PANEL | 25.B5
RR0851: -3.01K OHM | PANEL | SC | WHT | FU0137 | 20 | 11.C6 | XT0085:1 | TURBINE PANEL A JB70 | 11.C6
RR0851: -3.01K OHM | PANEL | SC | WHT | 009400 | 20 | 11.C6 | XT0085:2 | TURBINE PANEL A JB70 | 11.C6
RR0852: -1.0K OHM | PANEL | SC | WHT | 0V | 20 | 11.C6 | XT0085:3 | TURBINE PANEL A JB70 | 11.C6
SolarTools ver. 24.0.84.24712 (Jul 31, 2025)
Report date: 3/3/2026 11:48 AM

## Cable Part Numbers
Cable Part Numbers |  |  | SolarTools ver. 24.0.84.24712 (Jul 31, 2025)
Project # | J0630
Report date: 3/3/2026 11:49 AM
Project Name | TC TUSCARORA SHOETREE CR
Revision | A.3
Controls DE | G.JP
Phone:
Controls ME
Phone:
Device ID |  | Part Number |  | Description
WC8058 |  | 2684693-54 |  | CABLE, EXTENSION, BACKPLANE
WC5072 |  | PART OF 1103208-1 |  | CABLE, 2 CONDUCTOR UNSHIELDED PART OF HORN
WC0001 |  | 1302073-36 |  | CABLE, ETHERNET - 36 INCHES
WC0003 |  | 1302073-36 |  | CABLE, ETHERNET - 36 INCHES
WC0006 |  | 1302073-36 |  | CABLE, ETHERNET - 36 INCHES
WC0007 |  | 1302073-36 |  | CABLE, ETHERNET - 36 INCHES
WC0008 |  | 1302073-36 |  | CABLE, ETHERNET - 36 INCHES
WC0009 |  | 1302073-36 |  | CABLE, ETHERNET - 36 INCHES
WC0014 |  | 1302073-36 |  | CABLE, ETHERNET - 36 INCHES
WC0018 |  | 1302073-36 |  | CABLE, ETHERNET - 36 INCHES
WC0041 |  | 1302073-36 |  | CABLE, ETHERNET - 36 INCHES
WC0042 |  | 1302073-36 |  | CABLE, ETHERNET - 36 INCHES
WC0043 |  | 1302073-36 |  | CABLE, ETHERNET - 36 INCHES
WC0051 |  | 1302073-36 |  | CABLE, ETHERNET - 36 INCHES
WC0052 |  | 1302073-36 |  | CABLE, ETHERNET - 36 INCHES
WC0101 |  | 1302073-36 |  | CABLE, COMMUNICATION CABLE - 36 INCHES
WC0680 |  | 1302073-36 |  | CABLE
WC4193 |  | 1022941-12 |  | TPE, 1 PAIR TWISTED SHIELDED
WC4524 |  | 1022941-12 |  | TPE, 1 PAIR TWISTED SHIELDED
WC4749 |  | 1075034-5 |  | PVC, 1 TRIAD TWISTED SHIELDED
WC8040 |  | 1322418-90 |  | CABLE, SYTSTEM FUNCTION
WC8041 |  | 1322418-90 |  | CABLE, SUPPLIED BY OTHERS
WC8042 |  | 1322418-90 |  | CABLE, DYNAMIX 1444 BUS
WC8043 |  | 1322418-90 |  | CABLE, SUPPLIED BY OTHERS
WC8051 |  | 1322418-90 |  | CABLE, SYTSTEM FUNCTION

## Part Number List
Part Number List |  | SolarTools ver. 24.0.84.24712 (Jul 31, 2025)
Project # | J0630
Report date: 3/3/2026 11:49 AM
Project Name | TC TUSCARORA SHOETREE CR
Revision | A.3
Controls DE | G.JP
Phone:
Controls ME
Phone:
Device ID | Part Number | Description | Location
AF0141 | 2684693-17,2684693-25 | 5094-OB8XT, 8 DISCRETE OUTPUT | BOP PANEL^JB74
AF0142 | 2684693-17,2684693-23 | 5094-IB16XT, 16 DISCRETE INPUT | BOP PANEL^JB74
AF0143 | 2684693-18,2684693-56 | 5094-IF8IHXT, 8 ANALOG INPUT, ISOLATED | BOP PANEL^JB74
AF0144 | 2684693-18,2684693-27 | 5094-OF8IHXT, 8 ANALOG OUTPUT, ISOLATED | BOP PANEL^JB74
AF0145 | 2684693-19,2684693-33 | 5094-IY8XT, 8 ANALOG INPUT,TC/RTD/I&V | BOP PANEL^JB74
AF0146 | 2684693-17,2684693-25 | 5094-OB8XT, 8 DISCRETE OUTPUT | BOP PANEL^JB74
AF0181 | 2684693-17,2684693-25 | 5094-OB8XT, 8 DISCRETE OUTPUT | BOP PANEL^JB74
AF0182 | 2684693-17,2684693-23 | 5094-IB16XT, 16 DISCRETE INPUT | BOP PANEL^JB74
AF0183 | 2684693-18,2684693-28 | 5094-IB16SXT, 16 DISCRETE INPUT, S | BOP PANEL^JB74
AF0184 | 2684693-18,2684693-55 | 5094-OB16SXT, 16 DISCRETE OUTPUT, S | BOP PANEL^JB74
AF0185 | 2684693-18,2684693-56 | 5094-IF8IHXT, 8 ANALOG INPUT, ISOLATED | BOP PANEL^JB74
AU0140 | 2684693-22 | 5094-AENTRXT, DEVICE LEVEL RING | BOP PANEL^JB74
AU0180 | 2684693-22 | 5094-AENTRXT, DEVICE LEVEL RING | BOP PANEL^JB74
BA1212 | 1337728-12 | SWITCH, ETAP, DLR INTERFACE | BOP PANEL^JB74
FU0140 | 1043265-1,1043265-5 | FUSE, 10A | BOP PANEL^JB74
FU0141 | 1043265-1,1043265-5 | FUSE, 10A | BOP PANEL^JB74
FU0142 | 1043265-1,1043265-5 | FUSE, 10A | BOP PANEL^JB74
FU0143 | 1043265-1,1043265-5 | FUSE, 10A | BOP PANEL^JB74
FU0180 | 1043265-1,1043265-5 | FUSE, 10A | BOP PANEL^JB74
FU0181 | 1043265-1,1043265-5 | FUSE, 10A | BOP PANEL^JB74
FU0184 | 1043265-1,1043265-5 | FUSE, 10A | BOP PANEL^JB74
FU0570 | 1043265-1,1043265-7 | FUSE, 20A | BOP PANEL^JB74
FU1212 | 1043265-1,1043265-3 | FUSE, 2A | BOP PANEL^JB74
GR0140 | 903842C1 | RAIL LUG, DINRAIL GROUNDING | BOP PANEL^JB74
GR0180 | 903842C1 | RAIL LUG, DINRAIL GROUNDING | BOP PANEL^JB74
GR0257 | 903842C1 | RAIL LUG, DINRAIL GROUNDING | BOP PANEL^JB74
IEG0257 | 232941-200 | BUS BAR, BOP - INSTRUMENT EARTH GROUNDING | BOP PANEL^JB74
KA0531 | 1061979-1 | RELAY, NO EMERGENCY SHUTDOWN SUMMARY | BOP PANEL^JB74
KA0532 | 1061979-1 | RELAY, NO EMERGENCY SHUTDOWN SUMMARY | BOP PANEL^JB74
KA0533 | 1061979-1 | RELAY, NO EMERGENCY SHUTDOWN SUMMARY | BOP PANEL^JB74
KA0534 | 1061979-1 | RELAY, NO EMERGENCY SHUTDOWN SUMMARY | BOP PANEL^JB74
KA0535 | 1061979-1 | RELAY, CONTROLLER ACTIVE | BOP PANEL^JB74
KA0536 | 1061979-1 | RELAY, CONTROLLER ACTIVE | BOP PANEL^JB74
KA0537 | 1061979-1 | RELAY, NO EMERGENCY SHUTDOWN SUMMARY | BOP PANEL^JB74
KA0540 | 1061979-1 | RELAY, OPEN SUCTION VALVE | BOP PANEL^JB74
KA0541 | 1061979-1 | RELAY, OPEN DISCHARGE VALVE | BOP PANEL^JB74
KA0550 | 1061979-1 | RELAY, OPEN SUCTION VALVE SAFETY | BOP PANEL^JB74
KA0551 | 1061979-1 | RELAY, OPEN DISCHARGE VALVE SAFETY | BOP PANEL^JB74
KA0552 | 1061979-1 | RELAY, CLOSE SUCTION VALVE SAFETY | BOP PANEL^JB74
KA0553 | 1061979-1 | RELAY, CLOSE DISCHARGE VALVE SAFETY | BOP PANEL^JB74
KA0554 | 1061979-1 | RELAY, CLOSE VENT VALVE SAFETY | BOP PANEL^JB74
KT0572 | 2651077-1 | TIMER RELAY, SUCTION VALVE CLOSED | BOP PANEL^JB74
KT0573 | 2651077-1 | TIMER RELAY, DISCHARGE VALVE CLOSED | BOP PANEL^JB74
XT0140 | 1066730-7,1066730-8,1067996-4 | TERMINAL BLOCK, SPRING, 4 CONDUCTOR,30-12 AWG (0.05-3.31 MM2),NON-IS | BOP PANEL^JB74
XT0141 | 1066730-7 | TERMINAL BLOCK, SPRING, 4 CONDUCTOR,30-12 AWG (0.05-3.31 MM2),NON-IS | BOP PANEL^JB74
XT0180 | 1066730-7,1066730-8,1067996-4 | TERMINAL BLOCK, SPRING, 4 CONDUCTOR,30-12 AWG (0.05-3.31 MM2),NON-IS | BOP PANEL^JB74
XT0570 | 1066730-16,1066730-17,1067996-4 | TERMINAL STRIP, 2 CONDUCTOR | BOP PANEL^JB74
XT0572 | 1066730-7,1066730-8,1067996-4 | TERMINAL BLOCK, SPRING, 4 CONDUCTOR,30-12 AWG (0.05-3.31 MM2),NON-IS | BOP PANEL^JB74
XT0573 | 1066730-10,1066730-9,1067996-4 | DIODE TERMINAL STRIP, 4 CONDUCTOR | BOP PANEL^JB74
CCKA2160 | CUSTOMER DEFINED | CUSTOMER CONNECTION, CLOSE GAS BLOCK VALVE | GAS FUEL BLOCK BLEED VALVE
CCKA2161 | CUSTOMER DEFINED | CUSTOMER CONNECTION, OPEN GAS BLEED VALVE | GAS FUEL BLOCK BLEED VALVE
AF0510 | 1322418-11,1322418-20,1322418-70,1322418-71 | 1444-DYN04-01RA, 4-CH VIBRATION INPUT^DYNAMIX 1444 VIBRATION | HP COMPRESSOR^JB73 ONSKID PANEL
AF0520 | 1322418-11,1322418-20,1322418-70,1322418-71 | 1444-DYN04-01RA, 4-CH VIBRATION INPUT^DYNAMIX 1444 VIBRATION | HP COMPRESSOR^JB73 ONSKID PANEL
AF1201 | 2684693-17,2684693-25 | 5094-OB8XT, 8 DISCRETE OUTPUT | HP COMPRESSOR^JB73 ONSKID PANEL
AF1202 | 2684693-17,2684693-23 | 5094-IB16XT, 16 DISCRETE INPUT | HP COMPRESSOR^JB73 ONSKID PANEL
AF1203 | 2684693-18,2684693-56 | 5094-IF8IHXT, 8 ANALOG INPUT, ISOLATED | HP COMPRESSOR^JB73 ONSKID PANEL
AF1204 | 2684693-18,2684693-30 | 5094-IF4IHSXT, 4 ANALOG INPUT, S | HP COMPRESSOR^JB73 ONSKID PANEL
AF1205 | 2684693-18,2684693-30 | 5094-IF4IHSXT, 4 ANALOG INPUT, S | HP COMPRESSOR^JB73 ONSKID PANEL
AF1206 | 2684693-21,2684693-36 | 5094-IRT8SXT, 8 RTD/TC ANALOG INPUT, S | HP COMPRESSOR^JB73 ONSKID PANEL
AF1207 | 2684693-18,2684693-28 | 5094-IB16SXT, 16 DISCRETE INPUT, S | HP COMPRESSOR^JB73 ONSKID PANEL
AF1208 | 2684693-19,2684693-33 | 5094-IY8XT, 8 ANALOG INPUT,TC/RTD/I&V | HP COMPRESSOR^JB73 ONSKID PANEL
AF1209 | 2684693-19,2684693-33 | 5094-IY8XT, 8 ANALOG INPUT,TC/RTD/I&V | HP COMPRESSOR^JB73 ONSKID PANEL
AF1210 | 2684693-18,2684693-56 | 5094-IF8IHXT, 8 ANALOG INPUT, ISOLATED | HP COMPRESSOR^JB73 ONSKID PANEL
AF1211 | 2684693-18,2684693-56 | 5094-IF8IHXT, 8 ANALOG INPUT, ISOLATED | HP COMPRESSOR^JB73 ONSKID PANEL
AF1212 | 2684693-18,2684693-27 | 5094-OF8IHXT, 8 ANALOG OUTPUT, ISOLATED | HP COMPRESSOR^JB73 ONSKID PANEL
AU1200 | 2684693-50 | 5094-AEN2TR, FLEX 5000 I/O | HP COMPRESSOR^JB73 ONSKID PANEL
FU0120 | 1043265-1,1043265-5 | FUSE, 10A | HP COMPRESSOR^JB73 ONSKID PANEL
FU0121 | 1043265-1,1043265-5 | FUSE, 10A | HP COMPRESSOR^JB73 ONSKID PANEL
FU0122 | 1043265-1,1043265-4 | FUSE, 5A | HP COMPRESSOR^JB73 ONSKID PANEL
FU0130 | 1043265-1,1043265-7 | FUSE, 20A | HP COMPRESSOR^JB73 ONSKID PANEL
FU0131 | 1043265-1,1043265-4 | FUSE, 5A | HP COMPRESSOR^JB73 ONSKID PANEL
GR0120 | 903849C1 | RAIL GROUND, DIN RAIL GROUNDING | HP COMPRESSOR^JB73 ONSKID PANEL
GR0124 | 903849C1 | RAIL GROUND, DIN RAIL GROUNDING | HP COMPRESSOR^JB73 ONSKID PANEL
GR0845 | 903849C1 | RAIL GROUND, DIN RAIL GROUNDING | HP COMPRESSOR^JB73 ONSKID PANEL
IEG0130 | 232941-110 | BUS BAR, HP/LP CPSR - INSTRUMENT EARTH GROUNDING | HP COMPRESSOR^JB73 ONSKID PANEL
KA0120 | 1061979-1 | RELAY, CONTROLLER ACTIVE | HP COMPRESSOR^JB73 ONSKID PANEL
KA4401 | 1061979-1 | RELAY, CASE DEPRESSURIZED | HP COMPRESSOR^JB73 ONSKID PANEL
WC8058 | 2684693-54 |  | HP COMPRESSOR^JB73 ONSKID PANEL
XT0121 | 1066730-7,1066730-8,1067996-4 | TERMINAL BLOCK, SPRING, 4 CONDUCTOR,30-12 AWG (0.05-3.31 MM2),NON-IS | HP COMPRESSOR^JB73 ONSKID PANEL
XT0130 | 1066730-7,1066730-8,1067996-4 | TERMINAL BLOCK, SPRING, 4 CONDUCTOR,30-12 AWG (0.05-3.31 MM2),NON-IS | HP COMPRESSOR^JB73 ONSKID PANEL
XT0500 | 1066730-1,1066730-2,1067996-4 | TERMINAL STRIP, 4 CONDUCTOR | HP COMPRESSOR^JB73 ONSKID PANEL
XT0520 | 1066730-7,1066730-8,1067996-4 | TERMINAL BLOCK, SPRING, 4 CONDUCTOR,30-12 AWG (0.05-3.31 MM2),NON-IS | HP COMPRESSOR^JB73 ONSKID PANEL
XT0845 | 1066730-7,1066730-8,1067996-4 | TERMINAL BLOCK, SPRING, 4 CONDUCTOR,30-12 AWG (0.05-3.31 MM2),NON-IS | HP COMPRESSOR^JB73 ONSKID PANEL
SA0471 | 1035040-1652,2380746-2 | SELECTOR SWITCH, SPEED | JB70
SB0471 | 1035040-854,2380746-1 | PUSHBUTTON SWITCH, HORN SILENCE | JB70
SB0472 | 1035040-32,2380746-4 | PUSHBUTTON SWITCH, EMERGENCY STOP | JB70
SB0473 | 1035040-855,2380746-1 | PUSHBUTTON SWITCH, ACKNOWLEDGE | JB70
SB0474 | 1035040-121,2380746-1 | PUSHBUTTON SWITCH, RESET | JB70
SH0470 | 1035040-108,2380746-3 | LIGHTED SWITCH, STOP/STOPPING, RED | JB70
SH0471 | 1035040-857,2380746-3 | LIGHTED SWITCH, START/STARTING, GREEN | JB70
SH0472 | 1035040-859,2380746-3 | LIGHTED SWITCH, BACKUP SYSTEM ACTIVE/RESET, AMBER | JB70
XT4875 | DRIVEN COMMON | TERMINAL STRIP, HP COMPRESSOR CASE PRESSURE | JB75
AF0201 | 2684693-48,2684693-51 | 5094-IB32XT, 32 DISCRETE INPUT | LOOSESHIP PANEL
AF0202 | 2684693-49,2684693-57 | 5094-OB32XT, 32 DISCRETE OUTPUT | LOOSESHIP PANEL
AU0200 | 2684693-22 | 5094-AENTRXT, DEVICE LEVEL RING | LOOSESHIP PANEL
FU0200 | 1043265-1,1043265-5 | FUSE, 10A | LOOSESHIP PANEL
FU0201 | 1043265-1,1043265-5 | FUSE, 10A | LOOSESHIP PANEL
FU0273 | 1043265-1,1043265-4 | FUSE, 5A | LOOSESHIP PANEL
FU0560 | 1043265-1,1043265-7 | FUSE, 20A | LOOSESHIP PANEL
GR0200 | 903849C1 | RAIL GROUND, DIN RAIL GROUNDING | LOOSESHIP PANEL
IEG0200 | 232941-110 | BUS BAR, CONTROL CONSOLE - INSTRUMENT EARTH GROUNDING | LOOSESHIP PANEL
KA3103 | 1061979-1 | RELAY, LUBE OIL TANK HEATER | LOOSESHIP PANEL
KA3104 | 1061979-1 | RELAY, GAS FUEL HEATER | LOOSESHIP PANEL
KA3220 | 1061979-1 | RELAY, LUBE OIL COOLER FAN | LOOSESHIP PANEL
XT0200 | 1066730-1 | TERMINAL STRIP, 4 CONDUCTOR | LOOSESHIP PANEL
XT0561 | 1066730-53,1066730-7,1066730-8,1067996-4 | TERMINAL BLOCK, SPRING, 4 CONDUCTOR,30-12 AWG (0.05-3.31 MM2),NON-IS | LOOSESHIP PANEL
XT0562 | 1066730-53,1066730-7,1066730-8,1067996-4 | TERMINAL BLOCK, SPRING, 4 CONDUCTOR,30-12 AWG (0.05-3.31 MM2),NON-IS | LOOSESHIP PANEL
XT3150 | 1066730-7 | TERMINAL BLOCK, SPRING, 4 CONDUCTOR,30-12 AWG (0.05-3.31 MM2),NON-IS | LOOSESHIP PANEL
XT7112 | 1066730-7 | TERMINAL BLOCK, SPRING, 4 CONDUCTOR,30-12 AWG (0.05-3.31 MM2),NON-IS | LOOSESHIP PANEL
BUOSM | CUSTOMER DEFINED |  | PANEL
EL0273 | 1015796,1022899,1024594-100 | LIGHT | PANEL
ESDR1 | CUSTOMER DEFINED | RELAY, ESD RELAY | PANEL
RR0851 | 1066738-11 | RESISTOR, 3.01K OHM | PANEL
RR0852 | 1066738-1 | RESISTOR, 1.0K OHM | PANEL
S112-A | CUSTOMER DEFINED | PUSHBUTTON SWITCH, EMERGENCY STOP | PANEL
S112-B | CUSTOMER DEFINED | PUSHBUTTON SWITCH, EMERGENCY STOP | PANEL
SB7514 | CUSTOMER DEFINED | PUSHBUTTON SWITCH, CUSTOMER FAST STOP DEPRESSURIZED (EXTERNAL) | PANEL
ZS0273 | [2]1113474-2 | LIMIT SWITCH, CONSOLE DOOR OPEN | PANEL
AT1100 | 1577354-4501 | WORKSTATION, VERSA VIEW 1200H | TURBINE BOX^DOOR^JB70
HA0472 | 1103208-101 | HORN, CONTROL SYSTEM ALARM | TURBINE BOX^DOOR^JB70
SA0473 | 1139718-1 | SELECTOR SWITCH, OFF/LOC/AUX/CUST | TURBINE BOX^DOOR^JB70
SA0474 | 1035040-804,2380746-2 | SELECTOR SWITCH, SURGE VALVE | TURBINE BOX^DOOR^JB70
BA1100 | 1337728-10 | SWITCH, ETAP, DLR INTERFACE | TURBINE BOX^LEFT RAIL^JB70
FU0291 | 1043265-4 | FUSE, 5A | TURBINE BOX^LEFT RAIL^JB70
FU1100 | 1043265-1,1043265-5 | FUSE, 10A | TURBINE BOX^LEFT RAIL^JB70
FU1101 | 1043265-1,1043265-3 | FUSE, 2A | TURBINE BOX^LEFT RAIL^JB70
GR1101 | 903849C1 | RAIL GROUND, DIN RAIL GROUNDING | TURBINE BOX^LEFT RAIL^JB70
PC0470 | 2271605-1 | TIMER/COUNTER, ENGINE HOUR / START COUNTER | TURBINE BOX^LEFT RAIL^JB70
UV0291 | 1088442-4 | POWER CONVERTER, DC/DC INPUT TO 24V DC OUTPUT | TURBINE BOX^LEFT RAIL^JB70
XT0137 | 1066730-7,1066730-8,1067996-4 | TERMINAL BLOCK, SPRING, 4 CONDUCTOR,30-12 AWG (0.05-3.31 MM2),NON-IS | TURBINE BOX^LEFT RAIL^JB70
XT0291 | 1066730-7,1066730-8,1067996-4 | TERMINAL BLOCK, SPRING, 4 CONDUCTOR,30-12 AWG (0.05-3.31 MM2),NON-IS | TURBINE BOX^LEFT RAIL^JB70
XT0292 | 1066730-7,1066730-8,1067996-4 | TERMINAL BLOCK, SPRING, 4 CONDUCTOR,30-12 AWG (0.05-3.31 MM2),NON-IS | TURBINE BOX^LEFT RAIL^JB70
GR1100 | 903849C1 | RAIL GROUND, DIN RAIL GROUNDING | TURBINE BOX^RIGHT RAIL^JB70
AF0081 | 2684693-18,2684693-28 | 5094-IB16SXT, 16 DISCRETE INPUT, S | TURBINE PANEL A JB70
AF0082 | 2684693-17,2684693-23 | 5094-IB16XT, 16 DISCRETE INPUT | TURBINE PANEL A JB70
AF0083 | 2684693-19,2684693-33 | 5094-IY8XT, 8 ANALOG INPUT,TC/RTD/I&V | TURBINE PANEL A JB70
AF0084 | 2684693-19,2684693-33 | 5094-IY8XT, 8 ANALOG INPUT,TC/RTD/I&V | TURBINE PANEL A JB70
AF0085 | 2684693-18,2684693-56 | 5094-IF8IHXT, 8 ANALOG INPUT, ISOLATED | TURBINE PANEL A JB70
AF0086 | 2684693-18,2684693-26,2684693-56 | 5094-IF8IHXT, 8 ANALOG INPUT, ISOLATED | TURBINE PANEL A JB70
AF0087 | 2684693-17,2684693-23 | 5094-IB16XT, 16 DISCRETE INPUT | TURBINE PANEL A JB70
AF0091 | 2684693-17,2684693-23 | 5094-IB16XT, 16 DISCRETE INPUT | TURBINE PANEL A JB70
AF0092 | 2684693-17,2684693-24 | 5094-OB16XT, 16 DISCRETE OUTPUT | TURBINE PANEL A JB70
AF0093 | 2684693-17,2684693-24 | 5094-OB16XT, 16 DISCRETE OUTPUT | TURBINE PANEL A JB70
AF0094 | 2684693-19,2684693-33 | 5094-IY8XT, 8 ANALOG INPUT,TC/RTD/I&V | TURBINE PANEL A JB70
AF0095 | 2684693-17,2684693-25 | 5094-OB8XT, 8 DISCRETE OUTPUT | TURBINE PANEL A JB70
AF0096 | 2684693-21,2684693-36 | 5094-IRT8SXT, 8 RTD/TC ANALOG INPUT, S | TURBINE PANEL A JB70
AP0601 | 1089241-20 | MODULE, BLANK FILLER | TURBINE PANEL A JB70
AP0602 | 1089241-40 | 1756-EN2TRXT, ETHERNET | TURBINE PANEL A JB70
AP0603 | 1089241-40 | 1756-EN2TRXT, ETHERNET | TURBINE PANEL A JB70
AP0604 | 1089241-36 | 1756-EN2TXT, ETHERNET | TURBINE PANEL A JB70
AP0605 | 1089241-20 | MODULE, BLANK FILLER | TURBINE PANEL A JB70
AP0606 | 1089241-36 | 1756-EN2TXT, ETHERNET | TURBINE PANEL A JB70
AR0600 | 1089241-29 | RACK CHASSIS, 1756-A7XT (7 SLOT) | TURBINE PANEL A JB70
AT0600 | 1089241-43 | 1756-L83EXTS, CONTROLLER^GUARDLOGIX | TURBINE PANEL A JB70
AU0080 | 2684693-22 | 5094-AENTRXT, FLEX 5000 I/O | TURBINE PANEL A JB70
AU0090 | 2684693-22 | 5094-AENTRXT, FLEX 5000 I/O | TURBINE PANEL A JB70
FU0010 | 1043265-1,1043265-5 | FUSE, 10A | TURBINE PANEL A JB70
FU0011 | 1043265-1,1043265-7 | FUSE, 20A | TURBINE PANEL A JB70
FU0012 | 1043265-1,1043265-5 | FUSE, 10A | TURBINE PANEL A JB70
FU0013 | 1043265-1,1043265-5 | FUSE, 10A | TURBINE PANEL A JB70
FU0014 | 1043265-1,1043265-5 | FUSE, 10A | TURBINE PANEL A JB70
FU0015 | 1043265-1,1043265-5 | FUSE, 10A | TURBINE PANEL A JB70
FU0020 | 1043265-1,1043265-7 | FUSE, 20A | TURBINE PANEL A JB70
FU0021 | 1043265-1,1043265-7 | FUSE, 20A | TURBINE PANEL A JB70
FU0022 | 1043265-1,1043265-7 | FUSE, 20A | TURBINE PANEL A JB70
FU0080 | 1043265-1,1043265-5 | FUSE, 10A | TURBINE PANEL A JB70
FU0081 | 1043265-1,1043265-5 | FUSE, 10A | TURBINE PANEL A JB70
FU0082 | 1043265-1,1043265-5 | FUSE, 10A | TURBINE PANEL A JB70
FU0090 | 1043265-1,1043265-5 | FUSE, 10A | TURBINE PANEL A JB70
FU0091 | 1043265-1,1043265-5 | FUSE, 10A | TURBINE PANEL A JB70
FU0092 | 1043265-1,1043265-5 | FUSE, 10A | TURBINE PANEL A JB70
FU0093 | 1043265-1,1043265-5 | FUSE, 10A | TURBINE PANEL A JB70
FU0136 | 1043265-1,1043265-9 | FUSE, 30A | TURBINE PANEL A JB70
FU0137 | 1043265-1,1043265-7 | FUSE, 20A | TURBINE PANEL A JB70
FU0139 | 1043265-1,1043265-4 | FUSE, 5A | TURBINE PANEL A JB70
FU0211 | 1043265-1,1043265-4 | FUSE, 5A | TURBINE PANEL A JB70
GR0131 | 903849C1 | RAIL GROUND, DIN RAIL GROUNDING | TURBINE PANEL A JB70
GR0132 | 903849C1 | RAIL GROUND, DIN RAIL GROUNDING | TURBINE PANEL A JB70
GR0133 | 903849C1 | RAIL GROUND, DIN RAIL GROUNDING | TURBINE PANEL A JB70
GR0134 | 903849C1 | RAIL GROUND, DIN RAIL GROUNDING | TURBINE PANEL A JB70
GR0135 | 903842C1 | RAIL LUG, DINRAIL GROUNDING | TURBINE PANEL A JB70
KA0135 | 1061979-1 | RELAY, AC PRE/POST PUMP DRIVE | TURBINE PANEL A JB70
KA0221 | 1061979-1 | RELAY, PRIMARY GAS FUEL^SHUTOFF VALVE | TURBINE PANEL A JB70
KA0224 | 1061979-1 | RELAY, EMERGENCY SHUTDOWN ACTIVE | TURBINE PANEL A JB70
KA0270 | 1061979-1 | RELAY, HUFF/PUFF MANUAL | TURBINE PANEL A JB70
KA2160 | 1061979-1 | RELAY, SPARE | TURBINE PANEL A JB70
KA2161 | 1061979-1 | RELAY, SPARE | TURBINE PANEL A JB70
PEG0130 | 232941-300 | BUS BAR, PANEL A - POWER EARTH GROUNDING | TURBINE PANEL A JB70
UA1520 | 1061979-1,1105411-11 | SIGNAL CONVERTER, BAM 2 SIGNAL CONDITIONER | TURBINE PANEL A JB70
UJ0131 | 1286570-1 | POWER CONVERTER, AC/DC INPUT TO 28V DC OUTPUT | TURBINE PANEL A JB70
UV0600 | 1089241-28 | POWER SUPPLY, RSLOGIX CHASSIS | TURBINE PANEL A JB70
XT0011 | 1066730-16,1066730-17,1066730-18 | TERMINAL STRIP, 2 CONDUCTOR | TURBINE PANEL A JB70
XT0014 | 1247052-1 | BUS BAR, SYSTEM FUNCTION (USE) | TURBINE PANEL A JB70
XT0050 | 1066730-7 | TERMINAL BLOCK, SPRING, 4 CONDUCTOR,30-12 AWG (0.05-3.31 MM2),NON-IS | TURBINE PANEL A JB70
XT0080 | 1066730-7,1066730-8,1067996-4 | TERMINAL BLOCK, SPRING, 4 CONDUCTOR,30-12 AWG (0.05-3.31 MM2),NON-IS | TURBINE PANEL A JB70
XT0085 | 1066730-7,1066730-8,1067996-4 | TERMINAL BLOCK, SPRING, 4 CONDUCTOR,30-12 AWG (0.05-3.31 MM2),NON-IS | TURBINE PANEL A JB70
XT0090 | 1066730-7,1066730-8,1067996-4 | TERMINAL BLOCK, SPRING, 4 CONDUCTOR,30-12 AWG (0.05-3.31 MM2),NON-IS | TURBINE PANEL A JB70
XT0134 | 1066730-16,1066730-17,1066730-18 | TERMINAL STRIP, 2 CONDUCTOR | TURBINE PANEL A JB70
XT0135 | 1066730-7,1066730-8,1067996-4 | TERMINAL BLOCK, SPRING, 4 CONDUCTOR,30-12 AWG (0.05-3.31 MM2),NON-IS | TURBINE PANEL A JB70
XT0138 | 1066730-16,1066730-17,1066730-18 | TERMINAL STRIP, 2 CONDUCTOR | TURBINE PANEL A JB70
XT0139 | 1066730-7,1066730-8,1067996-4 | TERMINAL BLOCK, SPRING, 4 CONDUCTOR,30-12 AWG (0.05-3.31 MM2),NON-IS | TURBINE PANEL A JB70
XT0150 | 1066730-7 | TERMINAL BLOCK, SPRING, 4 CONDUCTOR,30-12 AWG (0.05-3.31 MM2),NON-IS | TURBINE PANEL A JB70
XT0575 | 1066730-7 | TERMINAL BLOCK, SPRING, 4 CONDUCTOR,30-12 AWG (0.05-3.31 MM2),NON-IS | TURBINE PANEL A JB70
XT1521 | 1066730-7,1066730-8,1067996-4 | TERMINAL BLOCK, SPRING, 4 CONDUCTOR,30-12 AWG (0.05-3.31 MM2),NON-IS | TURBINE PANEL A JB70
XT7512 | 1066730-7 | TERMINAL BLOCK, SPRING, 4 CONDUCTOR,30-12 AWG (0.05-3.31 MM2),NON-IS | TURBINE PANEL A JB70
XTFGH | 1066730-1,1066730-2 | TERMINAL STRIP, 4 CONDUCTOR | TURBINE PANEL A JB70
AF0061 | 2684693-17,2684693-25 | 5094-OB8XT, 8 DISCRETE OUTPUT | TURBINE PANEL B JB70
AF0062 | 2684693-17,2684693-25 | 5094-OB8XT, 8 DISCRETE OUTPUT | TURBINE PANEL B JB70
AF0063 | 2684693-17,2684693-23 | 5094-IB16XT, 16 DISCRETE INPUT | TURBINE PANEL B JB70
AF0064 | 2684693-18,2684693-30 | 5094-IF4IHSXT, 4 ANALOG INPUT, S | TURBINE PANEL B JB70
AF0065 | 2684693-18,2684693-30 | 5094-IF4IHSXT, 4 ANALOG INPUT, S | TURBINE PANEL B JB70
AF0066 | 2684693-18,2684693-27 | 5094-OF8IHXT, 8 ANALOG OUTPUT, ISOLATED | TURBINE PANEL B JB70
AF0067 | 2684693-17,2684693-25 | 5094-OB8XT, 8 DISCRETE OUTPUT | TURBINE PANEL B JB70
AF0068 | 2684693-21,2684693-36 | 5094-IRT8SXT, 8 RTD/TC ANALOG INPUT, S | TURBINE PANEL B JB70
AF0071 | 2684693-18,2684693-32 | 5094-IJ2ISXT, 2 FAST COUNTER INPUT, S | TURBINE PANEL B JB70
AF0072 | 2684693-18,2684693-30 | 5094-IF4IHSXT, 4 ANALOG INPUT, S | TURBINE PANEL B JB70
AF0073 | 2684693-21,2684693-36 | 5094-IRT8SXT, 8 RTD/TC ANALOG INPUT, S | TURBINE PANEL B JB70
AF0074 | 2684693-18,2684693-56 | 5094-IF8IHXT, 8 ANALOG INPUT, ISOLATED | TURBINE PANEL B JB70
AF0075 | 2684693-18,2684693-30 | 5094-IF4IHSXT, 4 ANALOG INPUT, S | TURBINE PANEL B JB70
AF0076 | 2684693-18,2684693-29 | 5094-OB16SXT, 16 DISCRETE OUTPUT, S | TURBINE PANEL B JB70
AF0077 | 2684693-19,2684693-33 | 5094-IY8XT, 8 ANALOG INPUT,TC/RTD/I&V | TURBINE PANEL B JB70
AF0400 | 1322418-31,1322418-40,1322418-72,1322418-73 | 1444-TSCX02-02RB, 2-CH TACHOMETER INPUT^DYNAMIX 1444 VIBRATION | TURBINE PANEL B JB70
AF0410 | 1322418-11,1322418-20,1322418-70,1322418-71 | 1444-DYN04-01RA, 4-CH VIBRATION INPUT^DYNAMIX 1444 VIBRATION | TURBINE PANEL B JB70
AF0420 | 1322418-11,1322418-20,1322418-70,1322418-71 | 1444-DYN04-01RA, 4-CH VIBRATION INPUT^DYNAMIX 1444 VIBRATION | TURBINE PANEL B JB70
AF0430 | 1322418-11,1322418-20,1322418-70,1322418-71 | 1444-DYN04-01RA, 4-CH VIBRATION INPUT^DYNAMIX 1444 VIBRATION | TURBINE PANEL B JB70
AF0450 | 1322418-11,1322418-20,1322418-70,1322418-71 | 1444-DYN04-01RA, 4-CH VIBRATION INPUT^DYNAMIX 1444 VIBRATION | TURBINE PANEL B JB70
AT0680 | 1634974-100 | GATEWAY MODULE, TURBOTRONIC GATEWAY | TURBINE PANEL B JB70
AU0060 | 2684693-22 | 5094-AENTRXT, FLEX 5000 I/O | TURBINE PANEL B JB70
AU0070 | 2684693-22 | 5094-AENTRXT, FLEX 5000 I/O | TURBINE PANEL B JB70
FU0060 | 1043265-1,1043265-5 | FUSE, 10A | TURBINE PANEL B JB70
FU0061 | 1043265-1,1043265-5 | FUSE, 10A | TURBINE PANEL B JB70
FU0062 | 1043265-1,1043265-5 | FUSE, 10A | TURBINE PANEL B JB70
FU0063 | 1043265-1,1043265-5 | FUSE, 10A | TURBINE PANEL B JB70
FU0070 | 1043265-1,1043265-5 | FUSE, 10A | TURBINE PANEL B JB70
FU0071 | 1043265-1,1043265-5 | FUSE, 10A | TURBINE PANEL B JB70
FU0110 | 1043265-1,1043265-7 | FUSE, 20A | TURBINE PANEL B JB70
FU0113 | 1043265-1,1043265-4 | FUSE, 5A | TURBINE PANEL B JB70
FU0123 | 1043265-1,1043265-5 | FUSE, 10A | TURBINE PANEL B JB70
FU0210 | 1043265-1,1043265-7 | FUSE, 20A | TURBINE PANEL B JB70
FU0212 | 1043265-1,1043265-3 | FUSE, 2A | TURBINE PANEL B JB70
FU0213 | 1043265-1,1043265-4 | FUSE, 5A | TURBINE PANEL B JB70
FU0680 | 1043265-1,1043265-4 | FUSE, 5A | TURBINE PANEL B JB70
GR0231 | 903842C1 | RAIL LUG, DINRAIL GROUNDING | TURBINE PANEL B JB70
GR0232 | 903842C1 | RAIL LUG, DINRAIL GROUNDING | TURBINE PANEL B JB70
GR0233 | 903842C1 | RAIL LUG, DINRAIL GROUNDING | TURBINE PANEL B JB70
GR0680 | 903849C1 | RAIL GROUND, DIN RAIL GROUNDING | TURBINE PANEL B JB70
IEG0230 | 232941-300 | BUS BAR, PANEL B - INSTRUMENT EARTH GROUNDING | TURBINE PANEL B JB70
KA0130 | 1061979-1 | RELAY, LOWSPEED/OPEN PROBE SETPOINT | TURBINE PANEL B JB70
KA0131 | 1061979-1 | RELAY, CONTROLLER ACTIVE | TURBINE PANEL B JB70
KA0132 | 1061979-1 | RELAY, CONTROLLER ACTIVE | TURBINE PANEL B JB70
KA0133 | 1061979-1 | RELAY, POST LUBE NOT REQUIRED | TURBINE PANEL B JB70
KA0134 | 1061979-1 | RELAY, BACKUP COMMAND OFF | TURBINE PANEL B JB70
KA0136 | 1061979-1 | RELAY, LUBE OIL HEADER^PRESSURE HIGH | TURBINE PANEL B JB70
KA0137 | 1061979-1 | RELAY, LUBE PUMP INHIBIT | TURBINE PANEL B JB70
KA0138 | 1061979-1 | RELAY, BACKUP LUBE OIL PUMP OFF | TURBINE PANEL B JB70
KA0141 | 1061979-1 | RELAY, CONTROLLER ACTIVE | TURBINE PANEL B JB70
KA0144 | 1061979-1 | RELAY, AC PRE-POST PUMP | TURBINE PANEL B JB70
KA0222 | 1061979-1 | RELAY, SECONDARY GAS FUEL^ SHUTOFF VALVE | TURBINE PANEL B JB70
KA0230 | 1061979-1 | RELAY, CONTROLLER ACTIVE | TURBINE PANEL B JB70
KA0231 | 1061979-1 | RELAY, CONTROLLER ACTIVE | TURBINE PANEL B JB70
KA0232 | 1061979-1 | RELAY, CONTROLLER ACTIVE | TURBINE PANEL B JB70
KA0233 | 1061979-1 | RELAY, CONTROLLER ACTIVE | TURBINE PANEL B JB70
KA0234 | 1061979-1 | RELAY, CONTROLLER ACTIVE | TURBINE PANEL B JB70
KA0235 | 1061979-1 | RELAY, NO EMERGENCY ^SHUTDOWN SUMMARY | TURBINE PANEL B JB70
KA0236 | 1061979-1 | RELAY, NO EMERGENCY ^SHUTDOWN SUMMARY | TURBINE PANEL B JB70
KA0237 | 1061979-1 | RELAY, NO EMERGENCY ^SHUTDOWN SUMMARY | TURBINE PANEL B JB70
KA0238 | 1061979-1 | RELAY, NO EMERGENCY SHUTDOWN SUMMARY | TURBINE PANEL B JB70
KA0239 | 1061979-1 | RELAY, NO EMERGENCY SHUTDOWN SUMMARY | TURBINE PANEL B JB70
KA0240 | 1061979-1 | RELAY, NO EMERGENCY SHUTDOWN SUMMARY | TURBINE PANEL B JB70
KA0241 | 1061979-1 | RELAY, BACKUP SYSTEM RESET | TURBINE PANEL B JB70
KA0242 | 1061979-1 | RELAY, BACKUP SYSTEM RESET | TURBINE PANEL B JB70
KA0243 | 1061979-1 | RELAY, NO FIRE DETECTED | TURBINE PANEL B JB70
KA0244 | 1061979-1 | RELAY, NO FIRE DETECTED | TURBINE PANEL B JB70
KA0245 | 1061979-1 | RELAY, NO GAS DETECTED | TURBINE PANEL B JB70
KA0246 | 1061979-1 | RELAY, NO FIRE DETECTED | TURBINE PANEL B JB70
KA0247 | 1061979-1 | RELAY, NO FIRE DETECTED | TURBINE PANEL B JB70
KA0248 | 1061979-1 | RELAY, NO EMERGENCY SHUTDOWN SUMMARY | TURBINE PANEL B JB70
KA0249 | 1061979-1 | RELAY, NO GAS DETECTED | TURBINE PANEL B JB70
KA0250 | 1061979-1 | RELAY, NO EMERGENCY SHUTDOWN SUMMARY | TURBINE PANEL B JB70
KA1020 | 1061979-1 | RELAY, IGNITION START | TURBINE PANEL B JB70
KT0140 | 2651077-1 | TIMER RELAY, BACKUP PUMP POST LUBE OFF CYCLE | TURBINE PANEL B JB70
KT0141 | 2651077-1 | TIMER RELAY, BACKUP POST LUBE CONTINUOUS | TURBINE PANEL B JB70
KT0142 | 2651077-1 | TIMER RELAY, TOTAL POST LUBE | TURBINE PANEL B JB70
KT0143 | 2651077-1 | TIMER RELAY, BACKUP PUMP POST LUBE ON CYCLE | TURBINE PANEL B JB70
KT0144 | 2651077-1 | TIMER RELAY, HEADER PRESSURE HIGH BACKUP PUMP OFF | TURBINE PANEL B JB70
KT0145 | 2651077-1 | TIMER RELAY, FIRE DETECTED ROLLDOWN LUBE | TURBINE PANEL B JB70
KT0146 | 2651077-3 | TIMER RELAY, WATCHDOG | TURBINE PANEL B JB70
UA1200 | 1053834-7 | SIGNAL CONVERTER, BACKUP OVERSPEED MODULE | TURBINE PANEL B JB70
XT0060 | 1066730-7,1066730-8,1067996-4 | TERMINAL BLOCK, SPRING, 4 CONDUCTOR,30-12 AWG (0.05-3.31 MM2),NON-IS | TURBINE PANEL B JB70
XT0070 | 1066730-7,1066730-8,1067996-4 | TERMINAL BLOCK, SPRING, 4 CONDUCTOR,30-12 AWG (0.05-3.31 MM2),NON-IS | TURBINE PANEL B JB70
XT0110 | 1066730-7,1066730-8,1067996-4 | TERMINAL BLOCK, SPRING, 4 CONDUCTOR,30-12 AWG (0.05-3.31 MM2),NON-IS | TURBINE PANEL B JB70
XT0136 | 1066730-7,1066730-8,1067996-4 | TERMINAL BLOCK, SPRING, 4 CONDUCTOR,30-12 AWG (0.05-3.31 MM2),NON-IS | TURBINE PANEL B JB70
XT0233 | 1066730-7,1066730-8,1067996-4 | TERMINAL BLOCK, SPRING, 4 CONDUCTOR,30-12 AWG (0.05-3.31 MM2),NON-IS | TURBINE PANEL B JB70
XT0235 | 1066730-7,1066730-8,1067996-4 | TERMINAL BLOCK, SPRING, 4 CONDUCTOR,30-12 AWG (0.05-3.31 MM2),NON-IS | TURBINE PANEL B JB70
XT0236 | 1066730-7,1066730-8,1067996-4 | TERMINAL BLOCK, SPRING, 4 CONDUCTOR,30-12 AWG (0.05-3.31 MM2),NON-IS | TURBINE PANEL B JB70
XT0237 | 1066730-10,1066730-9,1067996-4 | DIODE TERMINAL STRIP, 4 CONDUCTOR | TURBINE PANEL B JB70
XT0240 | 1066730-7,1066730-8,1067996-4 | TERMINAL BLOCK, SPRING, 4 CONDUCTOR,30-12 AWG (0.05-3.31 MM2),NON-IS | TURBINE PANEL B JB70
XT0400 | 1066730-1,1066730-2,1067996-4 | TERMINAL STRIP, 4 CONDUCTOR | TURBINE PANEL B JB70
XT0680 | 1066730-7,1066730-8,1067996-4 | TERMINAL BLOCK, SPRING, 4 CONDUCTOR,30-12 AWG (0.05-3.31 MM2),NON-IS | TURBINE PANEL B JB70