## Blue Labels
(SHT 1) JB175 DOOR | (SHT 2) INTELLIGENT START PANEL
HL0411 | IEG0130
HL0409 | PEG0230
HL0401 | GR0801
SB0403 | XT0804
SB0404 | XT0805
XT0806
KT0146
GR0803
XT0807
KA0121
KA0122
KA0123
KA0124
KA0125
KA0126
KA0127
KA0128
KA0129
KA0141
KA0142
KA0235
KA0240
FU0015
FU0016
FU0017
GR0804
AT0600
AP0601
AP0602
AP0603
AP0604
AP0605
AP0606
F0001
FU0011
FU0012
FU0013
FU0014
XT0802
XT0803
GR0802
FU0001
XT0801
GR0805

## White Labels
(SHT 2) INTELLIGENT START PANEL
0V
AT0600G
GR0801
PEG02301

## INTELLIGENT START PANEL
INTELLIGENT START PANEL
Project # | J2590
Project Name | FERNAND VAZ DAC C50 GS START UPGRADE
Revision | 0.1
Controls DE | A.LEACH
Phone: | 0
Controls ME | J. GARCIA
Phone:
From | [5 empty] | To
Device ID | Cable (W) Conductor (SC) Jumper Clip (JC) | Wire No. | Wire ID | Gauge/Size | Page/Zone | Device ID | Location | Page/Zone
XT0802:1 | JC | FU0014 | CLIP | --- | 4.B5 | XT0802:2 | INTELLIGENT START PANEL | 4.B5
XT0803:1 | JC | 0V | CLIP | --- | 4.C4 | XT0803:2 | INTELLIGENT START PANEL | 4.C4
XT0803:2 | JC | 0V | CLIP | --- | 4.C4 | XT0803:3 | INTELLIGENT START PANEL | 4.C4
XT0803:3 | JC | 0V | CLIP | --- | 4.C4 | XT0803:4 | INTELLIGENT START PANEL | 4.C4
XT0803:4 | JC | 0V | CLIP | --- | 4.C4 | XT0803:5 | INTELLIGENT START PANEL | 4.D4
XT0803:5 | JC | 0V | CLIP | --- | 4.D4 | XT0803:6 | INTELLIGENT START PANEL | 4.D4
XT0803:6 | JC | 0V | CLIP | --- | 4.D4 | XT0803:7 | INTELLIGENT START PANEL | 4.D4
XT0804:6 | JC | 0VC | CLIP | --- | 7.B3 | XT0804:7 | INTELLIGENT START PANEL | 7.B3
XT0804:7 | JC | 0VC | CLIP | --- | 7.B3 | XT0804:8 | INTELLIGENT START PANEL | 7.C3
XT0804:8 | JC | 0VC | CLIP | --- | 7.C3 | XT0804:9 | INTELLIGENT START PANEL | 7.C3
XT0804:9 | JC | 0VC | CLIP | --- | 7.C3 | XT0804:10 | INTELLIGENT START PANEL | 7.C3
XT0805:1 | JC | FU0017 | CLIP | --- | 7.A5 | XT0805:2 | INTELLIGENT START PANEL | 7.A5
XT0805:2 | JC | FU0017 | CLIP | --- | 7.A5 | XT0805:3 | INTELLIGENT START PANEL | 7.B5
XT0805:3 | JC | FU0017 | CLIP | --- | 7.B5 | XT0805:4 | INTELLIGENT START PANEL | 7.B5
XT0805:4 | JC | FU0017 | CLIP | --- | 7.B5 | XT0805:5 | INTELLIGENT START PANEL | 7.C5
XT0805:5 | JC | FU0017 | CLIP | --- | 7.C5 | XT0805:6 | INTELLIGENT START PANEL | 7.C5
XT0805:6 | JC | FU0017 | CLIP | --- | 7.C5 | XT0805:7 | INTELLIGENT START PANEL | 7.C5
XT0805:7 | JC | FU0017 | CLIP | --- | 7.C5 | XT0805:8 | INTELLIGENT START PANEL | 7.D5
XT0805:8 | JC | FU0017 | CLIP | --- | 7.D5 | XT0805:9 | INTELLIGENT START PANEL | 7.D5
XT0806:1 | JC | FU0017 | CLIP | --- | 9.A2 | XT0806:2 | INTELLIGENT START PANEL | 9.A2
XT0806:2 | JC | FU0017 | CLIP | --- | 9.A2 | XT0806:3 | INTELLIGENT START PANEL | 9.A2
XT0806:3 | JC | FU0017 | CLIP | --- | 9.A2 | XT0806:4 | INTELLIGENT START PANEL | 9.A2
XT0806:4 | JC | FU0017 | CLIP | --- | 9.A2 | XT0806:5 | INTELLIGENT START PANEL | 9.A2
XT0806:5 | JC | FU0017 | CLIP | --- | 9.A2 | XT0806:6 | INTELLIGENT START PANEL | 9.A2
AP0601:0 | SC | KA012114 | WHT | 20 | 7.A6 | XT0805:10 | INTELLIGENT START PANEL | 7.A6
AP0601:1 | SC | KA012214 | WHT | 20 | 7.A6 | XT0805:11 | INTELLIGENT START PANEL | 7.A6
AP0601:10 | SC | 060110 | WHT | 20 | 9.B6 | XT0806:11 | INTELLIGENT START PANEL | 9.B5
AP0601:11 | SC | 060111 | WHT | 20 | 9.B6 | XT0806:12 | INTELLIGENT START PANEL | 9.B5
AP0601:12 | SC | 060112 | WHT | 20 | 9.B6 | XT0806:13 | INTELLIGENT START PANEL | 9.B5
AP0601:13 | SC | 060113 | WHT | 20 | 9.C6 | XT0806:14 | INTELLIGENT START PANEL | 9.C5
AP0601:14 | SC | 060114 | WHT | 20 | 9.C6 | XT0806:15 | INTELLIGENT START PANEL | 9.C5
AP0601:15 | SC | 060115 | WHT | 20 | 9.D6 | XT0806:16 | INTELLIGENT START PANEL | 9.D5
AP0601:2 | SC | KA012314 | WHT | 20 | 7.B6 | XT0805:12 | INTELLIGENT START PANEL | 7.B6
AP0601:3 | SC | KA012414 | WHT | 20 | 7.B6 | XT0805:13 | INTELLIGENT START PANEL | 7.B6
AP0601:4 | SC | KA012514 | WHT | 20 | 7.C6 | XT0805:14 | INTELLIGENT START PANEL | 7.C6
AP0601:5 | SC | 06015 | WHT | 20 | 7.C6 | XT0805:15 | INTELLIGENT START PANEL | 7.C6
AP0601:6 | SC | 06016 | WHT | 20 | 7.C6 | XT0805:16 | INTELLIGENT START PANEL | 7.C6
AP0601:7 | SC | 06017 | WHT | 20 | 7.D6 | XT0805:17 | INTELLIGENT START PANEL | 7.D6
AP0601:8 | SC | KA012914 | WHT | 20 | 7.D6 | XT0805:18 | INTELLIGENT START PANEL | 7.D6
AP0601:9 | SC | 06019 | WHT | 20 | 9.A6 | XT0806:10 | INTELLIGENT START PANEL | 9.A5
AP0602:0 | SC | KA014124 | WHT | 20 | 5.D6 | KA0141:24 | INTELLIGENT START PANEL | 5.D5
AP0602:1 | SC | KA014121 | WHT | 20 | 5.D6 | KA0141:21 | INTELLIGENT START PANEL | 5.D5
AP0602:3 | SC | KA0141A1 | WHT | 20 | 5.B6 | KT0146:15 | INTELLIGENT START PANEL | 5.C5
AP0603:0 | SC | KT014618 | WHT | 20 | 5.C6 | KT0146:18 | INTELLIGENT START PANEL | 5.C5
AP0603:1 | SC | KT0146B1 | WHT | 20 | 5.A6 | KT0146:B1 | INTELLIGENT START PANEL | 5.A6
AP0603:12 | SC | KA014114 | WHT | 20 | 6.D6 | KA0141:14 | INTELLIGENT START PANEL | 6.D5
AP0603:16 | SC | 0V | WHT | 14 | 3.C4 | XT0803:4 | INTELLIGENT START PANEL | 4.C4
AP0603:17 | SC | FU0015 | WHT | 14 | 3.C4 | XT0802:3 | INTELLIGENT START PANEL | 4.C5
AP0603:2 | SC | KA014221 | WHT | 20 | 5.C6 | KA0142:21 | INTELLIGENT START PANEL | 5.C5
AP0603:5 | SC | KT0146A2 | WHT | 20 | 5.A6 | KT0146:A2 | INTELLIGENT START PANEL | 5.A6
AP0603:6 | SC | KA0240A2 | WHT | 20 | 5.C6 | KA0240:A2 | INTELLIGENT START PANEL | 5.C5
AP0603:7 | SC | 0V | WHT | 14 | 3.C4 | XT0803:4 | INTELLIGENT START PANEL | 4.C4
AP0603:8 | SC | FU0015 | WHT | 14 | 3.C4 | XT0802:3 | INTELLIGENT START PANEL | 4.C5
AP0605:16 | SC | FU0016 | WHT | 14 | 3.C5 | XT0802:4 | INTELLIGENT START PANEL | 4.C5
AP0605:17 | SC | 0V | WHT | 14 | 3.C5 | XT0803:6 | INTELLIGENT START PANEL | 4.D4
AP0606:16 | SC | FU0016 | WHT | 14 | 3.C5 | XT0802:4 | INTELLIGENT START PANEL | 4.C5
AP0606:17 | SC | 0V | WHT | 14 | 3.C5 | XT0803:6 | INTELLIGENT START PANEL | 4.D4
AT0600:MOD - | SC | 0V | WHT | 14 | 3.C2 | XT0803:1 | INTELLIGENT START PANEL | 4.C4
AT0600:MOD + | SC | FU0011 | WHT | 14 | 3.C2 | FU0011:LD | INTELLIGENT START PANEL | 4.B4
AT0600:SA - | SC | 0V | WHT | 14 | 3.C2 | XT0803:2 | INTELLIGENT START PANEL | 4.C4
AT0600:SA + | SC | FU0012 | WHT | 14 | 3.C2 | FU0012:LD | INTELLIGENT START PANEL | 4.B4
AT0600:SA G | SC | AT0600G | GRN | 14 | 3.C2 | IEG0130:1 | INTELLIGENT START PANEL | 3.C1
F0001:GND | SC | PEG02301 | GRN/YEL | 12 | 4.B3 | PEG0230:1 | INTELLIGENT START PANEL | 4.B3
F0001:LD - | SC | 0V | WHT | 10 | 4.B3 | XT0803:1 | INTELLIGENT START PANEL | 4.C4
F0001:LI - | SC | CC0525A | WHT | 10 | 4.B3 | XT0801:2 | INTELLIGENT START PANEL | 4.B2
F0001:LI + | SC | FU0001LD | WHT | 10 | 4.B3 | FU0001:LD | INTELLIGENT START PANEL | 4.B2
FU0001:LI | SC | FU0001LI | WHT | 10 | 4.B2 | XT0801:1 | INTELLIGENT START PANEL | 4.B2
FU0011:LI | SC | 24V | WHT | 10 | 4.B4 | F0001:LD + | INTELLIGENT START PANEL | 4.B3
FU0011:LI | SC | 24V | WHT | 10 | 4.B4 | FU0012:LI | INTELLIGENT START PANEL | 4.B4
FU0012:LI | SC | 24V | WHT | 10 | 4.B4 | FU0013:LI | INTELLIGENT START PANEL | 4.B4
FU0013:LI | SC | 24V | WHT | 10 | 4.B4 | FU0014:LI | INTELLIGENT START PANEL | 4.B4
FU0014:LD | SC | FU0014 | WHT | 14 | 4.B4 | XT0802:1 | INTELLIGENT START PANEL | 4.B5
FU0014:LI | SC | 24V | WHT | 10 | 4.B4 | FU0015:LI | INTELLIGENT START PANEL | 4.C4
FU0015:LD | SC | FU0015 | WHT | 14 | 4.C4 | XT0802:3 | INTELLIGENT START PANEL | 4.C5
FU0015:LI | SC | 24V | WHT | 10 | 4.C4 | FU0016:LI | INTELLIGENT START PANEL | 4.C4
FU0016:LD | SC | FU0016 | WHT | 14 | 4.C4 | XT0802:4 | INTELLIGENT START PANEL | 4.C5
FU0016:LI | SC | 24V | WHT | 10 | 4.C4 | FU0017:LI | INTELLIGENT START PANEL | 4.C4
FU0017:LD | SC | FU0017 | WHT | 14 | 4.C4 | XT0802:5 | INTELLIGENT START PANEL | 4.C5
GR0801: | SC | GR0801 | GRN | 14 | 2.B4 | IEG0130:4 | INTELLIGENT START PANEL | 2.B3
GR0802: | SC | GR0802 | GRN/YEL | 14 | 2.B4 | FRAME | INTELLIGENT START PANEL | 2.B3
GR0803: | SC | GR0803 | GRN/YEL | 14 | 2.B4 | FRAME | INTELLIGENT START PANEL | 2.B3
GR0804: | SC | GR0804 | GRN/YEL | 14 | 2.B4 | FRAME | INTELLIGENT START PANEL | 2.B3
GR0805: | SC | GR0805 | GRN/YEL | 14 | 2.C4 | FRAME | INTELLIGENT START PANEL | 2.C3
KA0121:11 | SC | FU0017 | WHT | 20 | 7.A5 | XT0805:1 | INTELLIGENT START PANEL | 7.A5
KA0121:14 | SC | KA012114 | WHT | 20 | 7.A5 | XT0805:10 | INTELLIGENT START PANEL | 7.A6
KA0121:A1 | SC | KA0121A1 | WHT | 20 | 7.A3 | XT0804:1 | INTELLIGENT START PANEL | 7.A3
KA0121:A2 | SC | 0VC | WHT | 20 | 7.A3 | KA0122:A2 | INTELLIGENT START PANEL | 7.A3
KA0122:11 | SC | FU0017 | WHT | 20 | 7.A5 | XT0805:2 | INTELLIGENT START PANEL | 7.A5
KA0122:14 | SC | KA012214 | WHT | 20 | 7.A5 | XT0805:11 | INTELLIGENT START PANEL | 7.A6
KA0122:A1 | SC | KA0122A1 | WHT | 20 | 7.A3 | XT0804:2 | INTELLIGENT START PANEL | 7.A3
KA0122:A2 | SC | 0VC | WHT | 20 | 7.A3 | KA0123:A2 | INTELLIGENT START PANEL | 7.A3
KA0123:11 | SC | FU0017 | WHT | 20 | 7.B5 | XT0805:3 | INTELLIGENT START PANEL | 7.B5
KA0123:14 | SC | KA012314 | WHT | 20 | 7.B5 | XT0805:12 | INTELLIGENT START PANEL | 7.B6
KA0123:A1 | SC | KA0123A1 | WHT | 20 | 7.A3 | XT0804:3 | INTELLIGENT START PANEL | 7.A3
KA0123:A2 | SC | 0VC | WHT | 20 | 7.A3 | KA0124:A2 | INTELLIGENT START PANEL | 7.B3
KA0124:11 | SC | FU0017 | WHT | 20 | 7.B5 | XT0805:4 | INTELLIGENT START PANEL | 7.B5
KA0124:14 | SC | KA012414 | WHT | 20 | 7.B5 | XT0805:13 | INTELLIGENT START PANEL | 7.B6
KA0124:A1 | SC | KA0124A1 | WHT | 20 | 7.B3 | XT0804:4 | INTELLIGENT START PANEL | 7.B3
KA0124:A2 | SC | 0VC | WHT | 20 | 7.B3 | KA0125:A2 | INTELLIGENT START PANEL | 7.B3
KA0125:11 | SC | FU0017 | WHT | 20 | 7.C5 | XT0805:5 | INTELLIGENT START PANEL | 7.C5
KA0125:14 | SC | KA012514 | WHT | 20 | 7.C5 | XT0805:14 | INTELLIGENT START PANEL | 7.C6
KA0125:A1 | SC | KA0125A1 | WHT | 20 | 7.B3 | XT0804:5 | INTELLIGENT START PANEL | 7.B3
KA0125:A2 | SC | 0VC | WHT | 20 | 7.B3 | XT0804:6 | INTELLIGENT START PANEL | 7.B3
KA0129:11 | SC | FU0017 | WHT | 14 | 7.D5 | XT0805:9 | INTELLIGENT START PANEL | 7.D5
KA0129:14 | SC | KA012914 | WHT | 20 | 7.D5 | XT0805:18 | INTELLIGENT START PANEL | 7.D6
KA0129:A1 | SC | KA0129A1 | WHT | 20 | 7.D3 | XT0804:14 | INTELLIGENT START PANEL | 7.D3
KA0129:A2 | SC | 0VC | WHT | 20 | 7.D3 | XT0804:10 | INTELLIGENT START PANEL | 7.C3
KA0141:12 | SC | FU0014 | WHT | 14 | 6.D5 | XT0802:1 | INTELLIGENT START PANEL | 4.B5
KA0141:A1 | SC | KA0141A1 | WHT | 20 | 5.C5 | KT0146:15 | INTELLIGENT START PANEL | 5.C5
KA0141:A1 | SC | KA0141A1 | WHT | 20 | 5.C5 | KA0142:A1 | INTELLIGENT START PANEL | 5.C5
KA0141:A2 | SC | KA0141A2 | WHT | 20 | 5.C5 | AP0603:4 | INTELLIGENT START PANEL | 5.C6
KA0141:A2 | SC | KA0141A2 | WHT | 20 | 5.C5 | KA0142:A2 | INTELLIGENT START PANEL | 5.C5
KA0142:11 | SC | PS32004 | WHT | 20 | 11.D6 | XT0806:8 | INTELLIGENT START PANEL | 11.D5
KA0142:14 | SC | UF1300 | WHT | 20 | 11.D6 | XT0806:9 | INTELLIGENT START PANEL | 11.D6
KA0142:24 | SC | KA0240A1 | WHT | 20 | 5.C5 | KA0240:A1 | INTELLIGENT START PANEL | 5.C5
KA0240:11 | SC | KA024014 | WHT | 20 | 8.A4 | XT0807:3 | INTELLIGENT START PANEL | 8.A3
KA0240:14 | SC | KA024011 | WHT | 20 | 8.A4 | XT0807:2 | INTELLIGENT START PANEL | 8.A3
KA0240:21 | SC | KA024012 | WHT | 20 | 8.A4 | XT0807:1 | INTELLIGENT START PANEL | 8.A3
KA0240:22 | SC | KA024011 | WHT | 20 | 8.A4 | XT0807:2 | INTELLIGENT START PANEL | 8.A3
KT0146:A1 | SC | FU0014 | WHT | 14 | 5.A6 | XT0802:2 | INTELLIGENT START PANEL | 4.B5
PEG0230:2 | SC | 0V | GRN/YEL | 12 | 4.D5 | XT0803:7 | INTELLIGENT START PANEL | 4.D4
XT0802:5 | SC | FU0017 | WHT | 14 | 4.C5 | XT0805:1 | INTELLIGENT START PANEL | 7.A5
XT0806:1 | SC | FU0017 | WHT | 16 | 9.A2 | XT0802:5 | INTELLIGENT START PANEL | 4.C5
AP0602:10 | SC | SB040423 | WHT | 20 | 6.A6 | SB0404:23 | JB175 DOOR | 6.A2
AP0602:6 | SC | SB040324 | WHT | 20 | 6.A6 | SB0403:24 | JB175 DOOR | 6.A2
AP0602:7 | SC | SB040323 | WHT | 20 | 6.A6 | SB0403:23 | JB175 DOOR | 6.A2
AP0602:9 | SC | SB040424 | WHT | 20 | 6.A6 | SB0404:24 | JB175 DOOR | 6.A2
AP0603:10 | SC | HL0409AP | WHT | 20 | 6.C6 | HL0409:A+ | JB175 DOOR | 6.C2
AP0603:11 | SC | HL0401AP | WHT | 20 | 6.D6 | HL0401:A+ | JB175 DOOR | 6.D2
AP0603:14 | SC | HL0409A | WHT | 20 | 6.C6 | HL0409:A | JB175 DOOR | 6.C2
KA0141:11 | SC | HL0411AP | WHT | 20 | 6.D5 | HL0411:A+ | JB175 DOOR | 6.D2
KA0141:11 | SC | HL0411AP | WHT | 20 | 6.D5 | HL0411:A+ | JB175 DOOR | 6.D2
SolarTools ver. 24.0.84.24712 (Jul 31, 2025)
Report date: 4/3/2026 3:25 AM

## JB175 DOOR
JB175 DOOR
INTELLIGENT START JB175
Project # | J2590
Project Name | FERNAND VAZ DAC C50 GS START UPGRADE
Revision | 0.1
Controls DE | A.LEACH
Phone: | 0
Controls ME | J. GARCIA
Phone:
From | [5 empty] | To
Device ID | Cable (W) Conductor (SC) Jumper Clip (JC) | Wire No. | Wire ID | Gauge/Size | Page/Zone | Device ID | Location | Page/Zone
HL0401:A | SC | HL0409A | WHT | 20 | 6.D2 | HL0409:A | JB175 DOOR | 6.C2
HL0401:A | SC | HL0409A | WHT | 20 | 6.D2 | HL0411:A | JB175 DOOR | 6.D2
HL0401:A+ | SC | HL0401AP | WHT | 20 | 6.D2 | AP0603:11 | INTELLIGENT START PANEL | 6.D6
HL0409:A | SC | HL0409A | WHT | 20 | 6.C2 | AP0603:14 | INTELLIGENT START PANEL | 6.C6
HL0409:A+ | SC | HL0409AP | WHT | 20 | 6.C2 | AP0603:10 | INTELLIGENT START PANEL | 6.C6
HL0411:A+ | SC | HL0411AP | WHT | 20 | 6.D2 | KA0141:11 | INTELLIGENT START PANEL | 6.D5
HL0411:A+ | SC | HL0411AP | WHT | 20 | 6.D2 | KA0141:11 | INTELLIGENT START PANEL | 6.D5
SB0403:23 | SC | SB040323 | WHT | 20 | 6.A2 | AP0602:7 | INTELLIGENT START PANEL | 6.A6
SB0403:24 | SC | SB040324 | WHT | 20 | 6.A2 | AP0602:6 | INTELLIGENT START PANEL | 6.A6
SB0404:23 | SC | SB040423 | WHT | 20 | 6.A2 | AP0602:10 | INTELLIGENT START PANEL | 6.A6
SB0404:24 | SC | SB040424 | WHT | 20 | 6.A2 | AP0602:9 | INTELLIGENT START PANEL | 6.A6
Report date: 4/3/2026 3:25 AM |  |  |  |  | SolarTools ver. 24.0.84.24712 (Jul 31, 2025)

## Panel Errors
Panel Errors
Project # | J2590
Project Name | FERNAND VAZ DAC C50 GS START UPGRADE
Revision | 0.1
Controls DE | A.LEACH
Phone: | 0
Controls ME | J. GARCIA
Phone:
From | [6 empty] | To
Device ID | Location | Cable (W) Conductor (SC) Jumper Clip (JC) | Wire ID | Wire No. | Gauge/Size | Page/Zone | Device ID | Location | Page/Zone
Report date: 4/3/2026 3:25 AM |  |  |  | SolarTools ver. 24.0.84.24712 (Jul 31, 2025)

## Cable Part Numbers
Cable Part Numbers |  |  | SolarTools ver. 24.0.84.24712 (Jul 31, 2025)
Project # | J2590
Report date: 4/3/2026 3:25 AM
Project Name | FERNAND VAZ DAC C50 GS START UPGRADE
Revision | 0.1
Controls DE | A.LEACH
Phone: | 0
Controls ME | J. GARCIA
Phone:
Device ID |  | Part Number |  | Description

## Part Number List
Part Number List |  | SolarTools ver. 24.0.84.24712 (Jul 31, 2025)
Project # | J2590
Report date: 4/3/2026 3:25 AM
Project Name | FERNAND VAZ DAC C50 GS START UPGRADE
Revision | 0.1
Controls DE | A.LEACH
Phone: | 0
Controls ME | J. GARCIA
Phone:
Device ID | Part Number | Description | Location
AP0601 | 1908163-21,1908163-6 | 5069-IB16, 16 DISCRETE INPUT | INTELLIGENT START PANEL
AP0602 | 1908163-21,1908163-5 | 5069-IB6F-3W, 6 DISCRETE INPUT^FAST,3-WIRE | INTELLIGENT START PANEL
AP0603 | 1908163-21,1908163-7 | 5069-OB8, 8 DISCRETE OUTPUT | INTELLIGENT START PANEL
AP0604 | 1908163-23,1908163-9 | 5069-IY4, 4 ANALOG INPUT^UNIVERSAL | INTELLIGENT START PANEL
AP0605 | 1908163-21,1908163-8 | 5069-OB16, 16 DISCRETE OUTPUT | INTELLIGENT START PANEL
AP0606 | 1908163-21,1908163-8 | 5069-OB16, 16 DISCRETE OUTPUT | INTELLIGENT START PANEL
AT0600 | 1908163-1,1908163-26 | 5069-L306ER, MICROPROCESSOR | INTELLIGENT START PANEL
F0001 | 1022716-1 | FILTER, EMI/SURGE FILTER | INTELLIGENT START PANEL
FU0001 | 1043265-6 | FUSE, 15A | INTELLIGENT START PANEL
FU0011 | 1043265-5 | FUSE, 10A | INTELLIGENT START PANEL
FU0012 | 1043265-5 | FUSE, 10A | INTELLIGENT START PANEL
FU0013 | 1043265-3 | FUSE, 2A | INTELLIGENT START PANEL
FU0014 | 1043265-5 | FUSE, 10A | INTELLIGENT START PANEL
FU0015 | 1043265-5 | FUSE, 10A | INTELLIGENT START PANEL
FU0016 | 1043265-4 | FUSE, 5A | INTELLIGENT START PANEL
FU0017 | 1043265-4 | FUSE, 5A | INTELLIGENT START PANEL
GR0801 | 903849C1 | RAIL LUG, DIN RAIL GROUNDING | INTELLIGENT START PANEL
GR0802 | 903849C1 | RAIL LUG, DIN RAIL GROUNDING | INTELLIGENT START PANEL
GR0803 | 903849C1 | RAIL LUG, DIN RAIL GROUNDING | INTELLIGENT START PANEL
GR0804 | 903849C1 | RAIL GROUND, DIN RAIL GROUNDING | INTELLIGENT START PANEL
GR0805 | 903849C1 | RAIL GROUND, DIN RAIL GROUNDING | INTELLIGENT START PANEL
IEG0130 | 232941-200 | BUS BAR, JB175 - INSTRUMENT EARTH GROUNDING | INTELLIGENT START PANEL
KA0121 | 1061979-1 | RELAY, REMOTE ALARM RESET | INTELLIGENT START PANEL
KA0122 | 1061979-1 | RELAY, STARTER ON TO CRANK | INTELLIGENT START PANEL
KA0123 | 1061979-1 | RELAY, IGNITION ON | INTELLIGENT START PANEL
KA0124 | 1061979-1 | RELAY, NGP 15% SPEED | INTELLIGENT START PANEL
KA0125 | 1061979-1 | RELAY, NGP 60% SPEED | INTELLIGENT START PANEL
KA0129 | 1061979-1 | RELAY, SPARE | INTELLIGENT START PANEL
KA0141 | 1061979-1 | RELAY, CONTROLLER ACTIVE | INTELLIGENT START PANEL
KA0142 | 1061979-1 | RELAY, CONTROLLER ACTIVE | INTELLIGENT START PANEL
KA0240 | 1061979-1 | RELAY, ALARM SUMMARY | INTELLIGENT START PANEL
KT0146 | 1071411-3 | TIMER RELAY, WATCHDOG | INTELLIGENT START PANEL
PEG0230 | 232941-200 | BUS BAR, JB175 - POWER EARTH GROUNDING | INTELLIGENT START PANEL
XT0801 | 1066730-16 | TERMINAL STRIP, SYSTEM FUNCTION (USE) | INTELLIGENT START PANEL
XT0802 | 1066730-5 | TERMINAL STRIP, 3 CONDUCTOR | INTELLIGENT START PANEL
XT0803 | 1066730-16 | TERMINAL STRIP, 2 CONDUCTOR | INTELLIGENT START PANEL
XT0804 | 1066730-5 | TERMINAL STRIP, 3 CONDUCTOR | INTELLIGENT START PANEL
XT0805 | 1066730-5 | TERMINAL STRIP, 3 CONDUCTOR | INTELLIGENT START PANEL
XT0806 | 1066730-5 | TERMINAL STRIP, 3 CONDUCTOR | INTELLIGENT START PANEL
XT0807 | 1066730-5 | TERMINAL STRIP, 3 CONDUCTOR | INTELLIGENT START PANEL
HL0401 | 2380746-7 | LIGHT, STARTER READY (STEADY)^STARTER ON (FLASHING), GREEN | JB175 DOOR
HL0409 | 2380746-7 | LIGHT, STARTER ALARM, AMBER | JB175 DOOR
HL0411 | 2380746-7 | LIGHT, STARTER SHUTDOWN (STEADY)^STARTER CONFIGURE (FLASHING), RED | JB175 DOOR
SB0403 | 2380746-1 | PUSHBUTTON SWITCH, RESET/LAMP TEST | JB175 DOOR
SB0404 | 2380746-1 | PUSHBUTTON SWITCH, VFD CONFIG | JB175 DOOR
2-J2590 | UPGRADE | UPGRADE, REVISED FOR SALES ORDER J2590 | PANEL
CC0525A | CUSTOMER DEFINED | CUSTOMER CONNECTION, CUSTOMER PROVIDED POWER^24VDC | PANEL